## Slide 1
Presented By: Sai Moorty MMS Project Engineer
EMS/MMS Agenda – Overview of Submitted White Paper Requirements

## Slide 2: EMS/MMS Agenda – Presentation Overview of Eight (8) EMS/MMS Whitepapers
Objective:
  Concurrence and disposition from TPTF of concepts described in White Papers
  Refine design direction based upon TPTF feedback
Background:
  Requirements analysis of Real-Time Operations related to Load Frequency Control (LFC) and its interaction with Security Constrained Economic Dispatch (SCED) raised some issues.
  Subsequent discussions between ERCOT, Vendors (AREVA and ABB) and Floyd Trefny (Consultant) resulted in decision to submit White Papers to TPTF for review.

## Slide 3: EMS/MMS Agenda – Presentation Overview of Eight (8) EMS/MMS Whitepapers
Base Point above HASL Flags
  It will not be necessary to implement either the “Base Point above HASL” or “Pseudo-Resource Dispatch” flags in the ICCP telemetry to QSEs
  Indication of Pseudo-Resource Dispatch will be provided in the MIS Secure Area
HDL And LDL During Start up and AS Recall
  During Responsive Reserve recall if the calculated HDL falls below LSL then calculate:
    HDL = LDL = Max (POWERTELEM - (SCED Down Ramp Rate * 5), LASL)
  During Generation Resource startup when POWERTELEM is above 90% but less than LSL then calculate
    LDL = HDL = Min (Actual Gen + (SCED Up Ramp Rate * 5), HASL)
  During Generation Resource startup when POWERTELEM falls below 90% of LSL then calculate
    HDL = LDL = POWERTELEM
Emergency Base points Calculation and Deployment
  During SCED failure, Emergency Base Points will be calculated and issued to QSEs through Generation Subsystem in the EMS. Distribution of Emergency Base Points will cause the current regulation deployment to be reset the same as an update of the SCED solution

## Slide 4: EMS/MMS Agenda – Presentation Overview of Eight (8) EMS/MMS Whitepapers
Coincidental Deployment of Up and Down Regulation
  LFC should not be artificially constrained in a way that regulation deployment of some QSEs may have opposite signs from the other QSEs
Ancillary Service Schedules and Deployment Telemetry
  Expand the set of data to be telemetered from QSE to ERCOT to include the Ancillary Service Resource Responsibility for each participating Resource

## Slide 5: EMS/MMS Agenda – Presentation Overview of Eight (8) EMS/MMS Whitepapers
Responsive Reserve Deployment and Recall
  ERCOT’s deployment of RRS to QSEs will include the following two signals:
    RRS capacity deployment signal wherein each QSE will simply adjust their RRS schedule on their Resources and wait for SCED to produce new Base Points that can include additional Responsive Reserve MW requirement.
    RRS energy deployment signal that requires each QSEs to produce that additional energy through their own deployment to its Resources providing RRS.
  QSE’s telemetry to ERCOT will include the following two signals:
    Signal to indicate the RRS Resource Responsibility
    Signal to indicate the remaining RRS Ancillary Service Schedule that is the difference between the RRS Resource Responsibility amount and deployed amount.
Non-Spin Deployment Notification and Availability
  QSEs are requested to provide to ERCOT two data items related to Non-Spin:
    Non-Spin Responsibility (reflects Non-Spin obligation for the Resource where deployed or not deployed)
    Non-Spin Ancillary Service Schedule (normally equal to Non-Spin responsibility, changes to zero when the QSE makes the Resource available for dispatch following an ERCOT request for Non-Spin deployment, and returns to the Non-Spin responsibility value when ERCOT recalls Non-Spin).

## Slide 6: EMS/MMS Agenda – Presentation Overview of Eight (8) EMS/MMS Whitepapers
SCED Base Point Dispatch
  QSEs will receive the following two Base Point values for each Resource:
    The Base Point as calculated by SCED at every SCED execution
    The Updated Desired Base Point updated every 4 seconds by LFC. The Updated Desired Base Points represent the ERCOT desired control each LFC cycle