## Slide 1
DTMPTHS5: Lake Creek – Temple Switch / Tradinghouse – Temple Pecan Creek 345 kV Dckt
DHILMAR5: Hill Country – Marion / Hill Country – STP 345 kV Dckt
DMARZOR5: Marion – Clear Springs / Marion – Zorn 345 kV Dckt

## Slide 2
Overloaded Element: Lake Creek – Temple Pecan Creek 138 kV
Overloaded Element: Seguin – Seguin West 138 kV
Arrows indicate direction of pre-contingency flow.
Overloaded Element: Marion – Skyline 345 kV

## Slide 3: October 17th Central Texas Congestion
Real-Time Contingency Analysis Results

## Slide 4: October 17th Central Texas Congestion
  Comparing DMARZOR5 with DHILMAR5 overloads shows that as the flow on the Marion – Skyline decreases, the flow on the Seguin – Seguin West increases.
  Generation increases/decreases in the South was effecting the North-South Congestion
  ERCOT systems are not capable of identifying units that have inverse effects in activated OC2s
  SPD will optimize the cost of the deployments

## Slide 5: October 17th Central Texas Congestion
Shift Factor Comparison
  Unit A
    DMARZOR5: -9.1 %
    DHILMAR5: +48.4 %
  Unit B
    DMARZOR5: -9.8 %
    DHILMAR5: +21.2 %
Shift Factor Comparison
  Unit C
    DMARZOR5: +8.6 %
    DTMPTHS5: -7.6 %
  Unit D
    DMARZOR5: +12.6 %
    DTMPTHS5: -7.3 %
  Unit E
    DMARZOR5: +5.1 %
    DTMPTHS5: -8.5 %

## Slide 6: October 17th Central Texas Congestion
Time Line
  02:30 Retracted OC2 for DTMPTHS5 overloading 1300_A
  04:04 Re-issued OC2 for DTMPTHS5
  04:06 Issued OC2 for DMARZOR5 overloading 428T428
  10:58 Issued OC2 fro DHILMAR5 overloading MAR_SKY
  12:21 Retracted OC2 for DHILMAR5 and DMARZOR5 due to OC2 conflict
    Replaced with unit specific OOME instruction (18:36 Re-issued OC2 for DMARZOR5 overloading 428T428
  22:31 Retracted OC2 for DTMPTHS5

## Slide 7: October 17th Central Texas Congestion
04:04
02:30
04:06
12:21
10:58
18:36
22:31
DTMPTHS5
DHILMAR5
DMARZOR5
OOMEs
Indicates OC2
Indicates Manual Action