## Slide 1: Compliance Update
ROS
December 2006

## Slide 2: Control Performance Highlights
NERC CPS1 Performance
  November performance indicated a fifth straight month of declining scores since scores peaked in June, which is not entirely unexpected with more outages and less generation on-line
    October – 137.3
    November – 132.0
PRR 525 Performance
  Preliminary scores for November indicate 32 QSEs passed / 1 non-wind-only QSE failed the measure
  Scores posted on the ERCOT Compliance Website
  Most wind generation is now in separate subQSEs
RRS/NSRS Performance – initial scoring under new criteria in progress.

## Slide 3: ERCOT’s CPS1 Monthly Trend

## Slide 4: 525 Passing 10-Min Interval Percentage Trends
Notes: This indicates that non-passing scores

## Slide 5: NERC ERO Developments
Proposed Delegation Agreement, Exhibits, & Related Documents for the Texas Regional Entity were submitted to NERC on November 17th.
FERC has a docket on these: Delegation Agreement Between the North American Electric Reliability Corporation and Texas Regional Entity, a division of ERCOT, Docket No. RR07-1-000
There are still approvals within ERCOT necessary, discussed at the TAC meeting last month & on January agenda.
Considerable work on standards remains – list of revisions in progress attached. Some of these revisions are in response to FERC comments.
ERCOT Compliance Staff participating with NERC on 2nd ERCOT Local Control Center Reliability Readiness Audits – TXU Electric Delivery (December)

## Slide 6: Self - Certifications
ERCOT TO/TDSP – due 12/1/06 (most are in)
Resource Entities – due 1/10/07
QSEs – due 1/10/07 (for those not audited in 2006)

## Slide 7: Events investigations (Closed)
4/17 EECP - Continued review by PUCT
  Violations have been followed up by PUCT inquiry
  Additional administrative penalties have been levied by PUCT
6/12 Central Texas Disturbance
  Generator protective system coordination followup continues.
  There were no clear violations of OG or standards.
  OG and NERC Standards language on coordination of generation and transmission protection is not clear and difficult to enforce.

## Slide 8: Event Investigation – 9/28 SPS Operation in North Texas
SPS operation tripped > 1000 MW generation - a NERC DCS event. Recovery met NERC requirement (15 minutes).
ERCOT Operations & Planning determined that the SPS operated correctly. Although plant did not decrease output per design, transmission equipment correctly tripped the line to the plant.
Plant personnel identified failure in plant controls, took corrective actions and made improvements to generator-owned equipment.
TDSP & generator each maintained their portions of the SPS as required. The companies proactively scheduled joint testing activities.
QSE SCADA failed, incorrectly indicating full plant output after the unit trip. QSE operators validated plant status after ERCOT Operations called for confirmation, just after the event. Equipment issues were addressed & enhancements made.
ERCOT Compliance recommends review of expectations for generation-owned SPS components. Generation company ownership of SPS equipment is not recognized in official ERCOT approvals or in Operating Guides 7.2.2.(13).

## Slide 9: 10/3 Bryan area event
  Separate compliance report will be issued shortly
  Summary to date:
    Aspects of relaying arrangement at Gibbons Creek did not meet Operating Guides requirements for new substations but these facilities were “grandfathered”
    Generally ERCOT and TDSPs coordinated their grid management activities including load shed, with minor issues in communications and
    LaaR performance following manual deployment did not meet 10 minute criteria at 5 QSEs
    ERCOT met NERC DCS frequency recovery standard, and no NERC Interconnection Reliability Operating Limit (IROL – major transmission security) violations were identified.