## Slide 1: Q: What is the Unit’s Primary Fuel Type?
Note: 716 wind units with 1669.6 MW are excluded.
Primary Fuel | # of units | % of Units | MW Capacity
BITUMINOUS COAL | 7 | 1.73 | 3857.00
LANDFILL GAS | 5 | 1.23 | 33.00
LIGNITE | 14 | 3.46 | 8092.00
NATURAL GAS | 345 | 85.19 | 46658.70
No 2 Fuel Oil | 2 | 0.49 | 3.20
NUCLEAR | 4 | 0.99 | 4922.00
Pet Coke | 1 | 0.25 | 140.00
PURCHASED STEAM | 4 | 0.99 | 240.00
SUB-BITUMINOUS COAL | 4 | 0.99 | 1696.00
HYDRO | 19 | 4.69 | 380.00
Grand Total | 405 | 100.00 | 66021.90

## Slide 2
2004 ROS - What is the unit’s maximum net sustainable
limit when using its alternative fuel?
Alternate Fuel Registered Output Max. Net Sustainable Output
Distillate Fuel Oil 1 23,502 18,674
Residual Fuel Oil2 2,955 3,124
Other Gas3 757 710
Jet Fuel 164 150
Propane 80 77
Natural Gas 320 305
Total 27,777 MW 23,040 MW
Of the 150 dual fuel capable units:

## Slide 3
2004 ROS -Hours of Operation on current inventory

## Slide 4: Q: How many hours can the unit operate using your current inventory of alternative fuel, at its maximum sustainable capacity?
Of the 87 operational dual fuel capable units that responded:

## Slide 5: Trend
Assume the winter peak load is 48000MW.
Assume the natural gas curtailment is 50%.
Capacity Shortage
-332
11678
944
4481

## Slide 6: Analysis--example
Total capacity from natural gas: 46931.7MW
natural gas(34619.7)+dual fuel(12312)=46931.7
If the natural gas supply decrease 50%
The remain capacity from natural gas: 17309.85 MW (34619.7*(100%-50%))
The capacity of dual fuel can supply for the first 24 hours is: 12312 MW
The total system available capacity without wind/hydro is: 48332.05MW (natural gas(17309.85)+dual fuel(12312)+coal/lignite(13788.2)+nuclear(4922))