# ERCOT Operations Report for ROS & OWG

# November 2006

## Frequency Control Disturbance (Less than 59.9 Hz or higher than 60.1Hz)

| Disturbance Data |  |  |  |  |
| --- | --- | --- | --- | --- |
| Time | Frequency (Hz) | Duration (s) | Details | Notes |
| 11/13/2006 07:09 | 60.101 | 4 |  |  |
| 11/14/2006 06:31 | 59.799 | 96 | Unit trip. 900MW lost | PDC |
| 11/15/2006 04:38 | 59.793 | 48 | Unit trip. 725MW lost | PDC |
| 11/17/2006 17:01 | 60.101 | 4 |  |  |
| 11/30/2006 00:12 | 59.878 | 32 | Unit ran back around 460MW |  |

## Deployed Responsive (27) (Reported Above)

| Time of deployed | Duration (h:mm:ss) | Max Deployed (MW) |
| --- | --- | --- |
| 11/02/06 06:11 | 0:04:50 | 291.20 |
| 11/06/06 06:21 | 0:04:46 | 253.76 |
| 11/07/06 21:59 | 0:09:07 | 253.76 |
| 11/09/06 23:13 | 0:08:48 | 243.93 |
| 11/10/06 06:10 | 0:06:54 | 237.21 |
| 11/10/06 13:02 | 0:25:54 | 249.01 |
| 11/11/06 09:01 | 0:18:28 | 251.89 |
| 11/13/06 22:21 | 0:02:50 | 262.08 |
| 11/14/06 06:31 | 0:15:16 | 640.23 |
| 11/14/06 21:59 | 0:06:00 | 274.57 |
| 11/15/06 04:38 | 0:15:48 | 736.33 |
| 11/15/06 06:08 | 0:04:00 | 236.06 |
| 11/15/06 17:38 | 0:08:10 | 245.65 |
| 11/16/06 21:59 | 0:08:16 | 266.25 |
| 11/18/06 17:42 | 0:13:48 | 247.46 |
| 11/22/06 22:00 | 0:02:58 | 257.92 |
| 11/24/06 21:59 | 0:07:54 | 274.57 |
| 11/25/06 21:59 | 0:09:10 | 266.25 |
| 11/26/06 22:00 | 0:05:18 | 270.41 |
| 11/26/06 23:14 | 0:07:10 | 253.76 |
| 11/27/06 21:58 | 0:09:20 | 291.20 |
| 11/28/06 21:59 | 0:10:36 | 257.92 |
| 11/29/06 01:16 | 0:04:24 | 278.73 |
| 11/29/06 20:29 | 0:06:46 | 250.85 |
| 11/30/06 00:12 | 0:12:56 | 382.73 |
| 11/30/06 03:49 | 0:04:02 | 257.92 |
| 11/30/06 07:15 | 0:12:56 | 229.04 |

## Day-Ahead RMR and OOMC Capacity Purchases

| Historical Totals | Nov-05 | Oct-06 | Nov-06 |
| --- | --- | --- | --- |
| Austin | 0 | 3 | 19 |
| Bryan Area | 29 | 8 | 0 |
| Corpus | 8 | 20 | 0 |
| DFW | 8 | 16 | 3 |
| E RIO | 142 | 10 | 12 |
| Houston | 3 | 0 | 1 |
| Laredo | 42 | 80 | 66 |
| North | 10 | 2 | 1 |
| Northeast | 2 | 13 | 2 |
| San Antonio | 61 | 0 | 4 |
| South | 0 | 0 | 5 |
| W RIO | 39 | 97 | 80 |
| Western | 7 | 6 | 19 |
| Total | 351 | 255 | 212 |

| Nov 06 Data in detail | RMR | OOMC | Total |
| --- | --- | --- | --- |
| Austin | 0 | 19 | 19 |
| Bryan Area | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 |
| DFW | 0 | 3 | 3 |
| E RIO | 0 | 12 | 12 |
| Houston | 0 | 1 | 1 |
| Laredo | 66 | 0 | 66 |
| North | 0 | 1 | 1 |
| Northeast | 0 | 2 | 2 |
| San Antonio | 0 | 4 | 4 |
| South | 0 | 5 | 5 |
| W RIO | 0 | 80 | 80 |
| Western | 0 | 19 | 19 |
| Total | 66 | 146 | 212 |

## Yearly MTLF Error Comparison

| Month | MAPE for MTLF run at 16:00 Day Ahead (2005) | MAPE for MTLF run at 16:00 Day Ahead (2006) |
| --- | --- | --- |
| January | 5.02 | 4.79 |
| February | 3.47 | 4.81 |
| March | 3.41 | 4.95 |
| April | 3.37 | 5.59 |
| May | 4.21 | 3.59 |
| June | 3.91 | 2.65 |
| July | 5.22 | 2.62 |
| August | 4.86 | 2.09 |
| September | 6.24 | 4.03 |
| October | 4.51 | 3.63 |
| November | 4.53 | 3.28 |
| December | 5.95 | N/A |
| Average MAPE for Year | 4.56 | 3.82 |

## OOME / Congestion Management Activity:

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days of Occurrences |
| --- | --- | --- |
| Temple Pecan Creek - Tradinghouse & Lake Creek - Temple Switch 345kV | Lake Creek - Temple Pecan Creek 138kV | 11 |
| Menard - Gillespe 138 kV | Menard 138/69 kV | 11 |
| Fisher Rd - Oklaunion & Fisher Rd - Bowman 345kV | Vernon - Grayback 69kV | 10 |
| Temple Pecan Creek - Tradinghouse & Lake Creek - Temple Switch 345kV | Evant - Adamsville 138kV | 9 |
| Precontingency Overload | Bluff Creek 345/138 kV | 8 |
| Temple Pecan Creek - Tradinghouse & Lake Creek - Temple Switch 345kV | Goldthwaite 138/69 kv Auto | 5 |
| Comanche Peak - Decordova & Wolf Hollow - Rocky Creek 345kV | Concord 345/138kV Auto | 5 |
| Midland East - Odessa EHV 138kV | Odessa EHV Auto | 4 |
| Odessa EHV SW Auto T2 | Odessa EHV SW Auto T1 | 3 |
| STP-Dow 345 kV | Danevang - Danevang Distribution 69 kV | 3 |
| Midland East - Odessa EHV 345kV | Odessa EHV #1 345/138kV Auto | 3 |
| Midland East - Odessa EHV 345kV | Moss Switch - Odessa EHV 138kV | 2 |
| Lon Hill - North Edinburg 345 kV | Multiple valley area 138 kV lines | 2 |
| Temple Switch - Lake Creek & Temple Switch - Temple Pecan Creek 345kV | Temple Pecan Creek-Temple SW 138kV | 2 |
| Odessa EHV - Moss SW 138 kV | General Tire Switch - Olefin Switch 138 kV | 2 |
| Rio Hondo-North Edinburg 345 kV | Weslaco-Magic Valley 138 KV | 2 |
| STP Dow18 & STP Dow27 345kv | Flewellen - Peters 138 kV | 2 |
| Paris Switch- Valley and Paris Switch-Valley South 345 kV | Paris switch - Kimberly Clark 138 kV | 1 |
| Allen Switch-Royse Switch and Allen Switch-Monticello 345 kV | Centerville Rd switch-Garland Rd 138 kV | 1 |
| Asherton-West Batesville 138 kV | Derby-Pearsall 69 KV | 1 |
| Comanche Peak - Decordova & Wolf Hollow - Rocky Creek 345 kV | Goldthwaite 138/69 kV Auto | 1 |
| Marion_Hill country and Hill Country_STP 345 kV | Marion to Skyline 345 kV | 1 |
| Enterprise - Trinidad and Martin Lake - Stryker Creek 345kV | Nacogdoches SE 345/138kV Auto | 1 |
| Lon Hill - North Edinburg 345 kV | Dilley SW 138/69 kVAuto | 1 |
| STP - SkyLine & White Point 345kV | Blessing - Lolita 138kV | 1 |
| Coleto Creek to Victoria 138 kV | Other Coleto Creek to Victoria 138kV | 1 |
| STP to Dow 345 kV | Bay City to Sargent 69 kV | 1 |
| Zorn - Clear Springs & Marion 345kV | Seguin - Seguin West 138 kV | 1 |
| Price Road - Filter Plant 138 kV | Loma Alta 138/69kV Auto | 1 |
| Rio Hondo to Nelson Sharpe 345 kV | South McAllen to Las Milpas 138 kV | 1 |
| Trinidad-Stryker Creek & Trinidad-Mt. Enterprise | Nacogdoches Auto #1H | 1 |
| Marion-Clear Springs-Zorn 345 kV | Comal-Henne 138 kV | 1 |

## Zonal OC1’s

| CSC | Days |
| --- | --- |
| South - Houston | 22 |
| North - Houston | 0 |
| South - North | 0 |
| Northeast - North | 0 |
| West - North | 0 |
| North - West | 0 |

## New RAPs

None

## New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 11/30/2006 | Transmission & Security Desk - V3R78 | 301 |
| 11/30/2006 | Frequency Control Desk - V3R45 | 300 |

## Blackout/Load Shed incidences

None

## Major system voltage problems

None

## Voltage Instructions

None

## Major Computer Problems, Enhancements & Fixes

One interval, 10:45 RTB, missed due to portal connections slowing the database 11/14/06

Two intervals lost,13:00 & 1315 RTB ,due to Operator entering a value that was too large (8 digits long) , cycled importer / exporter

0 minutes AGC Control lost

Database Loads: 11/8/2006, 11/21/2006

## Communication

None

## ERCOT peak (Unofficial)

11/30/2006	18:46	46106MW

## Other

None.

## OCN, Advisory, Alerts, and Emergency Notices

| Date | Start | End | Subject | Details |
| --- | --- | --- | --- | --- |
| 11/1/2006 | 5:10 | 20:15 | Advisory | Advisory Adjusted Responsive Reserve less than 3000 MW |
| 11/2/2006 | 6:12 |  |  | Deployed 290 MW of Responsive Reserve due to low frequency. Large Schedule changes and slow responding units. |
| 11/4/2006 | 2:20 |  | Advisory | Advisory Adjusted Responsive Reserve at 2893 MW |
| 11/4/2006 | 9:05 | 13:30 | Alert | Alert Adjusted Responsive Reserve less than 2500 MW |
| 11/5/2006 | 0:15 | 1:00 | Advisory | Advisory Adjusted Responsive Reserve less than 3000 MW. |
| 11/5/2006 | 11:45 | 22:45 | Advisory | Advisory Adjusted Responsive Reserve less than 3000 MW. |
| 11/5/2006 | 18:23 | 22:45 | Alert | Alert Adjusted Responsive Reserve less than 2500 MW |
| 11/5/2006 | 18:55 | 23:00 | OCN | OCN issued due to insufficient balancing up bids for hours ending 2100 and 2300. |
| 11/6/2006 | 1:20 | 20:25 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000MW. |
| 11/6/2006 | 6:21 | 6:22 |  | Frequency spiked to 59.911Hz. Deployed 254 MW of Responsive Reserve Service. Frequency spiked due to load growth and slow unit response. ERCOT load 29336. |
| 11/6/2006 | 7:48 | 8:30 | OCN | OCN for capacity shortage for hours 18:00 through 20:00. |
| 11/6/2006 | 8:00 | 8:30 | Alert | Alert - Adjustment Period Replacement Reserve Market opened for hours 12:00 to 24:00. |
| 11/6/2006 | 9:40 | 12:20 | Alert | Alert - Adjusted Responsive Reserve is less than 2500MW. |
| 11/7/2006 | 5:02 | 7:55 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000MW. |
| 11/7/2006 | 12:05 | 19:45 | Advisory | Advisory - Adjusted Responsive Reserve less than 3000MW. |
| 11/7/2006 | 22:00 | 22:05 |  | Responsive Reserve deployed 253 mw at 59.91 Hz due to 22:00 schedule changes and large SCEs. |
| 11/8/2006 | 9:20 | 10:08 |  | ERCOT performed a data base load. |
| 11/8/2006 | 10:05 | 24:00 | Advisory | Weather Advisory due to high pressure dominating Texas and temperatures forecasted 10 to 15 degrees higher than average. |
| 11/8/2006 | 12:00 | 24:00 | Transmission Emergency | Transmission Emergency for the Del Rio area due to the loss of Sonora - Hamilton Road 138kV. |
| 11/8/2006 | 14:00 | 24:00 |  | Scheduled 30 mw from CFE into ERCOT across Eagle Pass HVDC tie due to outages in Del Rio area. |
| 11/9/2006 | 0:15 | 24:00 | Advisory | Weather Advisory due to high pressure domintaing Texas and temperatures forecasted 10 to 15 degrees higher than average. |
| 11/9/2006 | 0:00 | 0:36 | Transmission Emergency | Transmission Emergency for the Del Rio area due to the loss of Sonora - Hamilton Road 138kV. |
| 11/9/2006 | 12:58 | 19:30 | Advisory | Advisory due to Adjusted Responsive below 3000MW. |
| 11/9/2006 | 10:45 | 24:00 |  | South to Houston CSC limit change to 1050MW per ERCOT engineering. |
| 11/9/2006 | 14:15 | 19:15 | Transmission Alert | Transmission Alert for the loss of South Texas Project - Skyline and South Texas Project - Whitepoint 345kV overloads Blessing - Lolita 138kV beyond first contingency limits with no market solution. |
| 11/9/2006 | 23:13 | 23:22 |  | Deployed 243 mw Responsive Reserve at 59.91 Hz due to schedule changes and SCEs. |
| 11/10/2006 | 4:00 | 15:00 | Advisory | Advisory due to Adjusted Responsive below 3000MW. |
| 11/10/2006 | 6:10 | 6:17 |  | Deployed 243 mw Responsive Reserve at 59.91 Hz due to schedule changes for 0700. Also the steel mills deployed at 150MW continuing to drive frequency down. |
| 11/10/2006 | 10:30 | 15:00 | Advisory | Alert issued due to Adjusted Responsive below 2500MW |
| 11/10/2006 | 13:02 | 13:26 |  | Deployed 249mws of RRS due to frequency sagging to 59.905. Due to schedule change across the top of the hour causing depletion of URS. RRS recalled to 22mws at 13:13. Total RRS recalled to 0 at 13:26. |
| 11/10/2006 | 10:45 | 21:30 | Transmission Emergency | Transmission Emergency for the Del Rio area due to the loss of Sonora - Hamilton Road 138kV. |
| 11/10/2006 | 10:45 | 23:15 | Transmission Emergency | Transmission Emergency issued for Temple area due to post contingency loss of 345kv double ckt Temple Pecan Creek-Trading House and Temple Switch - Lake Creek. |
| 11/11/2006 | 1:19 | 5:20 | Advisory | Advisory issued due to Adjusted Responsive below 3000MW. |
| 11/11/2006 | 9:14 | 12:10 | Advisory | Advisory issued due to Adjusted Responsive below 3000MW |
| 11/11/2006 | 9:01 | 9:19 |  | Responsive Reserve Deployed 251mws due to XXXX trip of 443mws. Frequency dropped to 59.904 and recovered to 60.00 at 09:08. Total recall of RRS at 09:19. System load at time of trip was 28838. |
| 11/12/2006 | 19:20 | 23:45 | Advisory | Advisory issued due to Adjusted Responsive below 3000MW. |
| 11/13/2006 | 10:10 | 17:05 | Advisory | Advisory issued due to Adjusted Responsive below 3000MW. |
| 11/13/2006 | 17:47 | 23:13 | Advisory | Advisory issued due to Adjusted Responsive below 3000MW. |
| 11/14/2006 | 6:31 |  |  | Tripped XXXX with 854mw frequency went to 59.799Hz back to 60Hz in 3min. |
| 11/14/2006 | 7:12 | 21:25 | Advisory | Advisory issued for Adjusted Responsive under 3000mw. |
| 11/14/2006 | 10:10 |  |  | EMMS site failover from Taylor to Austin. |
| 11/14/2006 | 10:30 | 11:00 |  | Balancing Energy deployments 10:30 held for 10:45 due to MOI down during site failover. |
| 11/14/2006 | 12:00 | 23:00 |  | Emergency Notice 30mw in across South DC Tie. |
| 11/14/2006 | 21:59 | 22:05 |  | Responsive Reserve Deployed with 232MW due to schedule change at 2200 and DC Tie mismatch of -400MW. FHZ went to 59.909. Load at 32748. |
| 11/15/2006 | 4:38 | 4:54 |  | Responsive Reserve Deployed with 736 MW due to trip on XXXX (loss of 725MW) Laars deployed. FHZ dropped to 59.793. |
| 11/15/2006 | 0:25 | 15:00 | Advisory | Advisory issued for Adjusted Responsive under 3000mw. |
| 11/15/2006 | 17:38 | 17:46 |  | Responsive Reserve Deployed at 245MW due to sharp load pick-up and depletion of regulation up. FHZ dropped to 59.903 |
| 11/15/2006 | 17:28 | 21:56 | Advisory | Advisory issued for Adjusted Responsive under 3000mw. |
| 11/15/2006 | 18:00 | 21:56 | Alert | Alert called for Responsive Reserve below 2500. |
| 11/15/2006 | 22:14 |  | Advisory | Advisory issued for Adjusted Responsive under 3000mw. |
| 11/16/2006 | 7:15 | 10:04 | Alert | Alert called for Responsive Reserve below 2500. |
| 11/16/2006 | 21:59 | 10:07 |  | Deployed 266 MW of Responsive Reserve. Freq. dropped to 59.91 due to QSE base power schedules changes. |
| 11/16/2006 | 18:21 | 22:51 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/16/2006 | 21:00 | 23:57 | Transmission Alert | Alert issued for the post contingency loss of the Menard-Gillespie 138kv line overloading the Menard 138/69kv Auto to 131% of 46MVA rating. |
| 11/17/2006 | 5:39 | 9:17 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/17/2006 | 23:10 | 24:00 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/18/2006 | 0:15 | 14:52 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/18/2006 | 17:42 | 17:56 |  | Deployed 248 MW of Responsive Reserve due to low frequency. Lighting Load pickup with slow unit response. |
| 11/18/2006 | 18:05 | 24:00 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/19/2006 | 0:15 | 6:34 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/19/2006 | 18:25 | 24:00 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/20/2006 | 0:15 | 6:00 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/21/2006 | 3:30 | 10:15 | Advisory | Advisory issued for Adjusted Responsive Reserve below 3000. |
| 11/21/2006 | 9:20 | 10:30 |  | ERCOT planned Data Base Load completed. |
| 11/22/2006 | 22:00 | 22:03 |  | Deployed 258 MW of Responsive Reserve. Frequency dropped to 59.908 Hz due to QSE base power schedule changes and slow unit response. ERCOT load 29418 MW. |
| 11/23/2006 | 9:00 | 13:45 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 11/24/2006 | 21:59 | 22:07 |  | Deployed 275 MW of Responsive Reserve. Frequency spiked to 59.909Hz due to QSE base power schedules changes. ERCOT load 28000. |
| 11/24/2006 | 170:00:00 |  | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 11/25/2006 | 17:40 | 23:12 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 11/25/2006 | 21:59 | 22:08 |  | Deployed 266 MW of Responsive Reserve. Frequency spiked to 59.906Hz due to QSE base power schedules changes. ERCOT load 28338. |
| 11/26/2006 | 17:31 | 22:52 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000MW. |
| 11/26/2006 | 22:00 | 22:06 |  | Deployed 270 MW of Responsive Reserve. Frequency spiked to 59.905Hz due to QSE base power schedules changes. ERCOT load 29531. |
| 11/26/2006 | 23:14 | 23:21 |  | Deployed 254 MW of Responsive Reserve. Frequency spiked to 59.909Hz due to a unit run back and steel mill ramping up. ERCOT load 26650. |
| 11/27/2006 | 12:45 |  |  | Held Interval 12:45 until 13:30 due to an incorrect entry in the South - Houston OC1. |
| 11/27/2006 | 18:24 | 23:12 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000MW. |
| 11/27/2006 | 21:58 | 22:07 |  | Deployed 291 MW of Responsive Reserve. Frequency spiked to 59.900Hz due to QSE base power schedules changes. ERCOT load 31908. |
| 11/28/2006 | 16:00 | 21:00 | Transmission Emergency | Transmission Emergency for the Del Rio area with loss of the Hamilton Rd to Sonora 138 kv line. 30 MW Schedule started with AEP for the South DC Tie. |
| 11/28/2006 | 9:47 | 15:08 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000MW. |
| 11/28/2006 | 13:30 | 24:00 | Weather Advisory | Weather Advisory issued for Thursday November 30, Friday December 1 and Saturday December 2. |
| 11/28/2006 | 21:59 | 22:07 |  | Deployed 291 MW of Responsive Reserve. Frequency spiked to 59.900Hz due to QSE base power schedules changes and slow unit response. ERCOT load 32900 |
| 11/29/2006 | 0:15 | 24:00 | Weather Advisory | Weather Advisory issued for Thursday November 30, Friday December 1 and Saturday December 2. |
| 11/29/2006 | 21:59 | 22:07 |  | Deployed 291 MW of Responsive Reserve. Frequency spiked to 59.900Hz due to non conforming load pick up and slow unit response. ERCOT load 26000 |
| 11/29/2006 | 0:43 | 13:03 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000MW. |
| 11/29/2006 | 20:29 | 20:32 |  | Deployed 260 MW of Responsive Reserve. Frequency spiked to 59.900Hz due to loss of 360 MW of generation at XXXX plant. ERCOT load 36200 MW |
| 11/30/2006 | 0:15 | 24:00 | Weather Advisory | Weather Advisory issued for Thursday November 30, Friday December 1 and Saturday December 2. |
| 11/30/2006 | 0:12 | 0:16 |  | Deployed 382 MW of Responsive Reserve. Frequency spiked to 59.878 due to XXXX running back 450 MW. ERCOT load 28250 MW |
| 11/30/2006 | 3:50 | 3:53 |  | Deployed 130 MW of Responsive Reserve. Frequency spiked to 59.908Hz due to loss of 190 MW of generation at XXXX. ERCOT load 27200 MW |
| 11/30/2006 | 7:15 | 7:28 |  | Deployed 229 MW of Responsive Reserve. Frequency spiked to 59.903 due to generation schedule change. ERCOT load 37070 |
| 11/30/2006 | 13:45 | 24:00 | Transmission Emergency | Transmission Emergency for the Del Rio Area |
| 11/30/2006 | 17:50 | 22:59 | Advisory | Advisory issued due to Adjusted Responsive Reserve below 3000MW. |