| OGRR Number | 189 | OGRR Title | Administrative Changes for January 1, 2007 Operating Guides |
| --- | --- | --- | --- |
| Status | Administrative Change |
| Operating Guide Section Requiring Revision | 4.5, Emergency Electric Curtailment Plan (EECP) |
| Revision Description | Administrative change to maintain Operating Guide consistency with Protocols as allowed by Operating Guide Section 1.3, Process for Operating Guide Revision. |
| Reason for Revision | PRR682, EECP Event Realignment has modified a Protocol Section that is referenced in the Operating Guides. This OGRR updates that reference. |
| Timeline |
| Date Posted | 12/12/06 |

| Sponsor |
| --- |
| Name | Ann Boren |
| E-mail Address | aboren@ercot.com |
| Company | ERCOT |
| Company Address | 7620 Metro Center Dr, Austin TX 78744 |
| Phone Number | 512-275-7411 |

Proposed Operating Guide Language Revision

## 4.5	Emergency Electric Curtailment Plan (EECP)

Reference:  Protocols Section 5.6.6.1, Emergency Electric Curtailment Plan (EECP), Section 5.6.7, EECP STEPS, and 5.6.7.1, Restoration of Market Operations

5.6.6.1	Emergency Electric Curtailment Plan (EECP)

At times it may be necessary to reduce electrical demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing demand during such emergencies, ERCOT will initiate and coordinate the implementation of the Emergency Electric Curtailment Plan following the EECP Steps set forth below in subsection 5.6.7, EECP Steps.

The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.

ERCOT’s operating procedures shall meet the following goals while continuing to respect the confidentiality of market sensitive data:

- Use of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT system;

- Use of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

- Maximum use of ERCOT System capability;

- Maintenance of station service for nuclear Generation Resource Facilities;

- Securing of startup power for Generation Resources;

- Operation of power Generation Resources during loss of communication with ERCOT;

- Restoration of service to critical Loads in the manner defined in the Operating Guides; and

- Restoration of service to all customers following major system disturbances, giving priority to the larger groups of customers.

ERCOT shall be responsible for coordinating with QSEs and TDSPs to monitor system conditions, initiating the EECP steps, notifying all QSEs, and coordinating the implementation of the EECP Steps while maintaining transmission security limits.

ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation.

During the EECP, ERCOT has the authority to obtain energy over the DC Ties when transmission capacity is available across the DC Tie.  ERCOT will not supercede any market use of the DC Ties.

[PRR543: Replace the paragraph above with the following upon ERCOT Legal review of the Comision Federal de Electricidad contract:] During the EECP, ERCOT has the authority to obtain energy from BtB Ties or Block Load Transfers (BLTs) from non-ERCOT Control Areas when capacity is available.

Some of the EECP Steps will not be applicable if transmission security violations exist. There may be insufficient time to implement all Steps in sequence, but to the extent practicable, ERCOT will use Ancillary Services which bidders have made available in the market to maintain or restore reliability.

ERCOT may immediately implement Step 3 of the EECP any time the steady-state system frequency is below 59.8 Hz and will immediately implement Step 3 any time the steady-state frequency is below 59.5 Hz.

Percentages for Step 3 Load shedding will be based on previous year’s TDSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

5.6.7	EECP STEPS

Step 1 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal to 2300 MW.

ERCOT will:

(1)	Utilize available DC tie capability that is not already being used by the market;

(2)	 Notify the Southwest Power Pool Security Coordinator; and

(3)	Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency.

[PRR543: Add the following bullet upon ERCOT Legal review of the Comision Federal de Electricidad contract:] (4) Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers.

QSEs will:

(1)  	Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency.

Step 2 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW Provided from LaaR Equal to 1750 MW.

In addition to measures associated with Step 1, ERCOT will:

(1)	Instruct TDSPs to reduce Customers load by using distribution voltage reduction measures, if deemed beneficial by the TDSP;

(2)	Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (controlled by high-set under-frequency relays);

(3)	With the approval of the affected Non-ERCOT control area, may instruct TDSPs to implement BLTs, which transfer load from the ERCOT control area to Non-ERCOT control areas.  Use of a BLT will be defined in the ERCOT Operating Guides; and

(4)	Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation.

Step 3 — Maintain system frequency at 59.8 Hz or greater

In addition to measures associated with Steps 1 and 2, ERCOT will direct all TDSPs and their agents to shed firm load, in 100 MW blocks, distributed as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hz.

In addition to measures associate with Steps 1 and 2, TDSPs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan.

5.6.7.1	Restoration of Market Operations

ERCOT shall continue EECP until sufficient bids are received and deployed by ERCOT to eliminate the conditions requiring the EECP.