| NPRR Number | 019 | NPRR Title | Black Start Testing Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approval |
| Nodal Protocol Section(s) Requiring Revision |  | 8.1.2.2.6, System Black Start Capability |  |  |
| Effective Date |  | Upon Texas Nodal Market implementation. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This PRR specifies the requirements for testing the Black Start Resource and which tests are allowed to be run simultaneously. |  |  |
| Overall Market Benefit |  | This NPRR documents ERCOT's practice of conducting Black Start Resource tests when new Black Start Resources are selected. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | None. |  |  |
| Credit Impacts: Has the Credit Workgroup reviewed the PRR? If so, are there credit impacts? (indicate Yes or No, and if Yes, include a summary of impact) |  | TBD |  |  |
| Procedural History |  | - On 08/23/06, NPRR019 was posted. - On 08/28/06, ERCOT posted the Impact Analysis (IA). - On 09/19/06, ERCOT Comments were posted. - On 09/21/06, PRS considered this NPRR. - On 11/16/06, PRS reconsidered this NPRR. - On 12/01/06, TAC considered this NPRR. - On 12/12/06, the ERCOT Board considered this NPRR. |  |  |
| PRS Recommendation |  | On 09/21/06, PRS unanimously voted to table NPRR019 until the Transition Plan Task Force (TPTF) reviewed the proposed language and ERCOT’s comments. All Market Segments were present for the vote. On 11/16/06, PRS unanimously voted to recommend approval of NPRR019 with ERCOT’s comments. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | There was no discussion on 9/21/06. On 11/16/06, ERCOT Staff reported that TPTF had reviewed NPRR019 and ERCOT’s comments and had voiced no objections. |  |  |
| TAC Recommendation |  | On 12/01/06, TAC voted to recommend approval of NPRR019 as recommended by PRS. There were two abstentions from the Consumer Segment. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | No discussion. |  |  |
| Board Action |  | On 12/12/06, the Board voted to approve NPRR019 as recommended by TAC. All Market Segments were present for the vote. |  |  |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 | NPRR documents current practices. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | None | None |
|  | 2 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 |  |  |
|  | 2 |  |  |
| Additional Qualitative Information | 1 | Clearly defines Black Start testing practices |  |
|  | 2 |  |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | David Wood on behalf of Black Start Task Force |
| E-mail Address | david.wood@austinenergy.com |
| Company | Austin Energy |
| Segment |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| 091906 ERCOT | Clarify the Black Start testing process and provide more detail regarding disqualification and decertification of Black Start Resources. |

Proposed Nodal Protocol Language Revision

8.1.2.2.6	System Black Start Capability

(1)	A Resource is qualified to be a Black Start Resource if it has met the following requirements:

(a)	Verified control communication path performance;

(b)	Verified primary and alternate voice circuits for receipt of instructions;

(c)	Passed the “Basic Starting Test” as defined below;

(d)	Passed the “Line-Energizing Test” as defined below;

(e)	Passed the “Load-Carrying Test” as defined below;

(f) 	Passed the “Next Start Resource Test” as defined below;

(g)	If not starting itself, has an ERCOT-approved firm standby power contract with deliverability under ERCOT blackout circumstances from a provider not inside the ERCOT Interconnection that can be finalized upon selection as a Black Start Resource;

(h)	If not starting itself, has an ERCOT approved agreement with the necessary TDSPs for access to another power pool, for coordination of switching during a black-start event, for coordination of maintenance through the ERCOT Outage scheduler for all non-redundant transmission startup feeds; and

(i)	If dependent upon non-ERCOT transmission resources, agreements providing this Transmission Service have been provided in the proposal.

(2)	On successful demonstration of system Black Start Service capability, ERCOT shall certify that the Black Start Resource is capable of providing system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource.  Qualification shall be valid for the time frames set forth below.  Except under extenuating circumstances, as reasonably determined by ERCOT, all qualification testing for the next year of Black Start Service must be completed by December 1 of each year.  ERCOT shall revoke the  Qualification of a Black Start Resource and reduce the Black Start Resources’ Hourly Standby Fee (if under an existing Black Start Agreement) to zero during the time of disqualification if the Black Start Resource fails to perform successfully duringa test described herein, until the Black Start Resource is successfully retested.  ERCOT may limit the number of retests allowed.  Retesting is required only for the aspect of system Black Start Service capability for which the Black Start Resource failed.  If a Black Start Resource under an existing Black Start Agreement does not successfully re-qualify within two months of failing a test described herein, ERCOT shall decertify the Black Start Resource for the remainder of the calendar year as described in Section 7 of the “Standard Form Black Start Agreement.” The following tests are required for Black Start Service qualification:

(a)	The “Basic Starting Test” includes the following:

(i)	The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another provider not inside the ERCOT Interconnection, without support from the ERCOT System;

(ii)	Annual testing, either as a stand-alone test or part of the Line Energizing and Load Carrying Tests, and the test is preformed during a one-week period agreed to in advance by the Black Start Resource and ERCOT and must not cause outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market;

(iii)	Confirmation of the dates of the test with the Black Start Resource by ERCOT;

(iv)	Initiation of the test at a time during a previously agreed test week window not previously disclosed to the Black Start Resource;

(v)	Isolation of the Black Start Resource, including all auxiliary Loads, from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT Interconnection if the startup power is supplied by a firm standby contract.  Black Start Resources starting with the assistance of a non-ERCOT Control Areae ERCOT Interconnection through a firm standby agreement will connect to the non-ERCOT Control Areaprovider not inside thn, start-up, carry internal Load, disconnect from the non-ERCOT Control Areaprovider not inside the ERCOT Interconnectiough a black-start capable DC Tie, and continue equivalently to what is required of other Black Start Resources;

(vi)	The ability of the Black Start Resource to start without assistance from the ERCOT System, except for the transmission that connects the Resource to a provider not inside the ERCOT Interconnection if the startup power is supplied by a firm standby contract;

(vii)	The ability of the Black Start Resource to remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least 30 minutes; and

(viii)	The Black Start Resource must have verified that its Volts/Hz relay, over-excitation limiter, and under-excitation limiter are set properly and that no protection devices will trip the Black Start Resource within the required reactive range. The Resource Entity for the Black Start Resource shall provide ERCOT with data to verify these settings.

(ix) 	Qualification under the Basic Starting Test is valid for one (1)  year.

(b)	The “Line-Energizing Test” must be conducted at a time agreed on by the Black Start Resource, TSP or DSP, and ERCOT and includes the following:

(i)	Energizing transmission with the Black Start Resource when conditions permit as determined by the TSP or DSP but at least once every three years;

(ii)	De-energizing sufficient transmission in such manner that when energized by the Black Start Resource it demonstrates the Black Start Resource’s ability to energize enough transmission to deliver to the Loads the Resource’s output that ERCOT’s restoration plan requires the Black Start Resource to supply.  ERCOT shall be responsible for transmission connections and operations that are compatible with the capabilities of the Black Start Resource;

(iii)	Conducting a Basic Starting Test;

(iv)	Energizing transmission with the Black Start Resource of the previously de-energized transmission, while monitoring frequency and voltages at both ends of the line.  Alternatively, if ERCOT agrees, the transmission line may be connected to the Black Start Resource before starting, allowing the Resource to energize the line as it comes up to speed; and

(v)	Stable operation of the Black Start Resource (in both frequency and voltage) while supplying only its auxiliary Loads or external Loads for at least 30 minutes.

(vi)	This test may be performed together with the Basic Starting Test in one thirty (30) minute interval.

(viii)	Qualification under the Line-Energizing Test is valid for three (3) years.

(c)	The “Load-Carrying Test”  shall be tested as conditions permit, but at least once every six years and includes the following:

(i)	Stable operation of the Black Start Resource (in both frequency and voltage) while supplying restoration power to Load specified by ERCOT’s restoration plan for the Black Start Resource.

(ii)	Conducting a Basic Starting Test;

(iii)	Conducting a Line-Energizing Test; and

(iv)	The TSP or DSP operator for the Black Start Resource shall direct picking up sufficient Load to demonstrate the Black Start Resource’s capability to supply the required power identified in ERCOT’s restoration plan, while maintaining voltage and frequency for at least 30 minutes.

(v)	This test may be performed together with the Basic Starting Test and Line Energizing test in one thirty (30) minute interval.

(vi)	Qualification under the Load- Carrying Test is valid for six (6) years.

(d)	Next Start Resource Test:

(i)	The ability of a Black Start Resource to start up the Next Start unit’s largest required motor while continuing to remain stable and control voltage and frequency shall be tested. This test shall be repeated when a new next start unit is selected;

(ii) 	To pass the test, (a) the potential Black Start Resource must start the next start unit (as determined by ERCOT), or start the next start unit’s largest required motor and satisfied the next start unit’s minimum startup Load requirements; or (b) the Resource Entity shall demonstrate to the satisfaction of ERCOT staff through simulation studies conducted by the Resource Entity or a qualified third party, that the potential Black Start Resource is capable of starting the next start unit’s largest required motor while meeting the next start unit’s minimum startup Load requirements.  Potential Black Start Service bidders may request next start unit information from ERCOT prior to the selection process to satisfy this requirement.  ERCOT shall request this information from the designated next start unit as follows:  ERCOT may require any Generation Resource to provide largest motor startup information and unit startup energy requirements as needed to validate Black Start proposals or plans submitted by other Generation Resources.  Such data, if requested by ERCOT, shall be provided by the QSE representing the Generation Resource or the Generation Resource Entity to ERCOT within thirty (30) days. Such information shall be considered Protected Information by the requesting Resource Entity when provided to the Resource Entity.

(ii)	If a physical test is performed, the test shall commence with a Basic Starting Test, followed by

a Line Energizing Test and

a Load Carrying Test as a stand-alone test or part of the Next Start Resource Test

(iii)	If a physical test is performed, the Black Start Resource must remain stable (in both voltage and frequency) and controlling voltage for thirty (30) minutes

(vi)	If a physical test is performed, this test may be performed together with the Basic Starting Test, Line Energizing Test, and Load Carrying Test in one thirty (30) minute interval.

(v)	Qualification under the Next Start Resource Test is valid until a new next start unit is selected.

(3)	ERCOT shall decertify a Black Start Resource for the calendar year if the Black Start Resource fails to perform successfully during an actual ERCOT System blackout event and the Black Start Resource has been declared available, as defined in Section 9B(1) of Section 22, Attachment A, Standard Form Black Start Agreement.