Texas Nodal

Energy Management System

Requirements Specification

For SCADA

Version 0.90

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 12/01/2006 | 0.90 | These requirements were developed through an iterative process and reviewed by various ERCOT teams, including Nodal EMS team, Nodal IDA team, ERCOT Operations and IT Support teams, as well as EMS vendor. | Nodal EMS Team |

Table of Contents

1.	Introduction	6

1.1	Purpose	6

1.2	Objectives	6

1.3	Scope	6

1.4	Traceability	7

2.	Supervisory Control and Data Acquisition (SCADA)	8

2.1	Proposed System Scope	8

2.2	System and Software Description	8

2.2.1	Conceptual Hardware Configuration	9

2.2.2	Standard SCADA functionality for Processing Telemetry Input	10

2.2.3	Additional SCADA functionality for Processing Telemetry Input	10

3.	Functional Requirements	11

3.1	Base SCADA Functions	11

3.2	Inputs to SCADA	15

3.3	Output Data to QSEs	16

3.4	Other Functionality	17

4.	Supplementary Requirements	21

5.	Protocol Coverage	24

6.	Data Elements to be Exchanged	26

6.1	QSE Data Exchange	26

6.1.1	Data Sent to QSEs	26

6.1.2	Data Received from QSEs	27

6.2	TDSP Data Exchange	29

6.3	Data Available to All Market Participants	31

This page is intentionally left blank.

Requirements Specification

This Requirements Document is Subordinate To and Compliant with the Texas Nodal Protocols Effective May 2006.

# Introduction

The requirements for Texas Nodal market implementation are described in the Texas Nodal Protocols.  This document focuses on elaborating the requirements for Supervisory Control and Data Acquisition (SCADA) of the Energy Management System.

This Requirements Specification is a part of the complete set of specification documents for the Texas Nodal market implementation.  For implementation purposes the Texas Nodal market functions are categorized into multiple systems based on clear distinction in functionality.  The Energy Management System is one of these systems.

The EMS requirements are documented in the Texas Nodal EMS Requirements Specification document; supplemented by the following Requirements Specifications:

- Texas Nodal EMS Data Model Requirements Specification

- Texas Nodal EMS SCADA Requirements Specification

- Texas Nodal EMS Dynamic Ratings Requirements Specification

- Texas Nodal EMS Forced Outage Detection Requirements Specification

- Texas Nodal EMS Generation Sub-system Requirements Specification

- Texas Nodal EMS Load Forecasting Requirements Specification

- Texas Nodal EMS Wind Power Forecasting Requirements Specification

- Texas Nodal EMS State Estimator Requirements Specification

- Texas Nodal EMS Network Security and Stability Analysis Requirements Specification

- Texas Nodal EMS Voltage Support Requirements Specification

- Texas Nodal EMS Outage Evaluation Requirements Specification

The definitions and acronyms from Section 2 of the Protocols are used in this document as applicable.  Any additional definitions and acronyms are defined in the Texas Nodal EMS Requirements Specification as needed.

## Purpose

The primary purpose of this requirements specification document is to fully describe the external behavior of the SCADA.  It also describes nonfunctional requirements, design constraints, and other factors necessary to provide a complete and comprehensive description of the requirements necessary to design and develop the corresponding software systems.

## Objectives

The objective of this requirements specification is to:

- Specify mutually exclusive and collectively exhaustive set of requirements for SCADA

- Ensure that requirements are in compliance with the Nodal Protocols

- Ensure that requirements are traceable to Nodal Protocols, NERC, FERC and any other applicable standards

## Scope

The scope of this document is to elicit requirements for SCADA to be in compliance with the Nodal Protocols published in May 2006, NERC, FERC and PUCT guidelines.  However, elaborating requirements that would change the intent of the protocols or proposing a design for the system is outside the scope of this document.  To ensure compliance the designers and developers of the systems are required to read and understand the Nodal Protocols.

Any scope changes to this requirements specification due to alternate design proposals must be driven by Nodal Protocol Revision Request (NPRR) and channeled through Nodal Change Control Board (CCB).  Any scope changes to this requirements specification due to further elaboration, while still being in compliance with Nodal Protocols, must be channeled through Nodal CCB.

## Traceability

All SCADA requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents.  In addition all requirements are traceable to the Functional Diagram that describes SCADA.

These requirements are based off of May 2006 version Nodal Protocols and NERC, FERC, PUCT requirements approved as of May 2006.

# Supervisory Control and Data Acquisition (SCADA)

Supervisory Control and Data Acquisition (SCADA) is a sub-system of the Energy management System (EMS).  It consists of several subsystems which transfer, display and control data between the ERCOT member systems and ERCOT in accordance with ERCOT nodal protocols, PUCT rules and  NERC standards.  Its primary function is serving as the dispatching and telemetry interface to QSEs and TSPs.

SCADA data will be used as inputs to the State Estimator application, Alarming application, Load Frequency Control, Security Constrained Economic Dispatch, the Dynamic Ratings Subsystem, Network Security Analysis, and Reliability Unit Commitment (RUC).  Additionally, some elements of SCADA must be made available on the MIS to Market Participants.

All future telemetry for both SCADA inputs and outputs must be provided from and to QSEs and TSPs using ICCP.  ERCOT currently monitors approximately 20,000 analog measurements, and 28,000 status measurements.  It is expected that compliance with nodal protocols will require the expansion of SCADA telemetered points to over 200,000 analog measurements and 160,000 status measurements.

ERCOT currently sends approximately 700 analog values using SCADA.  This number will increase to approximately 6900 analog values, after implementing the zonal market change to send dynamic ratings to the market participants, before Texas Nodal.  With Texas Nodal, ERCOT will initially be sending approximately 7900 analog values.

## Proposed System Scope

This document provides information to assist the SCADA provider in understanding the requirements for SCADA and is intended to supplement the Nodal Protocols.  In case of conflict, the protocols govern. The requirements in scope for this document include:

- TSP input data (including breaker status, switch status, dynamic ratings along with temperature and weather zone information, Block Load Transfer data) and associated quality codes for each input.

- QSE input data (including Resource Status) and associated quality codes.

- ERCOT data override capability and appropriate setting of quality codes.

- Outputs to QSEs (outputs from LFC).

- Alarming including status change detection, high and low limit monitoring, return to normal, and message categorization to facilitate routing of alarms to assignable work functions.

- Stale data detection

- Database modifications

- Inputs from WGR entities (data written to SCADA database.) These inputs include meteorological information telemetered from Wind Generation Resource (WGR) Entities.

- SCADA calculations (including hourly meteorological data)

## System and Software Description

This section presents ERCOT’s general requirements for the SCADA hardware configuration and provides a high level description the software functionality required. Detailed functional requirements are set forth in Sections 3 and 4.

### Conceptual Hardware Configuration

Figure 1 - Conceptual Hardware Configuration

As shown in Figure 1, the SCADA ICCP communication function will be provided by four ICCP servers at each of ERCOT’s two control centers. One server pair will provide ICCP communication with TSPs while the other pair will provide ICCP communication with QSEs. Each server pair provides redundancy for failover functions.

Two Time Receivers are included in the configuration at each ERCOT control center to provide Frequency and Time Error values to applications. SCADA will provide functionality to read all four Time Receivers and place the frequency and time error values in the real-time database.

Figure 2 - SCADA Functional Block Diagram

### Standard SCADA functionality for Processing Telemetry Input

SCADA’s primary functionality is to receive real-time and operational data from TDSPs and QSEs, and send AGC-related control signals to QSEs via ICCP data links. SCADA is the primary link between the EMS’s front end interface to outside entities and the real-time database.

The SCADA application will receive both status and analog data via ICCP, manually entered data, and data from external processes.  For the purposes of this document, communication services are considered as part of SCADA.  When an analog measurement is received; SCADA will check data against reasonability limits, check time receipt for identification of stale data, check measurements against limits, send alarms to operators, and save data into the real-time database for use by other applications.  When a status measurement is received, SCADA checks the new state against the previous state, and alarms operators if a status change is noted; SCADA also supports basic calculations.

### Additional SCADA functionality for Processing Telemetry Input

Required functions that may not be provided in the standard SCADA functionality are detailed in Sections 3 and 4 of this document.

# Functional Requirements

## Base SCADA Functions

| Requirement ID | SCD-FR16 |
| --- | --- |
| Requirement Name | Data Acquisition |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Telemetered data shall be collected from the computer systems of participant utilities connected to the ERCOT WAN. These systems use the IEC 870-6-503 TASE.2 protocol (ICCP). In addition to telemetered data, the SCADA system shall support the following data: - Non-telemetered data entered by the user including scheduled data from entities without computer systems. - Calculated data generated by programs that periodically and aperiodically produce database values. Programs that are part of the data acquisition function and other EMS application functions will generate calculated data. - Dynamic ratings data for all the real-time processes This data may be of any type, including analog, status, and accumulator data. All requirements pertaining to telemetered data, such as limit monitoring, state change detection, enabling and inhibiting alarms, and quality codes, shall also apply to non-telemetered and calculated data. All data acquired from any source shall be identically processed, as described in this clause, and stored in the database. Once processed and stored in the database, a data item from any source, including a calculated value or a non-telemetered value, shall be indistinguishable from any other data item from any other source. |  |

| Requirement ID | SCD-FR17 |
| --- | --- |
| Requirement Name | Status Data Processing |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Prior to storage in the database, status data shall be processed to convert the input data to a physical state, and to identify and report changes in state. |  |

| Requirement ID | SCD-FR18 |
| --- | --- |
| Requirement Name | Analog Data Processing |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: For measured values, multiple pairs of limits (high limit, low limit) shall be supported that allow increasing levels of severity to be defined. At least three pairs of limits shall be provided. The system shall also support reasonability limits and rate-of-change limits. |  |

| Requirement ID | SCD-FR25 |
| --- | --- |
| Requirement Name | SCADA Calculation Tool |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: An on-line calculation definition tool shall be provided that allows user defined calculations to be entered into the system. Once defined, the calculation shall be immediately available for execution. Calculations shall provide, as a minimum, the following features: Basic add, subtract, multiply, divide, square root, exponentiation, and logarithms, etc. If-Then-Else blocks. Comparison of values (<, =, >, ≠, etc.) Logical operations (AND, OR, NOT, etc.) Trigonometric functions (SIN, COS, TAN, Arc functions, Hyperbolic functions, etc.) Any type of data from the real-time database shall be supported, including measured values, accumulated values, and status indications. A calculation group shall support combined use of the various data types. For example, it shall be possible to use both status indications and measured values in the same calculation. |  |

| Requirement ID | SCD-FR19 |
| --- | --- |
| Requirement Name | Calculated Data |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: Calculated points shall be derived from pre-defined algorithms supplied with the SCADA system. This Requirements Document assumes that calculations will be performed periodically and that the periodicity of calculations will be assigned on a per-point basis. An implementation that triggers a calculation whenever any of the arguments of the calculation change is also acceptable. The data type of the calculation result characterizes each calculated point. The calculation function shall detect arithmetic exceptions such as division by zero and over-range results. Such conditions shall be managed as telemetry failures. |  |

| Requirement ID | SCD-FR20 |
| --- | --- |
| Requirement Name | Calculated Data Quality Codes |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: The quality of the calculated value shall be the quality of the input data point with the most severe quality code. Results of calculations that are manually overridden by users shall be denoted with a quality code that can be differentiated from the propagation of a manual entry quality code from one its component values. |  |

| Requirement ID | SCD-FR21 |
| --- | --- |
| Requirement Name | Redundant Data Processing |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Selected values in the SCADA database may be obtained from more than one source, including telemetered, calculated values, or values generated by other applications. For each multiple-source value, all of the source values (referred to as arguments) will be stored in the database including their quality codes and the source that was being used as the primary source. Redundant data processing shall produce another database value and store the resultant in the database. The resultant and its arguments shall be of the same data type (analog, status, or accumulator), except that it shall be possible to substitute an analog value for an accumulator value. The resultant value will typically be used as the “best available” representation of the value for use in displays, reports, and functions. |  |

| Requirement ID | SCD-FR22 |
| --- | --- |
| Requirement Name | Tagging |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Database values shall be tagged to call the users’ attention to exception conditions for field devices and to inhibit supervisory control actions. It shall be possible to apply a tag to any database point. The SCADA system shall support at least eight tag types. It shall be possible to place any number of tags of any type on a point. As part of the tag placement process, the SCADA system shall prompt the user to enter alphanumeric comment information to be stored with the tag. The comment field shall be at least sixty characters in length. It shall be possible to modify the tag comment information. Tags shall be individually removed by user command. Each tag placement and removal shall be recorded as an event. |  |

| Requirement ID | SCD-FR23 |
| --- | --- |
| Requirement Name | Supervisory Control |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Future |
| Sub-Process Element Coverage | Partial |
| Description: Although the SCADA system is not envisioned to be performing supervisory control of devices, the capability to control devices shall be provided. Basic control functions required are: - Two and three-State Control (switching devices) - Setpoint control - Control Completion Check |  |

| Requirement ID | SCD-FR24 |
| --- | --- |
| Requirement Name | ICCP |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Data exchanges shall use the IEC 870-6-503 TASE.2 communications protocol. The SCADA system shall be fully compliant with the protocol Version 2000-04, Conformance Blocks 1,2, and 4. |  |

## Inputs to SCADA

| Requirement ID | SCD-FR1 |
| --- | --- |
| Requirement Name | Input data from TDSPs |
| Protocol Reference | Section(s) (see Section 6.2 of this document) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive available telemetry from TDSPs for use by Network Applications. Data from TDSPs is described in detail in Section 6.2, TDSP Data Exchange. |  |

| Requirement ID | SCD-FR2 |
| --- | --- |
| Requirement Name | Input Data from QSEs |
| Protocol Reference | Section(s) (see Section 6.1.2 of this document) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive resource-related telemetry from QSEs. Data received from QSEs is described in detail in Section 6.1.2, Data Received from QSEs. |  |

| Requirement ID | SCD-FR3 |
| --- | --- |
| Requirement Name | BLT Calculations |
| Protocol Reference | Section(s): 6.5.9.5 (i) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate the net interchange for each Block Load Transfer Point. |  |

| Requirement ID | SCD-FR4 |
| --- | --- |
| Requirement Name | Weather Zone Load Calculations |
| Protocol Reference | Section(s): 3.12.1 (2) b; 3.12.2 (2) b |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate the load (generation minus net interchange) within each weather zone. |  |

| Requirement ID | SCD-FR5 |
| --- | --- |
| Requirement Name | WGR Meteorological Telemetry |
| Protocol Reference | Section(s): 3.13 (1) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate hourly average meteorological data (wind speed and temperature) for each WGR based on the telemetered meteorological data from each WGR. |  |

| Requirement ID | SCD-FR6 |
| --- | --- |
| Requirement Name | MVA Calculation |
| Protocol Reference | Section(s): 6.5.7.1.13 (1) (a) (ii) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate MVA for each MW/MVAR pair received for all lines, transformers, and reactors. GP&L Comment: Generally Reactors do not have a MW reading from which MVA can be calculated. |  |

## Output Data to QSEs

| Requirement ID | SCD-FR7 |
| --- | --- |
| Requirement Name | SCED/LFC Outputs to QSEs |
| Protocol Reference | Section(s) (see Section 6.1.1 of this document) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Generation Control Output Processor |
| Sub-Process Element Coverage | Full |
| Description: LFC produces a list of data items unique to each QSE to be sent to the respective QSEs every 4 seconds. The content of the list will vary depending on the execution cycle times of the various AGC applications. SCADA shall send the list of data to each respective QSE using either the Set Data Set Element Values or Set Data Value service of ICCP. Every value in the list shall have quality attributes applied. (Note that ERCOT must proactively write generation, regulation and other AGC-related signals to QSEs, so the “SET…” functions of ICCP Conformance Block 1 are required.) Values to be written shall be grouped together for each QSE and associated with a time stamp that is also written to the QSE. The time stamp shall indicate the time the group of values was written to the QSE. Refer to Section 6.1.1, Data Sent to QSEs, for details on AGC-related data sent to QSEs, and the Nodal Protocol references associated with each data item. |  |

## Other Functionality

| Requirement ID | SCD-FR8 |
| --- | --- |
| Requirement Name | Data Availability Statistics |
| Protocol Reference | Sections 8.1 (3)(c); 8.3 (1)(b); Telemetry Standards |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide availability statistics on a point by point basis and on an TSP and QSE aggregated basis. EMS displays shall be provided to show hourly, daily, monthly, and quarterly availability statistics on a point by point basis and on an aggregated basis. Each of these displays shall have sorting and filtering tabs Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR9 |
| --- | --- |
| Requirement Name | Summary Displays and Tables |
| Protocol Reference | Section 6.5.7.1.13 (3) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide a summary display for each of the following: - Suspect status points - Suspect analog points - Stale points - Manual disabled points - Manual override points - Abnormal breaker and switch status - Limit violations - Base Points Each of these displays shall have sorting and filtering tabs. All summary tables shall be archived. GP&L Comment: Please map the above points to the quality codes in FR14 for clarification |  |

| Requirement ID | SCD-FR10 |
| --- | --- |
| Requirement Name | ICCP Link Availability Statistics |
| Protocol Reference | Section(s) 8.1 (3)(c)(ii) and 8.3 (1)(b)(ii) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Communication Availability Monitor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide ICCP link availability statistics. EMS displays shall be provided to show hourly, daily, and monthly availability statistics for each ICCP link. Availability statistics shall exclude planned outages. Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR11 |
| --- | --- |
| Requirement Name | Critical Data Availability Statistics |
| Protocol Reference | Sections 8.1 (3);8.3 (1), Telemetry Standard |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: ERCOT shall uniquely identify critical data points and provide separate availability statistics on a point by point basis and on an aggregated basis. EMS displays shall be provided to show hourly, daily, monthly, and quarterly availability statistics on a point by point basis and on an aggregated basis. Each of these displays shall have sorting and filtering tabs. Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR12 |
| --- | --- |
| Requirement Name | Stale Data Processing |
| Protocol Reference | Section(s): 6.5.7.1.13(a) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Market participants will associate every telemetered value transferred via ICCP with a time stamp having at least a 1 second resolution. SCADA shall use the time stamp to determine if the value received is “stale”. Each point in the real-time database shall have an attribute indicating whether “stale” data processing is to be applied to the value, and the number of seconds elapsed (the “stale time” attribute) before the value is considered to be “stale”. A second attribute shall be associated with every point indicating whether the value is or is not stale. For points designated to have “stale” processing applied, the received value’s time stamp shall be compared with the current system time to determine whether the value has exceeded its “stale time” attribute. Values exceeding “stale time” shall be marked “stale”. Values not exceeding “stale time” shall be marked “not stale”. GP&L Comment: concerned about the items listed in the ERCOT Note below as well as processing requirements on MP end - understand the 1 second time stamp is just the real time value of time at the time of sending the data – has nothing to do with the time of any type of event impacting the values quality flag – is this correct? Note: ERCOT intends that the vendor assess the impact of this requirement on the processing requirements including any conflicts with reporting by exception or non-telemetered data being exchanged via ICCP. |  |

| Requirement ID | SCD-FR13 |
| --- | --- |
| Requirement Name | Manual Override |
| Protocol Reference | Section(s) 6.5.7.1.5 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Manual Entry Processor |
| Sub-Process Element Coverage | Partial |
| Description: There shall be the capability for the ERCOT operators to override SCADA telemetry from one-line diagrams and station tabular displays to correct erroneous breaker and switch status before that information is processed by the Network Security Analysis for the next SCED interval. |  |

| Requirement ID | SCD-FR14 |
| --- | --- |
| Requirement Name | ICCP Quality code processing |
| Protocol Reference | Section(s): 3.10.7.4 (3) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor; Manual Entry Processor |
| Sub-Process Element Coverage | Partial |
| Description: Per the TAC approved Telemetry Standards Document, SCADA shall process the following quality codes associated with ICCP status and analog data: - Valid – represents analog or status the market participant considers valid - Manual – represents a analog or status entered manually at the market participant (not received from the field electronically) - Suspect - Represents a analog or status in which the market participant is unsure of the validity - Invalid – Represents an analog or status, which the market participant has identified as out of reasonability limits. - Com_fail – informs ERCOT that due to communications failure, the analog or status provided ERCOT is not current SCADA shall produce alarms for any change in quality code as well as return to valid alarms. SCADA shall convert data condition codes from each TDSP and QSE in a consistent manner for all applicable ERCOT applications. GP&L Comment: ERCOT & the Market Participants (MP’s) will need to discuss the conversion or mapping of MP’s ICCP quality codes as there are more (at least in some systems) codes in the MP’s system than the above 5 and they are not necessarily converted on a 1 to 1 basis. There needs to be reconciliation between the above definitions and the definitions in the MP’s system to both ERCOT & the MP’s agreement. |  |

| Requirement ID | SCD-FR15 |
| --- | --- |
| Requirement Name | Failover Performance |
| Protocol Reference | Section(s): 3.10.7.4 (4)(a) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | Telemetry Input Processor; Generation Control Output Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA failover time shall not exceed five minutes. |  |

# Supplementary Requirements

| Requirement ID | SCD-SR1 |
| --- | --- |
| Requirement Name | SCADA Processing |
| Requirement Type | Performance |
| Description: SCADA shall perform all data processing within the applicable scan interval according to the following processing times: - 2-second data: 1 second - 4-second data: 1 second - 10-second data: 5 seconds - 5-minute data: 30 seconds - 10-minute data: 30 seconds - 60-minute data: 60 seconds Processing shall include data conversion (if necessary), reasonability checks, limit checks, initiation of logging and alarming, storage in the real-time database, and activation of external processes where applicable. |  |

| Requirement ID | SCD-SR2 |
| --- | --- |
| Requirement Name | Data Availability |
| Requirement Type | System and Communication |
| Description: SCADA shall monitor the availability of ICCP links. The cumulative availability in percentage shall be calculated for each hour, day and month. SCADA shall alarm if the availability falls below the pre-set monthly threshold. Availability thresholds shall be configurable by ERCOT Analysts. Initially these thresholds shall be configured as follows: - TDSP ICCP links shall achieve a monthly availability of ninety-eight (98%) percent, excluding approved planned outages. - QSE ICCP links shall achieve a monthly availability of ninety-nine point ninety-nine (99.99%) percent, excluding approved planned outages. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data. A link will be considered as available when at least the predefined percent (configurable by an ERCOT Analyst and initially set to eighty-five (85%)) of the data defined on that link is successfully transferred to ERCOT with a valid or manual quality code. The current and previous month’s availability data shall be stored in EMS database and shall be viewable through EMS user interface. |  |

| Requirement ID | SCD-SR3 |
| --- | --- |
| Requirement Name | No degradation in performance |
| Requirement Type | Performance |
| Description: There shall be no degradation in the performance of ERCOT systems as a result of the SCADA functions execution under full volume processing. |  |

| Requirement ID | SCD-SR4 |
| --- | --- |
| Requirement Name | Interface to ERCOT Custom Applications |
| Requirement Type | SCADA Application Interfaces |
| Description: SCADA shall interface to existing ERCOT custom applications (such as RTMONI) in the new system. (Please note that our current load forecast is dependent upon RTMONI calculations to support the weather zone calculations.) |  |

| Requirement ID | SCD-SR5 |
| --- | --- |
| Requirement Name | Online User Documentation and Help System Requirements |
| Requirement Type | Training and Documentation |
| Description: User and operator software messages shall be formatted in plain English and generated at the application level for each application and not at the OEM software level (ORACLE, UNIX, etc.) Online help shall be context sensitive. User documentation shall be made available for online access. |  |

| Requirement ID | SCD-SR6 |
| --- | --- |
| Requirement Name | Database Sizing |
| Requirement Type | System and Communication |
| Description: The SCADA application shall be sized to process the data sizing specified in Section 6 of this document. |  |

| Requirement ID | SCD-SR8 |
| --- | --- |
| Requirement Name | Standard SCADA functionality |
| Requirement Type | General |
| Description: SCADA shall include the following components: Data acquisition and transfer, supervisory control, topology system, tagging and notes, on-line editor, Inter-Process Communication Routines, short term history files and support, routines for mapping telemetered data to EMS applications, long term historical data recording support, user defined calculations, loadshed routines, methods for providing current time and system frequency, logging of SCADA activities, status of SCADA applications, user and configuration, maintenance, and support displays. |  |

| Requirement ID | SCD-SR9 |
| --- | --- |
| Requirement Name | Frequency Inputs |
| Requirement Type | Frequency Processing |
| Description: SCADA shall receive frequency measurements from Time receivers located at Austin and Taylor sites. Four time receivers will be provided with the system. Two time receivers will be located at Taylor and two at Austin. The SCADA process at each location shall read frequency and time error from all four time receivers and store the four Frequency and Time Error values in the real-time database. |  |

| Requirement ID | SCD-SR10 |
| --- | --- |
| Requirement Name | Database Modification |
| Requirement Type | Database Maintenance |
| Description: The SCADA function shall provide on-line editing tools and screens to allow an EMS Analysts to add, remove, and edit data points telemetered from QSEs and TDSPs. |  |

| Requirement ID | SCD-SR11 |
| --- | --- |
| Requirement Name | Process Redundant Links |
| Protocol Reference | System and Communication |
| Description: Communication between ERCOT and market participants is provided by redundant communication links. One link traverses ERCOT’s Frame Relay network, and the other link traverses ERCOT’s DACS network. The DACS network acts as a backup to the Frame Relay network. If communication with a market participant is lost on the primary link, SCADA shall automatically establish (or otherwise activate) communication over the backup link. |  |

# Protocol Coverage

The following table summarizes the coverage extent (Full/Partial) of all relevant Nodal Protocols that are mentioned in this requirements document.

| Protocol Sub-Section | Section title | Coverage by Requirements (Full/Partial) | Covered by Requirement |
| --- | --- | --- | --- |
| 3.6 | Load Participation | Partial | SCD-FR2 |
| 3.10.7.2 (3) | Modeling of Resources and Transmission Loads | Partial | SCD-FR1 |
| 3.10.7.4 | Telemetry Criteria | Partial | SCD-FR16 Thru SCD-FR24 |
| 3.10.7.4 (2) | Telemetry Criteria | Partial | SCD-FR1 |
| 3.10.7.4 (3) | Telemetry Criteria | Partial | SCD-FR14 |
| 3.10.7.4 (4)(a) | Telemetry Criteria | Partial | SCD-FR15 |
| 3.10.8 (2) a | Dynamic Ratings | Partial | SCD-FR1 |
| 3.10.8.1 (1) | Dynamic Ratings Delivered via ICCP | Full | SCD-FR1 |
| 3.10.8.2 (2) | Dynamic Ratings Delivered via ICCP | Full | SCD-FR1 |
| 3.12.1 (2) b | Mid-Term Load Forecast | Partial | SCD-FR4 |
| 3.12.2 (2) b | Long-Term Load Forecast | Partial | SCD-FR4 |
| 3.13 (1) | Renewable Production Potential Forecasts | Partial | SCD-FR5 |
| 4.2.2 (1) | Wind-Powered Generation Resource Production Potential | Partial | SCD-FR2 |
| 4.2.2 (2) | Wind-Powered Generation Resource Production Potential | Partial | SCD-FR2 |
| 6.3.2 (2) | Activities for Real-Time Operations | Partial | SCD-FR7 |
| 6.4.5 (1) | Resource Status | Partial | SCD-FR2 |
| 6.5.5.1 (1) | Operational Data Requirements | Partial | SCD-FR2 |
| 6.5.5.2 (2) | Operational Data Requirements | Full | SCD-FR2 |
| 6.5.5.2 (4) | Operational Data Requirements | Full | SCD-FR2 |
| 6.5.5.2 (6) | Operational Data Requirements | Full | SCD-FR2 |
| 6.5.5.2 (8) b | Operational Data Requirements | Partial | SCD-FR2 |
| 6.5.5.2 (8) c | Operational Data Requirements | Partial | SCD-FR2 |
| 6.5.7.1.1 | SCADA Telemetry | Partial | SCD-FR13 |
| 6.5.7.1.5 | Topology Consistency Analyzer / Override | Partial | SCD-FR13 |
| 6.5.7.1.7 (1) | Real-Time Weather and Dynamic Rating Processor | Partial | SCD-FR1 |
| 6.5.7.1.13 (1) (a) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Full | SCD-FR1 SCD-FR6 SCD-FR12 |
| 6.5.7.1.13 (1) (d) (ii) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Full | SCD-FR2 |
| 6.5.7.1.13 (1) (e) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Full | SCD-FR1 |
| 6.5.7.1.13 (3) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Partial | SCD-FR9 |
| 6.5.7.2 | Resource Limit Calculator | Partial |  |
| 6.5.7.3 | Security Constrained Economic Dispatch | Partial |  |
| 6.5.7.4 (1) | Base Points | Partial | SCD-FR7 |
| 6.5.7.5 (1) | Ancillary Services Capacity Monitor | Partial | Section 6.3 |
| 6.5.7.6.1 (3) | LFC Process Description | Partial | SCD-FR2 |
| 6.5.7.6.1 (4) | LFC Process Description | Partial | SCD-FR2 |
| 6.5.7.6.1 (8) j | LFC Process Description | Partial | SCD-FR2 |
| 6.5.7.6.1 (9) | LFC Process Description | Partial | SCD-FR7 |
| 6.5.7.6.2.1 (8) | Deployment of Regulation Service | Partial | SCD-FR7 |
| 6.5.7.6.2.2 (11) | Deployment of Responsive Reserve Service | Partial | SCD-FR7 |
| 6.5.7.6.2.2 (12) | Deployment of Responsive Reserve Service | Partial | SCD-FR7 |
| 6.5.7.6.2.3 (4) | Non-Spinning Reserve Service Deployment | Partial | SCD-FR7 |
| 6.5.9 (1) | Emergency Operations | Partial | SCD-FR7 |
| 6.5.9.5 (i) | Block Load Transfers between ERCOT and Non-ERCOT Control Areas | Full | SCD-FR3 SCD-FR1 |
| 8.1 (3) (c) | QSE/Resource Performance Monitoring and Compliance | Full | SCD-FR8 SCD-FR10 SCD-FR11 |
| 8.3 (1) (b) | TSP Performance Monitoring and Compliance | Partial | SCD-FR8 SCD-FR10 SCD-FR11 |
| 11.1.11 (3) | Treatment of EPS RID Data | Partial | SR8 |
| 11.6.2.1 | Sub-divide ERCOT into a practical granularity of “UFE Analysis Zones,” but no more than ten (10) zones, which can provide reliable and accurate data to be used for Cost/Benefit Analysis and decision making purposes | Partial | SR8 |
| 11.6.3 | Data Collection and Metering Requirements For UFE Analysis Zones | Partial | SR8 |

# Data Elements to be Exchanged

The tables below specify the data exchange requirements known as of the May 2006 protocols. The data includes information specifically identified in the protocols, and other data presently exchanged and/or expected to be needed to support operation under the TNP.

Data exchange undergoes continuous revision. The Operating Guides specify the official ERCOT data exchange requirements at any given point in time. Therefore, the tables below are intended as an initial guide to system sizing. The latest approved version of the Operating Guides supersede the information included here.

Anticipated maximum sizing parameters are:

Table 1 - Estimated Maximum Sizing Parameters

| Parameter | Quantity |
| --- | --- |
| Number of QSEs | 500 |
| Number of TDSPs | 100 |
| Number of Generation Resources | 2,000 |
| Number of Load Resources | 1,000 |
| Number of Busses | 24,000 |
| Number of Hubs | 200 |
| Number of Load Zones | 200 |
| Number of Generation Plants | 500 |
| Number of Autotransformers | 200 |
| Number of Reactors | 2,000 |
| Number of Capacitors | 2,000 |
| Number of Circuit Breakers | 35,000 |
| Number of Switches | 70,000 |
| Number of Weather Zones | 50 |
| Number of Transmission Lines | 20,000 |
| Number of Block Load Transfer Points | 20 |

## QSE Data Exchange

### Data Sent to QSEs

Table 2 - Per-QSE Data Sent to QSE

| Per-QSE Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Regulation MW | 4 | 6.5.7.6.2.1 (8) |
| RRS MW | 4 | 6.5.7.6.2.2 (11) |
| Non-Spin Dispatch Instruction (on/off) | 4 | 6.5.7.6.2.3 (4) |

Table 3 - Per- Generation Resource Data Sent to QSE

| Per-Generation Resource Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Generator Suspend Ramping to Base Point (on/off) | 4 | 6.5.7.6.1 (9) |
| Generator base point MW | 4 | 6.5.7.4 (1) b |
| Generator LMP | 4 | 6.3.2 (2) table |
| Generator BP above HASL due to RRS (on/off) | 4 | 6.5.7.4 (1) c |
| Pseudo unit dispatch (on/off) | 4 | 6.5.7.4 (1) e |
| Time of Dispatch | 4 | 6.5.7.4 (1) d |
| Other possible information (multiple values) | 4 | 6.5.7.4 (1) e |
| Emergency Basepoint (on/off) | 4 | 6.5.9 (1) |

Table 4 - Per-Bus Data Sent to QSE

| Per-Bus Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Hub or Load zone LMP | 4 | 6.3.2 (2) |

### Data Received from QSEs

Table 5 - Per-QSE Data Received from QSE

| Per-QSE Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Frequency (system) | 2 | 6.5.7.6.1 (3) |
| Any agreed-upon additional data Resource (multiple data items) | various | 6.5.5.2 (2) e 6.5.5.2 (4) b |

Table 6 - Per-Plant Data Received from QSE

| Per-Plant Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Plant auxiliary load | 10 | 6.5.5.2 (2) c |
| Switch status not monitored by TSP (possibly multiple switches) | RBE | 6.5.5.2 (2) d |

GP&L Question: Does “RBE” under “Frequency” in the above table mean “report by exception”?

Table 7 - Per-Generation Resource Data Received from QSE

| Per-Generation Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Combined Cycle config no. | 2 | 6.5.5.2 (8) b |
| Resource status | RBE | 6.4.5 (1) 6.5.5.1 (1) |
| Generation Resource MW value | 2 | 6.5.5.2 (2) a |
| Generation Resource Mvar | 10 | 6.5.5.2 (2) b |
| Generation Resource Breaker status | RBE | 6.5.5.2 (2) f |
| Generation Resource Hi Sustained Limit (HSL) | 2 | 6.4.5 (1) 6.5.5.2 (2) g 6.5.7.1.13 (1) (d) (ii) (B) |
| Generation Resource Lo Sustained Limit (LSL) | 2 | 6.4.5 (1) 6.5.5.2 (2) j 6.5.7.1.13 (1) (d) (ii) (C) |
| Generation Resource Hi Emergency Limit (HEL) | 2 | 6.5.5.2 (2) h |
| Generation Resource Lo Emergency Limit (LEL) | 2 | 6.5.5.2 (2) i |
| Text reason for any Resource where a Ramp Rate is deviating from a standard Ramp Rate curve for the Resource, or the HSL is less than, or LSL is greater than, the normal high and low limits set in protocol Section 3.7.1, Resource Parameter Criteria | 10 | 6.4.5 (1) |
| Generation Resource Reg-Up Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource Reg-Down Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource RRS Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource Non-Spin Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource Reg-Up participation factor | 2 | 6.5.5.2 (2) l |
| Generation Resource Reg-Down participation factor | 2 | 6.5.5.2 (2) l |
| Generation Resource RRS participation factor | 2 | 6.5.5.2 (2) l |
| Generation Resource Inhibit Reg-Up status | 2 | 6.5.5.2 (6) |
| Generation Resource Inhibit Reg-Down status | 2 | 6.5.5.2 (6) |
| Generation Resource Normal Ramp Rate | 2 | 6.4.5 (1) |
| Generation Resource Emergency Ramp Rate | 2 | 6.4.5 (1) |
| Generation Resource DSR Base Point | 2 | 6.5.7.6.1 (8) j |
| Generator Step-up transformers tap position | 10 | 6.5.7.1.13 (1) (d) (ii) (A) |

Table 8 - Per-Load Resource Data Received from QSE

| Per-Load Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Load Resource MW | 2 | 6.5.5.2 (4) a |
| Resource status | RBE | 6.4.5 (1) 6.5.5.1 (1) 6.5.5.2 (8) b 6.5.5.2 (8) c |
| Load Resource breaker status | RBE | 6.5.5.2 (4) c |
| Load Resource high-set under-frequency relay status (if RRS resource) | RBE | 6.5.5.2 (4) g |
| Load Resource Low Power Consumption (LPC) | 2 | 6.5.5.2 (4) d |
| Load Resource Maximum Power Consumption (MPC) | 2 | 6.5.5.2 (4) e |
| Load Resource Reg-Up Schedule | 2 | 3.6 (implied) |
| Load Resource Reg-Down Schedule | 2 | 3.6 (implied) |
| Load Resource RRS Schedule | 2 | 6.5.5.2 (4) f |
| Load Resource Non-Spin Schedule | 2 | 3.6 (implied) |
| Load Resource Reg-Up participation factor | 2 | 3.6 (implied) |
| Load Resource Reg-Down participation factor | 2 | 3.6 (implied) |
| Load Resource RRS participation factor | 2 | 3.6 (implied) |
| Load Resource Inhibit Reg-Up status | 2 | 3.6 (implied) |
| Load Resource Inhibit Reg-Down status | 2 | 3.6 (implied) |
| Load Resource NRAMP | 2 | 3.6 (implied) |
| Load Resource ERAMP | 2 | 3.6 (implied) |
| Load Resource DSR Output Schedule | 2 | 6.5.5.2 (2) e |

Table 9 - Per Wind Resource Data Received from QSE

| Per Wind Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Wind Speed | 10 | 6.5.7.1.13 (1) (e) 4.2.2 (1) (implied) |
| Wind Direction | 10 | 4.2.2 (1) (implied) |
| Temperature | 10 | 4.2.2 (1) (implied) |
| Barometric Pressure | 10 | 4.2.2 (1) (implied) |

## TDSP Data Exchange

Table 10 - Per-Buss Data Received from TDSP

| Per-Buss Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Buss Voltage kV | 10 | 6.5.7.1.13 (1) (a) (i) |

Table 11 - Per-Transformer Data Received from TDSP

| Per-Transformer Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Transformer Flow MW | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Transformer Flow Mvar | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Transformer Flow MVA (calculated) | 10 | 6.5.7.1.13 (1) (a) (ii) |
| LTC Tap Position | 10 | 6.5.7.1.13 (1) (a) (v) |

Table 12 - Per-Transmission Line Data Received from TDSP

| Per-Transmission Line Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Line Flow MW | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Line Flow Mvar | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Line Flow MVA (calculated) | 10 | 6.5.7.1.13 (1) (a) (ii) |

Table 13 - Per-Shunt (Inductive or Capacitive) Data Received from TDSP

| Per-Shunt (Inductive or Capacitive) Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Shunt Mvar | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Shunt Flow MVA (calculated) | 10 | 6.5.7.1.13 (1) (a) (ii) |

Table 14 - Per-Circuit Breaker Data Received from TDSP

| Per-Circuit Breaker Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Circuit Breaker MW flow | 10 | 3.10.7.4 (2) (implied) |
| Circuit Breaker Mvar | 10 | 3.10.7.4 (2) (implied) |
| Breaker Status (with normal status indicator) | RBE | 3.10.7.4 (2) (implied) 6.5.7.1.13 (1) (a) (iii) 6.5.7.1.13 (1) (a) (iv) |

Table 15 - Per-Load Data Received from TDSP

| Per-Switch Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Switch Status (with normal status indicator) | RBE | 3.10.7.4 (2) (implied) 6.5.7.1.13 (1) (a) (iv) 6.5.7.1.13 (1) (a) (iii) |

Table 16 - Per-Load Data Received from TDSP

| Per-Load Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Load in MW | 10 | 3.10.7.4 (2) (implied) |
| Load in Mvar | 10 | 3.10.7.4 (2) (implied) |

Table 17 - Per-DC Injection Point Data Received from TDSP

| Per-DC Injection Point Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| DC Injection in MW | 10 | 3.10.7.2 (3) |
| DC Injection in Mvar | 10 | 3.10.7.2 (3) |
| DC Tie Status | RBE | 3.10.7.2 (3) (implied) |

Table 18 - Per- Block Load Transfer Point Data Received from TDSP

| Per-Block Load Transfer Point Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Switching Device Status at BLT points | RBE | 6.5.9.5 (i) |
| BLT MW | 10 | 6.5.9.5(i) |
| BLT MVAR | 10 | 6.5.9.5(i) |

Table 19 - Per Weather Zone Tie Line Data Received from TDSP

| Per Weather Zone Tie Line Data Received from TDSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Temperature | 10 | 6.5.7.1.13 (1) (e) 6.5.7.1.7 (1) |
| Wind Speed (if available) | 10 | 6.5.7.1.13 (1) (e) 6.5.7.1.7 (1) |

Table 20 - Per Dynamic Rating Data Received from TDSP

GP&L Comment: Protocol  3.10.8.2(b) states “Each TSP may alternatively elect to provide ERCOT with a table of equipment rating versus temperature and a temperature values in Real-Time for each Weather Zone in which the Transmission Element is located”

| Per Dynamic Rating Data Received from TDSP | Frequency (min) | Nodal Protocol Reference |
| --- | --- | --- |
| Line ID | 10/RBE | 3.10.8.1 (1) (a) |
| From Status | 10/RBE | 3.10.8.1 (1) (b) |
| To Station | 10/RBE | 3.10.8.1 (1) (c) |
| Normal Rating | 10/RBE | 3.10.8.1 (1) (d) |
| Emergency Rating | 10/RBE | 3.10.8.1 (1) (d) |
| 15-Minute Rating | 10/RBE | 3.10.8.1 (1) (d) |

## Data Available to All Market Participants

Table 21 - Data Available for Reading by All Market Participants

| Data Available for Reading by Market Participants | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Responsive Reserve Capacity from Generation Resources GP&L Comment: believe “Available” should be inserted between Reserve & Capacity | 10 | 6.5.7.5 (1) a |
| Responsive Reserve Capacity from Load Resources GP&L Comment: believe “Available” should be inserted between Reserve & Capacity | 10 | 6.5.7.5 (1) b |
| Non-Spinning Reserve available from On-Line Generation Resources with Energy Offer Curves | 10 | 6.5.7.5 (1) c |
| Non-Spinning Reserve available from undeployed Load Resources | 10 | 6.5.7.5 (1) d |
| Non-Spinning Reserve available from Off-Line Generation Resources | 10 | 6.5.7.5 (1) e |
| Non-Spinning Reserve available from Resources with Output Schedules | 10 | 6.5.7.5 (1) f |
| Undeployed Reg-Up and undeployed Reg-Down | 10 | 6.5.7.5 (1) g |
| Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | 10 | 6.5.7.5 (1) h |
| Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | 10 | 6.5.7.5 (1) i |
| Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | 10 | 6.5.7.5 (1) j |
| Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | 10 | 6.5.7.5 (1) k |

Set Data Set Element Values and Set Data Value are standard ICCP services defined in IEC 870-6-503, TASE.2 Services and Protocol. These services are included in ICCP Conformance Block 1 which defines the minimum required functionality of ICCP. Set Data Set Element Values and Set Data Value services are specified here to make it clear that ERCOT will not send AGC-related services to QSEs using the Device Control services of ICCP Conformance Block 5. The Device Control services of ICCP are unacceptable because they do not support quality codes. TASE.2 is another name for ICCP.