Texas Nodal

Energy Management System

Requirements Specification

For SCADA

Version 0.90

Reliant Energy, Inc. comments – December 14, 2006

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 12/01/2006 | 0.90 | These requirements were developed through an iterative process and reviewed by various ERCOT teams, including Nodal EMS team, Nodal IDA team, ERCOT Operations and IT Support teams, as well as EMS vendor. | Nodal EMS Team |

Table of Contents

1.	Introduction	7

1.1	Purpose	7

1.2	Objectives	7

1.3	Scope	7

1.4	Traceability	8

2.	Supervisory Control and Data Acquisition (SCADA)	9

2.1	Proposed System Scope	9

2.2	System and Software Description	9

2.2.1	Conceptual Hardware Configuration	10

2.2.2	Standard SCADA functionality for Processing Telemetry Input	11

2.2.3	Additional SCADA functionality for Processing Telemetry Input	11

3.	Functional Requirements	12

3.1	Base SCADA Functions	12

3.2	Inputs to SCADA	16

3.3	Output Data to QSEs	17

3.4	Other Functionality	18

4.	Supplementary Requirements	22

5.	Protocol Coverage	25

6.	Data Elements to be Exchanged	27

6.1	QSE Data Exchange	27

6.1.1	Data Sent to QSEs	27

6.1.2	Data Received from QSEs	28

6.2	TSP Data Exchange	30

6.3	Data Available to All Market Participants	32

This page is intentionally left blank.

Requirements Specification

This Requirements Document is Subordinate To and Compliant with the Texas Nodal Protocols Effective May 2006.

# Introduction

The requirements for Texas Nodal market implementation are described in the Texas Nodal Protocols.  This document focuses on elaborating the requirements for Supervisory Control and Data Acquisition (SCADA) of the Energy Management System.

This Requirements Specification is a part of the complete set of specification documents for the Texas Nodal market implementation.  For implementation purposes the Texas Nodal market functions are categorized into multiple systems based on clear distinction in functionality.  The Energy Management System is one of these systems.

The EMS requirements are documented in the Texas Nodal EMS Requirements Specification document; supplemented by the following Requirements Specifications:

- Texas Nodal EMS Data Model Requirements Specification

- Texas Nodal EMS SCADA Requirements Specification

- Texas Nodal EMS Dynamic Ratings Requirements Specification

- Texas Nodal EMS Forced Outage Detection Requirements Specification

- Texas Nodal EMS Generation Sub-system Requirements Specification

- Texas Nodal EMS Load Forecasting Requirements Specification

- Texas Nodal EMS Wind Power Forecasting Requirements Specification

- Texas Nodal EMS State Estimator Requirements Specification

- Texas Nodal EMS Network Security and Stability Analysis Requirements Specification

- Texas Nodal EMS Voltage Support Requirements Specification

- Texas Nodal EMS Outage Evaluation Requirements Specification

The definitions and acronyms from Section 2 of the Protocols are used in this document as applicable.  Any additional definitions and acronyms are defined in the Texas Nodal EMS Requirements Specification as needed.

## Purpose

The primary purpose of this requirements specification document is to fully describe the external behavior of the SCADA.  It also describes nonfunctional requirements, design constraints, and other factors necessary to provide a complete and comprehensive description of the requirements necessary to design and develop the corresponding software systems.

## Objectives

The objective of this requirements specification is to:

- Specify mutually exclusive and collectively exhaustive set of requirements for SCADA

- Ensure that requirements are in compliance with the Nodal Protocols

- Ensure that requirements are traceable to Nodal Protocols, NERC, FERC and any other applicable standards

## Scope

The scope of this document is to elicit requirements for SCADA to be in compliance with the Nodal Protocols published in May 2006, NERC, FERC and PUCT guidelines.  However, elaborating requirements that would change the intent of the protocols or proposing a design for the system is outside the scope of this document.  To ensure compliance the designers and developers of the systems are required to read and understand the Nodal Protocols.

Any scope changes to this requirements specification due to alternate design proposals must be driven by Nodal Protocol Revision Request (NPRR) and channeled through Nodal Change Control Board (CCB).  Any scope changes to this requirements specification due to further elaboration, while still being in compliance with Nodal Protocols, must be channeled through Nodal CCB.

## Traceability

All SCADA requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents.  In addition all requirements are traceable to the Functional Diagram that describes SCADA.

These requirements are based off of May 2006 version Nodal Protocols and NERC, FERC, PUCT requirements approved as of May 2006.

# Supervisory Control and Data Acquisition (SCADA)

Supervisory Control and Data Acquisition (SCADA) is a sub-system of the Energy management System (EMS).  It consists of several subsystems which transfer, display and control data between the ERCOT member systems and ERCOT in accordance with ERCOT nodal protocols, PUCT rules and NERC standards.  Its primary function is serving as the dispatching and telemetry interface to QSEs and TSPs.

SCADA data will be used as inputs to ERCOT operator displays of SCADA data including one-line graphical displays of all SCADA data and summary displays as required, the State Estimator application, Alarming application, Load Frequency Control, Security Constrained Economic Dispatch, the Dynamic Ratings Subsystem, Network Security Analysis, and Reliability Unit Commitment (RUC).  Additionally, some elements of SCADA must be made available on the MIS to Market Participants.

All future telemetry for both SCADA inputs and outputs must be provided from and to QSEs and TSPs using ICCP.  ERCOT currently monitors approximately 20,000 analog measurements, and 28,000 status measurements.  It is expected that compliance with nodal protocols will require the expansion of SCADA telemetered points to over 200,000 analog measurements and 160,000 status measurements. This seems unrealistic. Does ERCOT have any studies to come up with this size?

ERCOT currently sends to QSEs approximately 700 analog values using SCADA.  This number will increase to approximately 6900 analog values, after implementing the zonal market change to send dynamic ratings to the market participants, before Texas Nodal ?? is this a requirement to send to TSPs or QSEs?.  With Texas Nodal, ERCOT will initially be sending approximately 7900 analog values. Does ERCOT have any studies to come up with this size?

## Proposed System Scope

This document provides information to assist the SCADA provider in understanding the requirements for SCADA and is intended to supplement the Nodal Protocols.  In case of conflict, the protocols govern. The requirements in scope for this document include:

- TSP input data (including breaker status, switch status, line flows, transformer taps, transformer flows, dynamic ratings along with temperature and weather zone information, Block Load Transfer data) and associated quality codes for each input. ( does ICCP specifications provide for a convention on flow direction? Is + flow into a bus and – flow out of a bus?  Are all QSEs and TSPs ICCP communications the same?  Should this specification require such??

- QSE input data to LFC and other applications (including Resource Status) and associated quality codes of each data element.

- ERCOT data Manual Replacement with ERCOT operator entries of data and appropriate setting of quality codes.

- Outputs to QSEs (outputs from LFC).

- Alarming including status change detection, high and low limit monitoring, return to normal, and message categorization to facilitate routing of alarms to assignable work functions. Does ERCOT alarm on MVA or MW?  You may not want to do both so that you can reduce the number of alarms.

- Summary displays of all data elements for each defined quality code showing the name of the SCADA point and a time and date stamp when the data element obtained the quality code.

- Stale data detection as established by ERCOT SCADA system loss of communication from a Market Participant

- Stale data detection as may be provided by a Market Participant to ERCOT indicating the Market Participant loss of communication with its field equipment.

- Database modifications??

- Inputs from WGR entities (data written to SCADA database.) These inputs include meteorological information telemetered from Wind Generation Resource (WGR) Entities.

- SCADA calculations (including hourly meteorological data)

## System and Software Description

This section presents ERCOT’s general requirements for the SCADA hardware configuration and provides a high level description the software functionality required. Detailed functional requirements are set forth in Sections 3 and 4.

### Conceptual Hardware Configuration

Figure 1 - Conceptual Hardware Configuration

As shown in Figure 1, the SCADA ICCP communication function will be provided by four ICCP servers at each of ERCOT’s two control centers. One server pair will provide ICCP communication with TSPs while the other pair will provide ICCP communication with QSEs. Each server pair provides redundancy for failover functions to meet the minimum failover time requirements of the protocols. Is the failover time performance specified in this document to meet protocol requirements?

Two Time Receivers are included in the configuration at each ERCOT control center to provide Frequency and Time Error values to applications. SCADA will provide functionality to read all four Time Receivers and place the frequency and time error values with appropriate quality codes in the real-time database.

Figure 2 - SCADA Functional Block Diagram

### Standard SCADA functionality for Processing Telemetry Input

SCADA’s primary functionality is to receive real-time and operational data from TSPs and QSEs, and send AGC-related control signals to QSEs via ICCP data links. SCADA is the primary link between the EMS’s front end interface to outside entities and the real-time database.

The SCADA application will receive both status and analog data and associated Market Participant quality codes via ICCP, ERCOT operator manually entered data, and data from external processes.  For the purposes of this document, communication services are considered as part of SCADA.  When an analog measurement is received; SCADA will check data against reasonability limits, check time receipt for identification of stale data, check measurements against limits, check data for Market Participant quality codes, send alarms and notices to ERCOT operators, summarize data elements for display by associated quality code, and save data into the real-time database for use by other applications.  When a status measurement is received, SCADA checks the new state against the previous state, and alarms operators if a status change is noted; SCADA also supports basic calculations.

### Additional SCADA functionality for Processing Telemetry Input

Required functions that may not be provided in the standard SCADA functionality are detailed in Sections 3 and 4 of this document.

# Functional Requirements

## Base SCADA Functions

| Requirement ID | SCD-FR16 |
| --- | --- |
| Requirement Name | Data Acquisition |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Telemetered data shall be collected from the computer systems of Market Participants connected to the ERCOT WAN. These systems use the IEC 870-6-503 TASE.2 protocol (ICCP). In addition to telemetered data, the SCADA system shall support the following data: - Non-telemetered data entered by the user including scheduled data from entities?? without computer systems.????? What protocol requires this? Is this a security problem? - Calculated data generated by programs that periodically and periodically produce database values. Programs that are part of the data acquisition function and other EMS application functions will generate calculated data. - Dynamic ratings data for all the real-time processes This data may be of any type, including analog, status, and accumulator data. All requirements pertaining to telemetered data, such as limit monitoring, state change detection, enabling and inhibiting alarms, and quality codes, shall also apply to non-telemetered and calculated data. All data acquired from any source shall be identically processed, as described in this clause, and stored in the database. Once processed and stored in the database, a data item from any source, including a calculated value or a non-telemetered value, shall be indistinguishable from any other data item from any other source. |  |

| Requirement ID | SCD-FR17 |
| --- | --- |
| Requirement Name | Status Data Processing |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Prior to storage in the database, status data shall be processed to convert the input data to a physical state, and to identify and report changes in state and update summary displays on detection of a change in a quality code |  |

| Requirement ID | SCD-FR18 |
| --- | --- |
| Requirement Name | Analog Data Processing |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: For measured values, multiple pairs of limits (high limit, low limit) shall be supported that allow increasing levels of severity to be defined. At least three pairs of limits shall be provided. If the limits are the same, the analog data processing system will alarm only once with the highest level of alarm. Alarm messages to ERCOT operators shall include the data base element name, the alarm type, the current analog value and the alarm threshold causing the alarm. The system shall also support reasonability limits and rate-of-change limits. |  |

| Requirement ID | SCD-FR25 |
| --- | --- |
| Requirement Name | SCADA Calculation Tool |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: An on-line calculation definition tool shall be provided that allows user defined calculations to be entered into the system. Once defined, the calculation shall be immediately available for execution. Calculations shall provide, as a minimum, the following features: Basic add, subtract, multiply, divide, square root, exponentiation, and logarithms, etc. If-Then-Else blocks. Comparison of values (<, =, >, ≠, etc.) Logical operations (AND, OR, NOT, etc.) Trigonometric functions (SIN, COS, TAN, Arc functions, Hyperbolic functions, etc.) Any type of data from the real-time database shall be supported, including measured values, accumulated values, and status indications. A calculation group shall support combined use of the various data types. For example, it shall be possible to use both status indications and measured values in the same calculation. |  |

| Requirement ID | SCD-FR19 |
| --- | --- |
| Requirement Name | Calculated Data |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: Calculated points shall be derived from pre-defined algorithms supplied with the SCADA system. This Requirements Document assumes that calculations will be performed periodically and that the periodicity of calculations mail be assigned on a per-point basis. An implementation that triggers a calculation whenever any of the arguments of the calculation change is acceptable. The data type of the calculation result characterizes each calculated point. The calculation function shall detect arithmetic exceptions such as division by zero and over-range results. Such conditions shall be managed as telemetry failures. |  |

| Requirement ID | SCD-FR20 |
| --- | --- |
| Requirement Name | Calculated Data Quality Codes |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: The quality code of the calculated value shall be the quality code of the input data point with the most severe quality. Results of calculations that are manually overridden by the ERCOT operator shall be denoted with a quality code that can be differentiated from the propagation of a manual entry quality code from one its component values. |  |

| Requirement ID | SCD-FR21 |
| --- | --- |
| Requirement Name | Redundant Data Processing |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Selected values in the SCADA database may be obtained from more than one source, including telemetered, calculated values, or values generated by other applications. For each multiple-source value, all of the source values (referred to as arguments) will be stored in the database including their quality codes and the source that was being used as the primary source. Redundant data processing shall produce another database value and store the resultant in the database. The resultant and its arguments shall be of the same data type (analog, status, or accumulator), except that it shall be possible to substitute an analog value for an accumulator value. The resultant value will typically be used as the “best available” representation of the value for use in displays, reports, and functions. |  |

| Requirement ID | SCD-FR22 |
| --- | --- |
| Requirement Name | Tagging |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Database values shall be tagged to call the users’ attention to exception conditions for field devices and to inhibit supervisory control actions. It shall be possible to apply a tag to any database point. The SCADA system shall support at least eight tag types. It shall be possible to place any number of tags of any type on a point. As part of the tag placement process, the SCADA system shall prompt the user to enter alphanumeric comment information to be stored with the tag. The comment field shall be at least sixty characters in length. It shall be possible to modify the tag comment information. Tags shall be individually removed by user command. Each tag placement and removal shall be recorded as an event. A summary display shall be made available to the ERCOT operator allowing the operator to view all tags by type on data elements showing the date and time the tag was entered and type of tag, and operator comment. |  |

| Requirement ID | SCD-FR23 |
| --- | --- |
| Requirement Name | Supervisory Control |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Future |
| Sub-Process Element Coverage | Partial |
| Description: Although the SCADA system is not envisioned to be performing supervisory control of devices, the capability to control devices shall be provided. Basic control functions required are: - Two and three-State Control (switching devices) - Set point control - Control Completion Check |  |

| Requirement ID | SCD-FR24 |
| --- | --- |
| Requirement Name | ICCP |
| Protocol Reference | Section(s): 3.10.7.4 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Data exchanges shall use the IEC 870-6-503 TASE.2 communications protocol. The SCADA system shall be fully compliant with the protocol Version 2000-04, Conformance Blocks 1,2, and 4. Do any of these specifications state the sign convention for transmission flows? |  |

## Inputs to SCADA

| Requirement ID | SCD-FR1 |
| --- | --- |
| Requirement Name | Input data from TSPs |
| Protocol Reference | Section(s) (see Section 6.2 of this document) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive available telemetry from TSPs for use by network applications. Data from TSPs is described in detail in Section 6.2, TSP Data Exchange. |  |

| Requirement ID | SCD-FR2 |
| --- | --- |
| Requirement Name | Input Data from QSEs |
| Protocol Reference | Section(s) (see Section 6.1.2 of this document) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall receive Resource-related telemetry from QSEs. Data received from QSEs is described in detail in Section 6.1.2, Data Received from QSEs. |  |

| Requirement ID | SCD-FR3 |
| --- | --- |
| Requirement Name | BLT Calculations |
| Protocol Reference | Section(s): 6.5.9.5 (i) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate the net interchange for each Block Load Transfer Point. Do we want to also calculate the actual flow between major areas of the ERCOT System, i.e. North to south, etc. for each “generic” flow constraint that is specified for use in ERCOT applications? |  |

| Requirement ID | SCD-FR4 |
| --- | --- |
| Requirement Name | Weather Zone Load Calculations |
| Protocol Reference | Section(s): 3.12.1 (2) b; 3.12.2 (2) b |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate the load (generation minus net flow into or out of an area) for each weather zone. |  |

| Requirement ID | SCD-FR5 |
| --- | --- |
| Requirement Name | WGR Meteorological Telemetry |
| Protocol Reference | Section(s): 3.13 (1) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate hourly average meteorological data (wind speed and temperature) for each WGR based on the telemetered meteorological data from each WGR. |  |

| Requirement ID | SCD-FR6 |
| --- | --- |
| Requirement Name | MVA Calculation |
| Protocol Reference | Section(s): 6.5.7.1.13 (1) (a) (ii) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Calculation Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall calculate MVA for each MW/MVAR pair received for all lines, transformers, and reactors. Does the alarm processor only alarm the MVA? |  |

## Output Data to QSEs

| Requirement ID | SCD-FR7 |
| --- | --- |
| Requirement Name | SCED/LFC Outputs to QSEs |
| Protocol Reference | Section(s) (see Section 6.1.1 of this document) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Generation Control Output Processor |
| Sub-Process Element Coverage | Full |
| Description: LFC produces a list of data items unique to each QSE to be sent to the respective QSEs every 4 seconds. The content of the list will vary depending on the execution cycle times of the various generation sub-system applications. SCADA shall send the list of data to each respective QSE using either the Set Data Set Element Values or Set Data Value service of ICCP. Every value in the list shall have quality attributes applied. (Note that ERCOT must proactively write generation, regulation and other AGC-related signals to QSEs, so the “SET…” functions of ICCP Conformance Block 1 are required.????) Values to be written shall be grouped together for each QSE and associated with a time stamp that is also written to the QSE. The time stamp shall indicate the time the group of values was written to the QSE. Refer to Section 6.1.1, Data Sent to QSEs, for details on AGC-related data sent to QSEs, and the Nodal Protocol references associated with each data item. |  |

## Other Functionality

| Requirement ID | SCD-FR8 |
| --- | --- |
| Requirement Name | Data Availability Statistics |
| Protocol Reference | Sections 8.1 (3)(c); 8.3 (1)(b); Telemetry Standards |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide availability statistics on a point by point basis and on an TSP and QSE aggregated basis. EMS displays shall be provided to show hourly, daily, monthly, and quarterly availability statistics on a point by point basis and on an aggregated basis. Each of these displays shall have sorting and filtering tabs Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR9 |
| --- | --- |
| Requirement Name | Summary Displays and Tables |
| Protocol Reference | Section 6.5.7.1.13 (3) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide a summary display showing the time and date of detection for each of the following: - Suspect status points?? - Suspect analog points ?? - Stale points - Manual Replaced by Market Participant - Manual Replaced by ERCOT operators - Abnormal breaker and switch status - Limit violations - Base Points Each of these displays shall have sorting and filtering tabs. All summary tables shall be archived. |  |

| Requirement ID | SCD-FR10 |
| --- | --- |
| Requirement Name | ICCP Link Availability Statistics |
| Protocol Reference | Section(s) 8.1 (3)(c)(ii) and 8.3 (1)(b)(ii) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Communication Availability Monitor |
| Sub-Process Element Coverage | Partial |
| Description: SCADA shall provide ICCP link availability statistics. EMS displays shall be provided to show hourly, daily, and monthly availability statistics for each ICCP link. Availability statistics shall exclude planned outages how do you do this?. Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR11 |
| --- | --- |
| Requirement Name | Critical Data Availability Statistics |
| Protocol Reference | Sections 8.1 (3);8.3 (1), Telemetry Standard |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: ERCOT shall uniquely identify critical data points and provide separate availability statistics on a point by point basis and on an aggregated basis. EMS displays shall be provided to show hourly, daily, monthly, and quarterly availability statistics on a point by point basis and on an aggregated basis. Each of these displays shall have sorting and filtering tabs. Availability statistics shall be archived. |  |

| Requirement ID | SCD-FR12 |
| --- | --- |
| Requirement Name | Stale Data Processing |
| Protocol Reference | Section(s): 6.5.7.1.13(a) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | Telemetry Input Processor |
| Sub-Process Element Coverage | Partial |
| Description: Market participants will associate every telemetered value transferred via ICCP with a time stamp having at least a 1 second resolution. SCADA shall use the time stamp to determine if the value received is “stale”. Each point in the real-time database shall have an attribute indicating whether “stale” data processing is to be applied to the value, and the number of seconds elapsed (the “stale time” attribute) before the value is considered to be “stale”. A second attribute shall be associated with every point indicating whether the value is or is not stale. For points designated to have “stale” processing applied, the received value’s time stamp shall be compared with the current system time to determine whether the value has exceeded its “stale time” attribute. Values exceeding “stale time” shall be marked “stale”. Values not exceeding “stale time” shall be marked “not stale”. This seems incorrect. The Market Participant does not know if ERCOT has received the ICCP data. Seems like ERCOT’s system must check if it has not received an update from a Market Participant after some established time interval, then ERCOT’s SCADA system must mark all data from that MP as stale. MPs will also be sending a quality code with each point if the MP looses communication with its field device. This “stale” quality code needs also to be processed. Please explain how all this works and ERCOT systems keeps track of which “stale” quality code it is processing. Note: ERCOT intends that the vendor assess the impact of this requirement on the processing requirements including any conflicts with reporting by exception or non-telemetered data being exchanged via ICCP. |  |

| Requirement ID | SCD-FR13 |
| --- | --- |
| Requirement Name | Manual Override |
| Protocol Reference | Section(s) 6.5.7.1.5 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Manual Entry Processor |
| Sub-Process Element Coverage | Partial |
| Description: There shall be the capability for the ERCOT operators to Manually Replace SCADA telemetry from one-line diagrams and station tabular displays to change breaker and switch status before that information is processed by the Network Security Analysis for the next SCED interval. Summary dispalys of all entries are provided according to above. |  |

| Requirement ID | SCD-FR14 |
| --- | --- |
| Requirement Name | ICCP Quality code processing |
| Protocol Reference | Section(s): 3.10.7.4 (3) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | Telemetry Input Processor; Manual Entry Processor |
| Sub-Process Element Coverage | Partial |
| Description: Per the TAC approved Telemetry Standards Document, SCADA shall process the following quality codes associated with ICCP status and analog data: - Valid – represents analog or status the market participant considers valid - Manual – represents a analog or status entered manually at the market participant (not received from the field electronically) - Suspect - Represents a analog or status in which the market participant is unsure of the validity - Invalid – Represents an analog or status, which the market participant has identified as out of reasonability limits. - Com_fail – informs ERCOT that due to communications failure, the analog or status provided ERCOT is not current - Manually Replaced by ERCOT operator SCADA shall produce alarms for any change in quality code as well as return to valid alarms. This can overload the alarm processor and well as the ERCOT operators. Suggest only putting them in the summary display. SCADA shall convert data condition codes from each TSP and QSE in a consistent manner for all applicable ERCOT applications. |  |

| Requirement ID | SCD-FR15 |
| --- | --- |
| Requirement Name | Failover Performance |
| Protocol Reference | Section(s): 3.10.7.4 (4)(a) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | Telemetry Input Processor; Generation Control Output Processor |
| Sub-Process Element Coverage | Partial |
| Description: Each TSP and QSE shall use fully redundant data communication links (ICCP or RTU) between its control center systems and ERCOT systems such that any single element of the communication system can fail and: (a) For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and (b) For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT’s control centers with updates of all data continuing at a 30 second or less scan rate. |  |

# Supplementary Requirements

| Requirement ID | SCD-SR1 |
| --- | --- |
| Requirement Name | SCADA Processing |
| Requirement Type | Performance |
| Description: SCADA shall perform all data processing within the applicable scan interval according to the following processing times: - 2-second data: 1 second - 4-second data: 1 second - 10-second data: 2 seconds [no data is allowed to be provided at less than 10 second scan rate] Processing shall include data conversion (if necessary), reasonability checks, limit checks, initiation of logging and alarming, storage in the real-time database, and activation of external processes where applicable. |  |

| Requirement ID | SCD-SR2 |
| --- | --- |
| Requirement Name | Data Availability |
| Requirement Type | System and Communication |
| Description: SCADA shall monitor the availability of ICCP links. The cumulative availability in percentage shall be calculated for each hour, day and month. SCADA shall alarm the ERCOT operator assigned maintenance funcationality messaging if the availability falls below the pre-set monthly threshold. Availability thresholds shall be configurable by ERCOT Analysts. Initially these thresholds shall be configured as follows: - TSP ICCP communication using both primary and secondary systems shall achieve a monthly availability of ninety-eight (98%) percent, excluding approved planned outages. Ninety eight percent is way to low. This allows the data link to be down over 15 hours a month. Not acceptable to meet nodal requriements. I suggest ICCP must me up at least 99.8% which still alows 6 hours a month failure. We have totally redundant communication paths in nodal and this should be achievable. - QSE ICCP communciation using both primary and secondary systems shall achieve a monthly availability of ninety-nine point ninety-nine (99.99%) percent, excluding approved planned outages. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data. A link will be considered as available when at least the predefined percent (configurable by an ERCOT Analyst and initially set to eighty-five (95%)) of the data defined on that link is successfully transferred to ERCOT with a valid or manual quality code. The current and previous month’s availability data shall be stored in EMS database and shall be viewable through EMS user interface. This data must be provided to the perfomance monitoring requiremnts in section 8.3 of the protocols and posed on the MIS for any failures to perform (secition 8.4). Has the TAC approved “TAC-approved TSP Monitoring Program referenced below been developed? This “monitoring program may influence technical requrements of this specifition. 8.3 TSP Performance Monitoring and Compliance (1) ERCOT shall develop a TAC-approved TSP Monitoring Program to be included in the Operating Guides for TSPs. The metrics developed by ERCOT must include the following elements of transmission system planning, operations and maintenance: (a) Transmission Element rating calculations; (b) Real-Time data: (i) Meeting telemetry standards, including the installation of new measurement equipment and the accuracy of measurements; (ii) Communications system availability; and 8.4 Non-Compliance (1) Reports of all activities that do not meet the performance criteria in this Section and in the Operating Guides must be provided to TAC, the ERCOT Board, the PUCT and to the NERC Board as appropriate. Non-compliance reports must be posted on the MIS Secure Area on delivery. |  |

| Requirement ID | SCD-SR3 |
| --- | --- |
| Requirement Name | No degradation in performance |
| Requirement Type | Performance |
| Description: There shall be no degradation in the performance of ERCOT systems as a result of the SCADA functions execution under full volume processing. |  |

| Requirement ID | SCD-SR4 |
| --- | --- |
| Requirement Name | Interface to ERCOT Custom Applications |
| Requirement Type | SCADA Application Interfaces |
| Description: SCADA shall interface to existing ERCOT custom applications (such as RTMONI)?? What is this? Is it required in the protocols? in the new system. (Please note that our current load forecast is dependent upon RTMONI calculations to support the weather zone calculations.) |  |

| Requirement ID | SCD-SR5 |
| --- | --- |
| Requirement Name | Online User Documentation and Help System Requirements |
| Requirement Type | Training and Documentation |
| Description: User and operator software messages shall be formatted in plain English and generated at the application level for each application and not at the OEM software level (ORACLE, UNIX, etc.) Online help shall be context sensitive. User documentation shall be made available for online access. |  |

| Requirement ID | SCD-SR6 |
| --- | --- |
| Requirement Name | Database Sizing |
| Requirement Type | System and Communication |
| Description: The SCADA application shall be sized to process the data sizing specified in Section 6 of this document. |  |

| Requirement ID | SCD-SR8 |
| --- | --- |
| Requirement Name | Standard SCADA functionality |
| Requirement Type | General |
| Description: SCADA shall include the following components: Data acquisition and transfer, supervisory control, topology system, tagging and notes, on-line editor, Inter-Process Communication Routines, short term history files and support, routines for mapping telemetered data to EMS applications, long term historical data recording support, user defined calculations, loadshed routines, methods for providing current time and system frequency, logging of SCADA activities, status of SCADA applications, user and configuration, maintenance, and support displays. |  |

| Requirement ID | SCD-SR9 |
| --- | --- |
| Requirement Name | Frequency Inputs |
| Requirement Type | Frequency Processing |
| Description: SCADA shall receive frequency measurements from Time receivers located at Austin and Taylor sites. Four time receivers will be provided with the system. Two time receivers will be located at Taylor and two at Austin. The SCADA process at each location shall read frequency and time error from all four time receivers and store the four Frequency and Time Error values in the real-time database. |  |

| Requirement ID | SCD-SR10 |
| --- | --- |
| Requirement Name | Database Modification |
| Requirement Type | Database Maintenance |
| Description: The SCADA function shall provide on-line editing tools and screens to allow an EMS Analysts to add, remove, and edit data points telemetered from QSEs and TSPs. Are these then avaliable on a summary page so that they eventually get fixed? Who at ERCOT is responsible for oversight of TSPs and QSEs who are sending bad data to ERCOT? |  |

| Requirement ID | SCD-SR11 |
| --- | --- |
| Requirement Name | Process Redundant Links |
| Protocol Reference | System and Communication |
| Description: Communication between ERCOT and market participants is provided by redundant communication links. One link traverses ERCOT’s Frame Relay network, and the other link traverses ERCOT’s DACS network. The DACS network acts as a backup to the Frame Relay network. If communication with a market participant is lost on the primary link, SCADA shall automatically establish (or otherwise activate) communication over the backup link. Will be be providing a use case to test the true redundancy of these links? |  |

# Protocol Coverage

The following table summarizes the coverage extent (Full/Partial) of all relevant Nodal Protocols that are mentioned in this requirements document.

| Protocol Sub-Section | Section title | Coverage by Requirements (Full/Partial) | Covered by Requirement |
| --- | --- | --- | --- |
| 3.6 | Load Participation | Partial | SCD-FR2 |
| 3.10.7.2 (3) | Modeling of Resources and Transmission Loads | Partial | SCD-FR1 |
| 3.10.7.4 | Telemetry Criteria | Partial | SCD-FR16 Thru SCD-FR24 |
| 3.10.7.4 (2) | Telemetry Criteria | Partial | SCD-FR1 |
| 3.10.7.4 (3) | Telemetry Criteria | Partial | SCD-FR14 |
| 3.10.7.4 (4)(a) | Telemetry Criteria | Partial | SCD-FR15 |
| 3.10.8 (2) a | Dynamic Ratings | Partial | SCD-FR1 |
| 3.10.8.1 (1) | Dynamic Ratings Delivered via ICCP | Full | SCD-FR1 |
| 3.10.8.2 (2) | Dynamic Ratings Delivered via ICCP | Full | SCD-FR1 |
| 3.12.1 (2) b | Mid-Term Load Forecast | Partial | SCD-FR4 |
| 3.12.2 (2) b | Long-Term Load Forecast | Partial | SCD-FR4 |
| 3.13 (1) | Renewable Production Potential Forecasts | Partial | SCD-FR5 |
| 4.2.2 (1) | Wind-Powered Generation Resource Production Potential | Partial | SCD-FR2 |
| 4.2.2 (2) | Wind-Powered Generation Resource Production Potential | Partial | SCD-FR2 |
| 6.3.2 (2) | Activities for Real-Time Operations | Partial | SCD-FR7 |
| 6.4.5 (1) | Resource Status | Partial | SCD-FR2 |
| 6.5.5.1 (1) | Operational Data Requirements | Partial | SCD-FR2 |
| 6.5.5.2 (2) | Operational Data Requirements | Full | SCD-FR2 |
| 6.5.5.2 (4) | Operational Data Requirements | Full | SCD-FR2 |
| 6.5.5.2 (6) | Operational Data Requirements | Full | SCD-FR2 |
| 6.5.5.2 (8) b | Operational Data Requirements | Partial | SCD-FR2 |
| 6.5.5.2 (8) c | Operational Data Requirements | Partial | SCD-FR2 |
| 6.5.7.1.1 | SCADA Telemetry | Partial | SCD-FR13 |
| 6.5.7.1.5 | Topology Consistency Analyzer / Override | Partial | SCD-FR13 |
| 6.5.7.1.7 (1) | Real-Time Weather and Dynamic Rating Processor | Partial | SCD-FR1 |
| 6.5.7.1.13 (1) (a) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Full | SCD-FR1 SCD-FR6 SCD-FR12 |
| 6.5.7.1.13 (1) (d) (ii) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Full | SCD-FR2 |
| 6.5.7.1.13 (1) (e) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Full | SCD-FR1 |
| 6.5.7.1.13 (3) | Data Inputs and Outputs for the Real-Time Sequence and SCED | Partial | SCD-FR9 |
| 6.5.7.2 | Resource Limit Calculator | Partial |  |
| 6.5.7.3 | Security Constrained Economic Dispatch | Partial |  |
| 6.5.7.4 (1) | Base Points | Partial | SCD-FR7 |
| 6.5.7.5 (1) | Ancillary Services Capacity Monitor | Partial | Section 6.3 |
| 6.5.7.6.1 (3) | LFC Process Description | Partial | SCD-FR2 |
| 6.5.7.6.1 (4) | LFC Process Description | Partial | SCD-FR2 |
| 6.5.7.6.1 (8) j | LFC Process Description | Partial | SCD-FR2 |
| 6.5.7.6.1 (9) | LFC Process Description | Partial | SCD-FR7 |
| 6.5.7.6.2.1 (8) | Deployment of Regulation Service | Partial | SCD-FR7 |
| 6.5.7.6.2.2 (11) | Deployment of Responsive Reserve Service | Partial | SCD-FR7 |
| 6.5.7.6.2.2 (12) | Deployment of Responsive Reserve Service | Partial | SCD-FR7 |
| 6.5.7.6.2.3 (4) | Non-Spinning Reserve Service Deployment | Partial | SCD-FR7 |
| 6.5.9 (1) | Emergency Operations | Partial | SCD-FR7 |
| 6.5.9.5 (i) | Block Load Transfers between ERCOT and Non-ERCOT Control Areas | Full | SCD-FR3 SCD-FR1 |
| 8.1 (3) (c) | QSE/Resource Performance Monitoring and Compliance | Full | SCD-FR8 SCD-FR10 SCD-FR11 |
| 8.3 (1) (b) | TSP Performance Monitoring and Compliance | Partial | SCD-FR8 SCD-FR10 SCD-FR11 |
| 11.1.11 (3) | Treatment of EPS RID Data | Partial | SR8 |
| 11.6.2.1 | Sub-divide ERCOT into a practical granularity of “UFE Analysis Zones,” but no more than ten (10) zones, which can provide reliable and accurate data to be used for Cost/Benefit Analysis and decision making purposes | Partial | SR8 |
| 11.6.3 | Data Collection and Metering Requirements For UFE Analysis Zones | Partial | SR8 |

# Data Elements to be Exchanged

The tables below specify the data exchange requirements known as of the May 2006 protocols. The data includes information specifically identified in the protocols, and other data presently exchanged and/or expected to be needed to support operation under the TNP.

Data exchange undergoes continuous revision. The Operating Guides specify the official ERCOT data exchange requirements at any given point in time. Therefore, the tables below are intended as an initial guide to system sizing. The latest approved version of the Operating Guides supersede the information included here.

Anticipated maximum sizing parameters are:

Table 1 - Estimated Maximum Sizing Parameters

| Parameter | Quantity |
| --- | --- |
| Number of QSEs | 500 |
| Number of TSPs | 100 |
| Number of Generation Resources | 2,000 |
| Number of Load Resources | 1,000 |
| Number of Busses | 24,000 |
| Number of Hubs seems high | 200 |
| Number of Load Zones seems high | 200 |
| Number of Generation Plants | 500 |
| Number of Autotransformers | 200 |
| Number of Reactors | 2,000 |
| Number of Capacitors | 2,000 |
| Number of Circuit Breakers | 35,000 |
| Number of Switches | 70,000 |
| Number of Weather Zones | 50 |
| Number of Transmission Lines | 20,000 |
| Number of Block Load Transfer Points | 20 |

## QSE Data Exchange

### Data Sent to QSEs

Table 2 - Per-QSE Data Sent to QSE

| Per-QSE Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Regulation Up MW Regulation Down Mw | 4 4 | 6.5.7.6.2.1 (8) 6.5.7.6.2.1 (8) |
| Responsive MW | 4 | 6.5.7.6.2.2 (11) |
| Non-Spin Mw | 4 | 6.5.7.6.2.3 (4) |

Table 3 - Per- Generation Resource Data Sent to QSE

| Per-Generation Resource Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Resource Suspend Ramping to Base Point (on/off) | 4 | 6.5.7.6.1 (9) |
| Resource Updated Desired Base Point MW SCED Base Point | 4 SCED Execution | 6.5.7.4 (1) b |
| Resource – LMP | 4 | 6.3.2 (2) table |
| Resource BP above HASL due to RRS (on/off) | 4 | 6.5.7.4 (1) c |
| Pseudo unit dispatch (on/off) | 4 | 6.5.7.4 (1) e |
| Time of Dispatch | 4 | 6.5.7.4 (1) d |
| Other possible information (multiple values) | 4 | 6.5.7.4 (1) e |
| Emergency Basepoint Mw | 4 | 6.5.9 (1) |

Table 4 - Per-Bus Data Sent to QSE

| Per-Bus Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Hubs and Load zones LMPs | 4 | 6.3.2 (2) |

### Data Received from QSEs

Table 5 - Per-QSE Data Received from QSE

| Per-QSE Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Frequency (system) | 2 | 6.5.7.6.1 (3) |
| Any agreed-upon additional data Resource (multiple data items) | various | 6.5.5.2 (2) e 6.5.5.2 (4) b |

Table 6 - Per-Plant Data Received from QSE

| Per-Plant Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Plant auxiliary load ???? | 10 | 6.5.5.2 (2) c |
| Switch status not monitored by TSP (possibly multiple switches) | RBE | 6.5.5.2 (2) d |

Table 7 - Per-Generation Resource Data Received from QSE

| Per-Generation Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Combined Cycle config no. | 2 | 6.5.5.2 (8) b |
| Resource status | RBE | 6.4.5 (1) 6.5.5.1 (1) |
| Generation Resource Net MW to be used in LFC and SCED | 2 | 6.5.5.2 (2) a |
| Generation Resource Mvar | 10 | 6.5.5.2 (2) b |
| Generation Resource Breaker status | RBE | 6.5.5.2 (2) f |
| Generation Resource High Sustained Limit (HSL) and Text Reason why limit is less than that limit specified in the Registration system | 2 | 6.4.5 (1) 6.5.5.2 (2) g 6.5.7.1.13 (1) (d) (ii) (B) |
| Generation Resource Low Sustained Limit (LSL) and Text Reason why limit is less than that limit specified in the Registration system | 2 | 6.4.5 (1) 6.5.5.2 (2) j 6.5.7.1.13 (1) (d) (ii) (C) |
| Generation Resource High Emergency Limit (HEL) and Text Reason why limit is less than that limit specified in the Registration system | 2 | 6.5.5.2 (2) h |
| Generation Resource Low Emergency Limit (LEL) and Text Reason why limit is less than that limit specified in the Registration system | 2 | 6.5.5.2 (2) i |
| Text reason for any Resource where a Ramp Rate is deviating from a standard Ramp Rate curve for the Resource, | 10 | 6.4.5 (1) |
| Generation Resource Reg-Up Ancillary Service Schedule and Resource Responsibility | 2 | 6.5.5.2 (2) k |
| Generation Resource Reg-Down Ancillary Service Schedule and Resource Responsibility | 2 | 6.5.5.2 (2) k |
| Generation Resource Responsive Ancillary Service Schedule and Resource Responsibility | 2 | 6.5.5.2 (2) k |
| Generation Resource Non-Spin Ancillary Service Schedule and Resource Responsibility | 2 | 6.5.5.2 (2) k |
| Generation Resource Reg-Up participation factor | 2 | 6.5.5.2 (2) l |
| Generation Resource Reg-Down participation factor | 2 | 6.5.5.2 (2) l |
| Generation Resource Responsive participation factor | 2 | 6.5.5.2 (2) l |
| Generation Resource Reg High Block status | 2 | 6.5.5.2 (6) |
| Generation Resource Inhibit Reg Low Block status This block is applied for either regulating up or down. It should be standard in AREVA’s system. It can limit either Reg up or Reg down; both either deployment or recall. This block status indications should be linked to the regulation control display available to the ERCOT operator showing him which units are not responding to control. Possibly need an alarm if this condition lasts for more than 5 minutes or so. (6) A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-Down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE. | 2 | 6.5.5.2 (6) |
| Generation Resource Normal Ramp Rate | 2 | 6.4.5 (1) |
| Generation Resource Emergency Ramp Rate | 2 | 6.4.5 (1) |
| Generation Resource DSR Base Point | 2 | 6.5.7.6.1 (8) j |
| Generator Step-up transformers no load tap position | 10 | 6.5.7.1.13 (1) (d) (ii) (A) |

Table 8 - Per-Load Resource Data Received from QSE

| Per-Load Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Load Resource MW | 2 | 6.5.5.2 (4) a |
| Resource Status | 2 | 6.4.5 (1) 6.5.5.1 (1) 6.5.5.2 (8) b 6.5.5.2 (8) c |
| Load Resource breaker status | 4 | 6.5.5.2 (4) c |
| Load Resource high-set under-frequency relay status (if RRS resource) | 4 | 6.5.5.2 (4) g |
| Load Resource Low Power Consumption (LPC) | 2 | 6.5.5.2 (4) d |
| Load Resource Maximum Power Consumption (MPC) | 2 | 6.5.5.2 (4) e |
| Controllable Load Resource Reg-Up Ancillary Service Schedule and Resource Responsibility | 2 | 3.6 (implied) |
| Controllable Load Resource Reg-Down Ancillary Service Schedule and Resource Responsibility | 2 | 3.6 (implied) |
| Load Resource RRS Ancillary Service Schedule and Resource Responsibility | 2 | 6.5.5.2 (4) f |
| Load Resource Non-Spin Ancillary Service Schedule and Resource Responsibility | 2 | 3.6 (implied) |
| Controllable Load Resource Reg-Up participation factor | 2 | 3.6 (implied) |
| Controllable Load Resource Reg-Down participation factor | 2 | 3.6 (implied) |
| Load Resource Responsive participation factor | 2 | 3.6 (implied) |
| Controllable Load Resource Inhibit Reg-Up status | 2 | 3.6 (implied) |
| Controllable Load Resource Inhibit Reg-Down status | 2 | 3.6 (implied) |
| Load Resource NRAMP What is this? Not sure it is in section 3.6 of protocols | 2 | 3.6 (implied) |
| Load Resource ERAMP What is this? Not sure it is in section 3.6 of protocols | 2 | 3.6 (implied) |
| What is this for? |  | 6.5.5.2 (2) e this reference is for Generator Resources only. |

Table 9 - Per Wind Resource Data Received from QSE

| Per Wind Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Wind Speed | 10 | 6.5.7.1.13 (1) (e) 4.2.2 (1) (implied) |
| Wind Direction | 10 | 4.2.2 (1) (implied) |
| Temperature | 10 | 4.2.2 (1) (implied) |
| Barometric Pressure | 10 | 4.2.2 (1) (implied) |

## TSP Data Exchange

Table 10 - Per-Buss Data Received from TSP

| Per-Buss Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Buss Voltage kV | 10 | 6.5.7.1.13 (1) (a) (i) |

Table 11 - Per-Transformer Data Received from TSP

| Per-Transformer Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Transformer Flow MW | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Transformer Flow Mvar | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Transformer Flow MVA (calculated) | 10 | 6.5.7.1.13 (1) (a) (ii) |
| LTC Tap Position | 10 | 6.5.7.1.13 (1) (a) (v) |

Table 12 - Per-Transmission Line Data Received from TSP

| Per-Transmission Line Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Line Flow MW | 10 | 3.10.7.4.2 |
| Line Flow Mvar | 10 | 3.10.7.4.2 |
| Line Flow MVA (calculated) | 10 | 3.10.7.4.2 |

Table 13 - Per-Shunt (Inductive or Capacitive) Data Received from TSP

| Per-Shunt (Inductive or Capacitive) Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Shunt Mvar what is this? Is it specified in 3.10.7.4.2 | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Shunt Flow MVA (calculated) | 10 | 6.5.7.1.13 (1) (a) (ii) |

Table 14 - Per-Circuit Breaker Data Received from TSP

| Per-Circuit Breaker Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Circuit Breaker MW flow I do not think this is required in the protocols. Only line and transformer flows are specified. | 10 | 3.10.7.4 (2) (implied) |
| Circuit Breaker Mvar | 10 | 3.10.7.4 (2) (implied) |
| Breaker Status (with normal status indicator) | 10 | 3.10.7.4.1 |

Table 15 - Per-Load Data Received from TSP

| Per-Switch Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Switch Status (with normal status indicator) | 10 | 3.10.7.4.1, 6.5.7.1.13 (1) (a) (iv) 6.5.7.1.13 (1) (a) (iii) |

Table 16 - Per-Load Data Received from TSPTSP

| Per-Load Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Load in MW | 10 | 3.10.7.4.2 |
| Load in Mvar | 10 | 3.10.7.4.2 |

Table 17 - Per-DC Injection Point Data Received from TSP

| Per-DC Injection Point Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| DC Injection in MW | 10 | 3.10.7.2 (3) |
| DC Injection in Mvar | 10 | 3.10.7.2 (3) |
| DC Tie Status | 10 | 3.10.7.2 (3) (implied) |

Table 18 - Per- Block Load Transfer Point Data Received from TSP

| Per-Block Load Transfer Point Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Switching Device Status at BLT points | 10 | 6.5.9.5 (i) |
| BLT MW | 10 | 6.5.9.5(i) |
| BLT MVAR | 10 | 6.5.9.5(i) |

Table 19 - Per Weather Zone Tie Line Data Received from TSP

| Per Weather Zone Tie Line Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Temperature | 10 | 6.5.7.1.13 (1) (e) 6.5.7.1.7 (1) |
| Wind Speed (if available) | 10 | 6.5.7.1.13 (1) (e) 6.5.7.1.7 (1) |

Table 20 - Per Dynamic Rating Data Received from TSP

| Per Dynamic Rating Data Received from TSP | Frequency (min) | Nodal Protocol Reference |
| --- | --- | --- |
| Line ID | 10/RBE | 3.10.8.1 (1) (a) |
| From Status | 10/RBE | 3.10.8.1 (1) (b) |
| To Station | 10/RBE | 3.10.8.1 (1) (c) |
| Normal Rating | 10/RBE | 3.10.8.1 (1) (d) |
| Emergency Rating | 10/RBE | 3.10.8.1 (1) (d) |
| 15-Minute Rating | 10/RBE | 3.10.8.1 (1) (d) |

## Data Available to All Market Participants

Table 21 - Data Available for Reading by All Market Participants

| Data Available for Reading by Market Participants | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Responsive Reserve Capacity from Generation Resources | 10 | 6.5.7.5 (1) a |
| Responsive Reserve Capacity from Load Resources | 10 | 6.5.7.5 (1) b |
| Non-Spinning Reserve available from On-Line Generation Resources with Energy Offer Curves | 10 | 6.5.7.5 (1) c |
| Non-Spinning Reserve available from undeployed Load Resources | 10 | 6.5.7.5 (1) d |
| Non-Spinning Reserve available from Off-Line Generation Resources | 10 | 6.5.7.5 (1) e |
| Non-Spinning Reserve available from Resources with Output Schedules | 10 | 6.5.7.5 (1) f |
| Undeployed Reg-Up and undeployed Reg-Down | 10 | 6.5.7.5 (1) g |
| Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | 10 | 6.5.7.5 (1) h |
| Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | 10 | 6.5.7.5 (1) i |
| Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | 10 | 6.5.7.5 (1) j |
| Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | 10 | 6.5.7.5 (1) k |
| Total ERCOT load | 10 |  |
| Total ERCOT Generation | 10 |  |
| Total ERCOT Generation Operating Reserve | 10 |  |

Set Data Set Element Values and Set Data Value are standard ICCP services defined in IEC 870-6-503, TASE.2 Services and Protocol. These services are included in ICCP Conformance Block 1 which defines the minimum required functionality of ICCP. Set Data Set Element Values and Set Data Value services are specified here to make it clear that ERCOT will not send AGC-related services to QSEs using the Device Control services of ICCP Conformance Block 5. The Device Control services of ICCP are unacceptable because they do not support quality codes. TASE.2 is another name for ICCP.