ERCOT Operating Guides

- Table of Contents

- January 1, 2007

1.	Introduction	1-3

1.1	Document Purpose	1-3

1.2	Document Relationship	1-5

1.3	Process for Operating Guide Revision	1-6

1.4	Market Overview	1-15

1.5	Conformance to NERC Policies and Procedures	1-17

1.6	Operating Definitions	1-20

1.7	Entity Definitions and Roles	1-22

1.7.1	ERCOT Control Area Authority	1-22

1.7.2	Qualified Scheduling Entities	1-22

1.7.3	Transmission Operator (TO)	1-22

1.7.4	Resource Entity	1-23

1.7.5	Load Serving Entities (LSE)	1-24

1.8	Operational Training	1-25

1.8.1	Operator Training Objectives	1-25

1.8.2	System Operator Training Requirements	1-25

1.8.3	ERCOT Operations Training Seminar	1-25

1.8.4	ERCOT Black Start Training	1-26

1.8.5	ERCOT Severe Weather Drill	1-26

1.8.6	Criteria For The Selection Of Operators	1-26

1.8.7	Training Practices	1-26

1.9	Document Revisions	1-28

2.	System Operations	2-5

2.1	Operational Duties	2-5

2.2	System Monitoring and Control	2-7

2.2.1	Overview	2-7

2.2.2	Security Criteria	2-8

2.2.3	Automatic Generation Control Systems	2-9

2.2.4	Automatic Voltage Regulators And Power System Stabilizers	2-11

2.2.5	Turbine Speed Governors	2-11

2.2.6	Performance/Disturbance/Compliance Analysis	2-12

2.2.7	Time Error And Time Synchronization	2-12

2.3	Dispatch Duties	2-15

2.3.1	Control Area Operator Authority	2-15

2.3.2	Dispatch Instruction Procedures	2-16

2.4	Scheduling	2-19

2.4.1	Day Ahead Scheduling	2-19

2.4.2	Adjustment Period Scheduling Process	2-21

2.4.3	Direct Current Tie Interconnection Day Ahead Scheduling Process	2-23

2.4.4	Temporary Deviations from Scheduling Procedures	2-24

2.4.5	Real-Time Schedules	2-24

2.5	Ancillary Services	2-31

2.5.1	ERCOT Responsibilities	2-31

2.5.2	Responsive Reserve	2-37

2.5.3	Non-Spinning Reserve Service (NSRS)	2-40

2.5.4	Replacement Reserve Service (RPRS)	2-41

2.5.5	Balancing Energy Service	2-42

2.6	Changes in System Status	2-44

2.6.1	Changes in Resource Status	2-44

2.6.2	Changes in Transmission Facility Status	2-44

2.7	Outage Coordination	2-45

2.7.1	ERCOT Control Area Authority Responsibilities	2-45

2.7.2	Forced Outages	2-45

2.7.3	Scheduled Outages	2-46

2.8	Congestion Management	2-48

2.8.1	Overview of ERCOT Coordinated Congestion Management	2-48

2.9	Requirements for Under-Frequency Relaying	2-50

2.9.1	Automatic Firm Load Shedding	2-50

2.9.2	Generators	2-51

2.10	System Voltage Profile	2-52

2.10.1	Introduction	2-52

2.10.2	Maintaining Voltage Profile	2-52

2.10.3	Special Consideration for Nuclear Power Plants	2-53

2.10.4	Reactive Considerations for Gas and Steam Turbine Power Plants	2-54

2.11	External Control Area Inter-Ties	2-55

2.11.1	Control Area Operations	2-55

2.11.2	Operation of DC Ties	2-55

2.12	Document Control	2-56

3.	Operational Interfaces	3-4

3.1	System Control Interfaces with ERCOT	3-4

3.1.1	Introduction	3-4

3.1.2	Compliance with Dispatch Instructions	3-4

3.1.3	Qualified Scheduling Entities	3-6

3.1.4	Power Generation Companies	3-10

3.1.5	Transmission and/or Distribution Service Providers	3-22

3.1.6	Responsibility For Equipment Ratings	3-25

3.2	Scheduling Interfaces with ERCOT	3-26

3.2.1	Scheduling-Related Duties of Qualified Scheduling Entities	3-26

3.2.2	Scheduling Process	3-28

3.2.3	Procurement of Replacement Reserve Service Resources	3-29

3.2.4	Procurement of Additional Ancillary Services	3-30

3.2.5	Direct Current Tie Interconnection Day Ahead Scheduling Process	3-30

3.2.6	Dynamic Schedules	3-31

3.2.7	Approval of the Use of Responsibility Transfer (RspT) Schedules	3-32

3.3	Document Control	3-34

4.	Emergency Operation	4-4

4.1	Introduction	4-4

4.2	Emergency Notifications	4-5

4.2.1	Operating Condition Notice	4-5

4.2.2	Advisory	4-6

4.2.3	Alert	4-7

4.2.4	Emergency Notice	4-8

4.3	Operation To Maintain Transmission System Security	4-10

4.3.1	Remedial Action Plans	4-12

4.4	Block Load Transfers between ERCOT and Non-ERCOT Control Areas	4-13

4.4.1	Introduction and General Information	4-13

4.4.2	BLTs to ERCOT	4-13

4.4.3	BLTs from ERCOT	4-13

4.5	Emergency Electric Curtailment Plan (EECP)	4-15

4.5.1	General	4-17

4.5.2	Operating Procedures	4-17

4.5.3	Implementation	4-18

4.6	Black Start	4-24

4.6.1	Principles	4-25

4.6.2	Strategies	4-25

4.6.3	Priorities	4-26

4.6.4	Responsibilities	4-26

4.6.5	Emergency Back Up Communication Facilities Criteria	4-28

4.7	Document Control	4-29

Attachment 4A:  Detailed Black Start Information	4-30

4A.1	CONSIDERATIONS FOR SYSTEM RESTORATION	4-30

4A.2	ERCOT COORDINATION	4-34

4A.3	Considerations For Black Start Testing	4-35

4A.4	Criteria for ERCOT and Transmission Operator Black Start Plans	4-35

5	Planning	5-3

5.1	Planning Criteria	5-3

5.1.1	Introduction	5-3

5.1.2	Load Forecasts	5-4

5.1.3	Resource Capability	5-4

5.1.4	Transmission Reliability Testing	5-4

5.1.5	Reports Of Testing	5-6

5.1.6	System Modeling Information	5-6

5.1.7	ERCOT Clarifications and Definitions of NERC Planning Standards Contingency Types C and D	5-12

5.2	Document Control	5-14

6	Reports and Forms	6-3

6.1	Reports	6-3

6.1.1	Disturbance Report	6-3

6.1.2	Relay Misoperation Report	6-4

6.2	Forms	6-5

6.2.1	Turbine Governor Speed Regulation Tests	6-5

6.2.2	Seasonal Unit Net Real Power Capability Verification	6-13

6.2.3	Biennial Unit Reactive Limits (Lead and Lag) Verification	6-14

6.2.4	Seasonal Hydro Responsive Reserve Net Capability Verification	6-18

6.2.5	Annual LaaR Telemetry Test	6-19

6.2.6	Biennial Test for LaaRs Providing Responsive Reserve Service	6-20

6.3	Document Control	6-25

7	Disturbance Monitoring and System Protection	7-3

7.1	Disturbance Monitoring Requirements	7-3

7.1.1	Introduction	7-3

7.1.2	Fault Recording Equipment	7-3

7.1.3	Dynamic Disturbance Recording Equipment	7-6

7.1.4	Equipment Reporting Requirements	7-6

7.1.5	Review Process	7-6

7.2	System Protective Relaying	7-7

7.2.1	Introduction	7-7

7.2.2	Design and Operating Requirements for ERCOT System Facilities	7-7

7.2.3	Performance Analysis Requirements for ERCOT System Facilities	7-10

7.2.4	Maintenance and Testing Requirements for ERCOT System Facilities	7-12

7.2.5	Requirements and Recommendations for ERCOT System Facilities	7-12

7.3	Document Control	7-23

8	Operational Metering and Communication	8-3

8.1	Operational Metering	8-3

8.1.1	ERCOT Interface RTUs	8-4

8.1.2	ERCOT ICCP Interface	8-4

8.1.3	Validation of Real Time Signals with Settlement Metering for Resources	8-4

8.1.4	Data from ERCOT to QSE’s	8-5

8.1.5	Data From ERCOT to TDSP	8-5

8.1.6	Data from QSE/TDSP to ERCOT	8-5

8.1.7	TDSP/QSE Metering Restoration	8-8

8.1.8	QSE and TDSP Data Acquisition	8-8

8.2	Calibration and Testing	8-8

8.2.1	Responsibility	8-8

8.2.2	Notification	8-8

8.2.3	Test Equipment	8-9

8.2.4	Disputes	8-9

8.2.5	Calibration Testing	8-9

8.2.6	Exchange of Information	8-9

8.2.7	Documentation	8-9

8.2.8	Operator One-line Displays	8-11

8.2.9	Notification of Changes	8-11

8.3	Communications	8-12

8.3.1	ERCOT WAN	8-12

8.3.2	ERCOT Responsibilities	8-15

8.3.3	QSE and TDSP Responsibilities	8-15

8.3.4	TDSP and QSE Supplied Communications	8-17

8.3.5	Maintenance and Restoration	8-17

8.4	Document Control	8-19

Attachment 8A:  ERCOT Data Sets	8-20