ERCOT Protocols

Section 5:  Dispatch

January 1, 2007

5	Dispatch	5-1

5.1	ERCOT Control Area Authority	5-1

5.2	North American Electric Reliability Council/ERCOT Tagging Procedures	5-1

5.3	Routine Dispatch Duties of ERCOT	5-3

5.4	Dispatch Instructions	5-4

5.5	Changes in ERCOT System Status	5-7

5.6	Emergency and Short Supply Operation	5-8

5.7	Block Load Transfers between ERCOT and Non-ERCOT Control Areas	5-15

5.8	BtB Ties and BLTs with the CFE Control Area	5-18

5.9	Frequency Response Requirements and Monitoring	5-18

# Dispatch

5.1	ERCOT Control Area Authority

5.1.1	Single Control Area

ERCOT will assume authority as Control Area Operator for the revised regional control area encompassing the boundaries of the previous control areas within the ERCOT interconnection.

5.1.2	Operating Guides and North American Electric Reliability Council Guidelines

ERCOT will perform all control area functions as defined in the Operating Guides and the North American Electric Reliability Council (NERC) guidelines.

5.2	North American Electric Reliability Council/ERCOT Tagging Procedures

The QSE will follow all NERC guidelines for tagging of Control Area interchange transactions.  ERCOT will be operated as a single Control Area.  Therefore, no internal ERCOT transactions require tagging.  Only transactions across ERCOT interconnections to SPP, WSCC, or Mexico, will be tagged by the QSE as prescribed in the NERC tagging guidelines.

5.2.1	Standards and Practices

Each TSP, DSP, and Private Use Network must meet the requirements specified in Section 5.2.1, Standards and Practices, or at their option, meet alternative requirements specifically approved by ERCOT.  Such alternative requirements may include requirements for aggregated groups of Facilities.

(1)	Sufficient static Reactive Power capability shall be installed by a DSP or a Private Use Network not subject to a TDSP tariff in substations and on the distribution voltage system to maintain at least a ninety-seven hundredths (0.97) lagging power factor for the maximum net active power supplied from a substation transformer at its distribution voltage terminals to the distribution voltage system. In those cases where a Private Use Network’s power factor is established and governed by a TDSP tariff, the TDSP and Private Use Network owner shall ensure that the Private Use Network meets the requirements as defined and measured in the applicable tariff.  For any substation transformer serving multiple DSPs, this power factor requirement shall be applied to each DSP individually for its portion of the total Load served.

(2)	Annually, ERCOT will review DSP power factors using the actual summer Load and power factor information included in the annual load data request to assess whether DSPs comply with the requirements of Section 5.2.1, Standards and Practices.  All DSP substations whose annual peak Load has exceeded ten (10) MW shall have and maintain Watt/VAR metering sufficient to monitor compliance; otherwise, DSPs will not be required to install additional metering to determine compliance.  At times selected by ERCOT, ERCOT will require manual power factor measurement at substations and points of interconnection that do not have power factor metering.  ERCOT will endeavor to provide DSPs sufficient notice to perform the manual measurements.  Such requests shall be limited to four (4) times per calendar year for each DSP substation or point of interconnection where power factor measurements are not available.

(3)	All DSPs shall report any changes in their estimated net impact on ERCOT as part of the annual Load data assessment.

(4)	As part of the annual Load-data-assessment, all Resource Entities owning Generation Resources shall provide an annual estimate of the highest potential affiliated MW and MVAR load (including any load netted with the generation output) and the highest potential MW and MVAR generation that could be experienced at the point of interconnection to the ERCOT Transmission Grid, based on the then current configuration (and the projected configuration if the configuration is going to change during the year) of the Generation Resource and any affiliated loads.

(5)	If actual conditions indicate probable non-compliance, ERCOT will require power factor measurements at the time of its choice while providing sufficient notice to perform the measurements.

(6)	Assuming optimal use of all other required installed Reactive Power capability, ERCOT Regional Planning Groups or Transmission Planning shall determine and demonstrate the need for any additional static and/or dynamic Reactive Power capability necessary to ensure compliance with the ERCOT Planning Criteria, and ERCOT Transmission Planning shall establish responsibility for any associated Facility additions among ERCOT TSPs.

(7)	For monitoring of compliance of the TSP's planned Facilities to the ERCOT Planning Criteria performance requirements, a self-certification process with random audits (similar to compliance to NERC Planning Standards), in conjunction with work performed in the ERCOT Regional Planning Groups, shall be used.  Except under Force Majeure conditions, if a TSP fails to maintain transmission system voltage within two percent (2%) of the scheduled voltage while reactive sources under its direct control are not fully utilized, ERCOT may, at its discretion, report this to the ERCOT Compliance Office.

(8)	The ERCOT Compliance Office will investigate claims of alleged non-compliance using ERCOT compliance procedures.  The ERCOT Compliance Office will use its compliance procedures to address confirmed non-compliance situations.  The ERCOT Compliance Office will advise ERCOT and TSP planning and operating staffs of the results of such investigations.

5.2.2	Operating Standards

ERCOT and TDSPs shall operate the ERCOT System in compliance with Good Utility Practice and NERC and ERCOT standards, policies, guidelines and operating procedures.  These Protocols shall control to the extent of any inconsistency between the Protocols and any of the following documents:

(1)	Any reliability guides applicable to ERCOT, including the Operating Guides;

(2)	The NERC Operating Manual and ERCOT procedures manual, supplied by NERC and ERCOT, respectively, as references for dispatchers to use during normal and emergency operations of the ERCOT Transmission Grid;

(3)	Specific operating procedures, submitted to ERCOT by individual transmission Facility owners or operators to address operating problems on their respective grids that could affect operation of the interconnected ERCOT Transmission Grid; and

(4)	Guidelines established by the ERCOT Board, which may be more stringent than those established by NERC for the secure operation of the ERCOT System.

5.2.3	Equipment Operating Limits

ERCOT Dispatch Instructions shall respect all equipment operating limits.  Except as stated in Section 5.6, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TDSP or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

The TDSP will notify ERCOT of any limitations on the TDSP’s system that may affect ERCOT Dispatch Instructions.  ERCOT shall continuously maintain a posting on the Market Information System (MIS) of any TDSP limitations that may affect Dispatch Instructions.  Any conflicts that cannot be satisfactorily resolved may be brought to ERCOT by any of the relevant affected Entities for investigation and resolution.

5.3	Routine Dispatch Duties of ERCOT

ERCOT will deploy Ancillary Services and dispatch transmission in accordance with these Protocols, including but not limited to Section 4, Scheduling, Section 5, Dispatch, and Section 6, Ancillary Services, respectively, including deploying Balancing Energy, Out of Merit (OOM), Replacement Reserve Resources, RMR Units, and Synchronous Condenser Units to ensure operational security and to remedy all Commercially Significant Constraints (CSC) and Operational Constraints.

ERCOT is the regional security coordinator for the ERCOT Region and is responsible for all regional security coordination as defined in the NERC Operating Manual and applicable ERCOT operating manuals or Operating Guides.

ERCOT may issue Dispatch Instructions to a TDSP (for the Real Time operation of Transmission Facilities) or to a QSE (for the Resources for which the QSE has scheduling responsibility.)

5.4	Dispatch Instructions

5.4.1	Control Area Operator Authority

ERCOT, as Control Area Operator (CAO), is authorized to take the following actions for the limited purpose of securely operating the ERCOT Transmission Grid in conformance with the standards specified in Section 5.2, Standards and Practices, including, but not limited to:

(1)	Direct the physical operation of the ERCOT System, including circuit breakers, switches, voltage control equipment, protective relays, metering and Load shedding equipment;

(2)	Call on Resources that have committed to provide Ancillary Services;

(3)	Direct changes in the operation of voltage control equipment;

(4)	Direct the implementation of OOM obligations and the use of RMR Service and transmission switching in order to prevent the violation of ERCOT System security limits; and

(5)	Take those additional actions required to prevent an imminent Emergency Condition or to restore the ERCOT System to a secure state in the event of an actual ERCOT System emergency.

5.4.2	Contents of Valid Dispatch Instructions

Dispatch Instructions consist of Verbal Dispatch Instructions and Dispatch Instructions issued via the Messaging System.

5.4.2.1	Verbal Dispatch Instructions

Valid verbal Dispatch Instructions shall contain the following information:

(1)	Identification of the responsible Entity and instructing authority (to include ERCOT operator’s and receiving operator’s names);

(2)	Specific Resources or TDSP Facilities that are the subject of the Dispatch Instruction;

(3)	Specific action required;

(4)	Current operating level or state of the Resources or TDSP Facilities that are the subject of the Dispatch Instruction;

(5)	Operating level or state to which such Resources or Facilities will be dispatched;

(6)	Time of notification of the Dispatch Instruction;

(7)	Time at which the QSE or TDSP is required to initiate the Dispatch Instruction;

(8)	Time within which the QSE or TDSP is required to complete the Dispatch Instruction; and

(9)	Other information relevant to the specific Dispatch Instruction.

5.4.2.2	Dispatch Instruction via the Messaging System

Valid Dispatch Instructions issued via the messaging system shall contain the following information:

(1)	Identification of the responsible Entity;

(2)	Specific Resources that are the subject of the Dispatch Instruction;

(3)	Specific action required;

(4)	Time of notification of the Dispatch Instruction via a timestamp on the Dispatch Instruction;

(5)	Time at which the QSE is required to initiate the Dispatch Instruction;

(6)	Time within which the QSE is required to complete the Dispatch Instruction; and

(7)	Other information relevant to the specific Dispatch Instruction.

5.4.3	Dispatch Instruction Procedures

The procedures for issuing and responding to Dispatch Instructions are as follows:

(1)	All Dispatch Instructions to Resources — whether for dispatch of Ancillary Services, System Emergencies or any other reason — shall be directed to the QSE responsible for the affected Resource.  ERCOT shall refrain from issuing dispatch instructions to generating units and other Resources undergoing testing with the exception of:

a)	Dispatch instructions that are a part of the testing; or

b)	During conditions when the generating unit is the only alternative for solving a transmission constraint; or

c)	During Force Majeure Events that threaten the reliability of the system.

(2)	Each QSE must immediately forward any valid Dispatch Instruction to the appropriate Resource or group of Resources or identify a reason for non-compliance to ERCOT in accordance with Section 5.4.4, Compliance with Dispatch Instructions.

(3)	If ERCOT believes that a Resource or group of Resources has inadequately responded to a Dispatch Instruction, ERCOT shall notify the relevant QSE.

(4)	The recipient of an oral Dispatch Instruction shall confirm the Dispatch Instruction by repeating it orally to ERCOT.

(5)	The recipient of a written or electronic Dispatch Instruction shall acknowledge receipt of the Dispatch Instruction to ERCOT in writing or electronically, within one (1) hour.

(6)	The recipient shall immediately request clarification of the Dispatch Instruction if the recipient fails to understand its responsibility under the Dispatch Instruction.

(7)	ERCOT shall record all voice conversations that occur in the communication of Dispatch Instructions.

(8)	ERCOT will record or file all written or electronic Dispatch Instructions and acknowledgements as soon as practicable after the issuance of the Dispatch Instruction.

(9)	By mutual agreement of the QSE and ERCOT, Dispatch Instructions to the QSE may be provided to the QSE’s designated agent.

(10)	By mutual agreement of the TDSP and ERCOT, Dispatch Instructions to the TDSP may be provided to the TDSP’s designated agent.

5.4.4	Compliance with Dispatch Instructions

(1)	Each TDSP and each QSE within the ERCOT System shall comply fully and promptly with valid Dispatch Instructions, unless in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols.

(2)	If the recipient of a valid Dispatch Instruction does not comply because in the sole and reasonable judgment of the TDSP or QSE, such compliance would create a threat to safety, risk of bodily harm or damage to the equipment, or is otherwise not in compliance with these Protocols, then, the TDSP or QSE must immediately notify ERCOT and provide the reason for non-compliance.

(3)	If the recipient of a Dispatch Instruction recognizes that the Dispatch Instruction conflicts with other valid instructions or is invalid, the recipient will immediately notify ERCOT of the conflict and request resolution.

(4)	Upon receipt of notice of non-compliance or conflict with Dispatch Instructions, ERCOT may, but is not required to, issue new Dispatch Instructions in response to the TDSP or QSE’s notice.

(5)	ERCOT’s final instruction in effect will apply for all Protocol-related processes. If the QSE does not comply after receiving the final instruction, the QSE shall remain liable for failure to meet its obligations under the Protocols and shall remain liable for any charges resulting from such failure.

(6)	ERCOT’s final instruction to a TDSP in effect will apply for all Protocol-related processes. If the TDSP does not comply after receiving the final instruction, the TDSP shall remain liable for such failure under these Protocols in accordance with the TDSP’s Agreement with ERCOT.

(7)	In all cases in which compliance with a Dispatch Instruction is disputed, both ERCOT and the QSE or TDSP shall document their communications, agreements, disagreements, and reasons for their actions, to enable resolution of the dispute through the ADR process in Section 20, Alternative Dispute Resolution.

5.5	Changes in ERCOT System Status

5.5.1	Changes in Resource Status

The QSE will notify ERCOT of an unplanned change in Resource status as soon as practicable following the change. The QSE representing the Resource will report any changes in Resource status to ERCOT in the Resource Plan by the beginning of the next hour following the change in status.

(1)	When the operating mode of a Generation Resource required to provide VSS’s AVR or PSS is changed while the unit is operating, the QSE shall promptly inform ERCOT.  The QSE shall also supply AVR or PSS status logs to ERCOT upon request.

(2)	Any short-term inability of a Generation Resource required to provide VSS to meet its reactive capability requirements shall be immediately reported to ERCOT and the TSP.

5.5.2	Changes in Transmission Facility Status

The TDSP will notify ERCOT of any changes in status of Transmission Facility elements as provided and clarified in the ERCOT procedures.  The TDSP will notify ERCOT of any other Transmission Facility status as soon as practicable following the change.  In addition, any short-term inability to meet minimum TSP or DSP reactive requirements shall be immediately reported to ERCOT by way of the TSP.

5.6	Emergency and Short Supply Operation

5.6.1	Introduction

ERCOT, as the single Control Area Operator, is responsible for maintaining reliability in normal and emergency operating conditions.  The Operating Guides are intended to ensure that minimum standards for reliability are maintained. Minimum standards for reliability are defined by the Operating Guides and the North American Electric Reliability Council (NERC) standards and include, but are not limited to:

(1)	Minimum operating reserve levels;

(2)	Criteria for determining acceptable operation of the frequency control system;

(3)	Criteria for determining and maintaining system voltages within acceptable limits;

(4)	Criteria for maximum acceptable transmission equipment loading levels; and

(5)	Criteria for determining when ERCOT is subject to unacceptable risk of widespread cascading outages.

In implementing these Protocols, ERCOT shall, to the fullest extent practicable, utilize market tools as prescribed in these Protocols before implementing command and control actions, such as OOMC, OOME, or RMR Service. It is anticipated that, with effective and timely communication, the tools available to ERCOT from the market will avert most threats to the reliability of the ERCOT System. However, these Protocols shall not preclude ERCOT from taking other actions to preserve the integrity of the ERCOT System.

5.6.2	Communication

Good, accurate, and timely communication between ERCOT, TDSPs, and QSEs is essential. The QSEs must be provided adequate information to make informed decisions and must receive the information with sufficient advance notice to facilitate generation and/or Load responses.

The type of communication ERCOT will issue will be determined primarily on the basis of the time available for the market to respond before an Emergency Condition occurs. The timing of these communications could range from days in advance to immediate. If there is insufficient time to allow the market to react, ERCOT may bypass one or more of the communication steps.

ERCOT shall consider the severity of the potential Emergency Condition as it determines which of the communications set forth in Section 5.6.3, Operating Condition Notice, through Section 5.6.6, Emergency Notice, to use. The severity of the Emergency Condition may be limited to an isolated local area affecting a small number of megawatts, or cover large areas affecting several hundred megawatts, or may be an ERCOT-wide condition potentially affecting all of the ERCOT Region.

The following sections describe the types of communications that will be issued by ERCOT to inform all QSEs and TDSPs of the operating situation. These communications may relate to transmission, distribution, and/or generation. The communications shall specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition.

5.6.3	Operating Condition Notice

ERCOT will issue an Operating Condition Notice (OCN) to inform all QSEs of a possible future need for more Resources due to conditions that could affect ERCOT System reliability. OCNs are for informational purposes only, and ERCOT exercises no extra operational authority with the issuance of this type of notice, but may solicit additional information from QSEs in order to determine whether the issuance of an Advisory, Alert, or Emergency Notice is warranted.

When time permits, ERCOT will issue an OCN before issuing an Advisory, Alert, or Emergency Notice.  However, issuance of an OCN may not require action on the part of any Market Participant, but rather simply serves as a reminder to QSEs and TDSPs that some attention to the changing condition may be warranted. OCNs serve to communicate to QSEs the need to take extra precautions to be prepared to serve the Load during times when contingencies are most likely to arise.

Reasons for OCNs include unplanned transmission outages, and weather related concerns such as anticipated freezing temperatures, hurricanes, wet weather, and ice storms.

ERCOT will monitor actual and forecasted weather for ERCOT and adjacent NERC regions. When adverse weather conditions are expected, ERCOT may confer with TDSPs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness.  Based on its assessment of the potential for adverse conditions, ERCOT may require information from QSEs representing Resources regarding their fuel capabilities.  Requests for this type of information shall be for a time period of no more than seven (7) days from the date of the request.  The specific information which may be requested shall be defined in the Operating Guides.  QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

QSEs and TDSPs are expected to establish and maintain internal procedures for monitoring actual and forecasted weather and for implementing appropriate measures when the potential for adverse weather or other conditions (which could threaten ERCOT System reliability) arise.

5.6.4	Advisory

ERCOT will issue an Advisory for informational purposes for the following reasons:

(1)	When it recognizes that conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability;

(2)	When weather or ERCOT System conditions require more lead-time than the normal Day Ahead market allows;

(3)	When communications or other controls are significantly limited; or

(4)	When ERCOT Transmission Grid conditions are such that operations within first contingency criteria as defined in the Operating Guides are not likely or possible because of Forced Outages or other conditions.

The Advisory communicates existing constraints.  ERCOT will notify TDSPs and QSEs. QSEs will notify appropriate Resources and LSEs.  ERCOT will communicate with TDSPs as needed to confirm their understanding of the condition and to determine the availability of Transmission Facilities.  For the purposes of verifying submitted information, ERCOT may communicate with QSEs.

Although an Advisory is for information purposes, ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities specified in the normal Day Ahead plan in accordance with scheduling procedures.  ERCOT may also increase the Day Ahead market to Two Days Ahead.  ERCOT may require information from QSEs representing Resources regarding their fuel capabilities.  Requests for this type of information shall be for a time period of no more than seven (7) days from the date of the request.  The specific information which may be requested shall be defined in the Operating Guides.  QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

5.6.5	Alert

ERCOT will issue an Alert when ERCOT determines:

(1)	That conditions have developed such that additional Ancillary Services are needed in the Operating Period;

(2)	That market Congestion Management techniques specified in these Protocols will not be adequate to resolve transmission problems; or

(3)	Forced Outages or other abnormal operating conditions occur which require operations outside first contingency security limits as defined in the ERCOT Operating Guides;

(4)	That there are insufficient AS bids.

ERCOT will post the Alert electronically and will notify all TDSPs and QSEs via the Messaging System of the posted Alert(s).

ERCOT must issue an Alert before acquiring Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services or Emergency Short Supply Non-Spinning Reserve Services.  With the issuance of an Alert pursuant to item (1) or (4) above, ERCOT may exercise its authority to immediately procure the following services from existing bids:

(1)	Regulation Services;

(2)	Responsive Reserve Services; and

(3)	Non-Spinning Reserve Services.

Emergency Short Supply Regulation Services, Emergency Short Supply Responsive Reserve Services or Emergency Short Supply Non-Spinning Reserve Services will be procured if there is insufficient availability of bids for any of the listed Ancillary Services.

ERCOT will post the Alert electronically on the MIS and will notify all TDSPs and QSEs via the Messaging System of the posted Alert(s).

Corrective actions identified by ERCOT shall be communicated through Dispatch Instructions to TDSPs and/or QSEs required to implement the corrective action.  Each QSE shall immediately notify the Market Participants that it represents of such Alert.  To minimize the effects on the ERCOT System, all TDSPs will identify and prepare to implement actions, including restoring outaged lines as appropriate and preparing for Load shedding.  ERCOT may instruct TDSPs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System.  On notification of an Alert, each QSE and TDSP will prepare for an emergency in case conditions worsen.  ERCOT may require information from QSEs representing Resources regarding their fuel capabilities.  Requests for this type of information shall be for a time period of no more than seven (7) days from the date of the request.  The specific information which may be requested shall be defined in the Operating Guides.  QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

5.6.6	Emergency Notice

ERCOT will issue an Emergency Notice only for the following reasons:

(1)	ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practicably obtainable from the market;

(2)	ERCOT is in an unreliable condition, as defined below;

(3)	Immediate action must be taken to avoid or relieve an overloaded transmission element; or

(4)	ERCOT varies from timing requirements or omits one or more scheduling procedures, as described in Section 4.8, Temporary Deviations from Scheduling Procedures.

The actions ERCOT takes during an Emergency Condition will depend on the nature and severity of the situation.

ERCOT is considered to be in an unreliable condition whenever ERCOT Transmission Grid status is such that the most severe single-contingency event presents the threat of uncontrolled separation or cascading outages and/or large-scale service disruption to Load (other than Load being served from radial transmission service) and/or overload of a critical transmission element, and no timely solution is obtainable from the market.

If the Emergency Condition is the result of a transmission problem that puts ERCOT in an unreliable condition, then ERCOT will act immediately to return ERCOT to a reliable condition, including instructing Resources to change output and instructing TDSPs to drop Load.

If the Emergency Condition is the result of a short supply situation, then the Emergency Electric Curtailment Plan procedures will be followed.

5.6.6.1	Emergency Electric Curtailment Plan (EECP)

At times it may be necessary to reduce electrical demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing demand during such emergencies, ERCOT will initiate and coordinate the implementation of the Emergency Electric Curtailment Plan following the EECP Steps set forth below in Section 5.6.7, EECP Steps.

The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.

ERCOT’s operating procedures shall meet the following goals while continuing to respect the confidentiality of market sensitive data:

(1)	Use of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT system;

(2)	Use of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(3)	Maximum use of ERCOT System capability;

(4)	Maintenance of station service for nuclear Generation Resource Facilities;

(5)	Securing of startup power for Generation Resources;

(6)	Operation of power Generation Resources during loss of communication with ERCOT;

(7)	Restoration of service to critical Loads in the manner defined in the Operating Guides; and

(8)	Restoration of service to all customers following major system disturbances, giving priority to the larger groups of customers.

ERCOT shall be responsible for coordinating with QSEs and TDSPs to monitor system conditions, initiating the EECP steps, notifying all QSEs, and coordinating the implementation of the EECP Steps while maintaining transmission security limits.

ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation.

During the EECP, ERCOT has the authority to obtain energy from BtB Ties or Block Load Transfers (BLTs) from non-ERCOT Control Areas when capacity is available.

Some of the EECP Steps will not be applicable if transmission security violations exist. There may be insufficient time to implement all Steps in sequence, but to the extent practicable, ERCOT will use Ancillary Services which bidders have made available in the market to maintain or restore reliability.

ERCOT may immediately implement Step 3 of the EECP any time the steady-state system frequency is below 59.8 Hz and will immediately implement Step 3 any time the steady-state frequency is below 59.5 Hz.

Percentages for Step 3 Load shedding will be based on previous year’s TDSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

5.6.6.2 	General Procedures Prior to EECP Operations

- Prior to declaring EECP Step 1 detailed in Section 5.6.7, EECP Steps, ERCOT shall:

(1)	Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability;

(2)	Issue Dispatch Instructions to QSEs to suspend any ongoing ERCOT required generating unit or Resource performance testing;

(3)	Utilize available resources providing Non-Spin Reserve Services that can be deployed to increase Responsive Reserves; and

(4)	ERCOT shall use the Reserve Discount Factor (RDF) for the purpose of monitoring Physical Responsive Capability (PRC).  The PRC will be used by ERCOT to determine the appropriate Emergency Notification and EECP Steps.

In addition, ERCOT may issue an appeal through the public news media for voluntary load reduction if authorized by the ERCOT Chief Executive Officer or its designee based on an evaluation of existing and expected system conditions.

5.6.7	EECP STEPS

Step 1 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal to 2300 MW.

ERCOT will:

(1)	Utilize available DC tie capability that is not already being used by the market;

(2)	 Notify the Southwest Power Pool Security Coordinator; and

(3)	Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency.

(4)	Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers.

QSEs will:

(1)  	Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency.

Step 2 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW Provided from LaaR Equal to 1750 MW.

In addition to measures associated with Step 1, ERCOT will:

(1)	Instruct TDSPs to reduce Customers load by using distribution voltage reduction measures, if deemed beneficial by the TDSP;

(2)	Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (controlled by high-set under-frequency relays);

(3)	With the approval of the affected Non-ERCOT control area, may instruct TDSPs to implement BLTs, which transfer load from the ERCOT control area to Non-ERCOT control areas.  Use of a BLT will be defined in the ERCOT Operating Guides; and

(4)	Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation.

Step 3 — Maintain system frequency at 59.8 Hz or greater

In addition to measures associated with Steps 1 and 2, ERCOT will direct all TDSPs and their agents to shed firm load, in 100 MW blocks, distributed as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hz.

In addition to measures associate with Steps 1 and 2, TDSPs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan.

5.6.7.1	Restoration of Market Operations

ERCOT shall continue EECP until sufficient bids are received and deployed by ERCOT to eliminate the conditions requiring the EECP.

5.6.8	Emergency Compensation

Deployment and compensation for OOMC and OOME Resources that ERCOT instructs for deployment due to a supply-related Emergency will be according to Section 6.8.2, Capacity and Energy Payments for Out of Merit Services.

There will be no compensation other than normal settlement methods to Loads in the event of Load shedding by the TDSP during EECP.

When energy is delivered to the ERCOT Control Area from a non-ERCOT Control Area through emergency instructions over a BtB Tie, the BtB Tie will be treated as a Resource receiving an OOME instruction via its QSE in the Congestion Zone where it is located.  For settlement purposes, the Resource Plan of the BtB Resource shall be set to zero.

When energy is delivered from the ERCOT Control Area through an emergency Dispatch Instruction over a BtB Tie, the BtB Tie will be treated as Load in the Congestion Zone in which the BtB Tie is located.  The QSE(s) representing the BtB Tie is responsible for any applicable fees and charges as described in Section 4.4.18.4, Settlement.

5.7	Block Load Transfers between ERCOT and Non-ERCOT Control Areas

Under Alert, EECP, or other Emergency Conditions, it may be necessary for ERCOT to request the implementation of Block Load Transfer (BLT) schemes which will transfer Loads normally located in the ERCOT Control Area to a Non-ERCOT Control Area.  Similarly, when Non-ERCOT Control Areas experience certain transmission contingency or short supply conditions; it may be necessary for ERCOT to agree to the implementation of BLT schemes which will transfer Loads normally located in a Non-ERCOT Control Area to the ERCOT Control Area.  BLTs will be restricted to the following conditions:

(1)	BLTs shall occur only under a specific Dispatch Instruction from ERCOT.

(2)	BLTs that are looped systems may be tied to the other Control Area’s electrical system through multiple interconnection points at the same time.  Transfers of looped configurations will be permitted only if all interconnection points are netted under a single ESI ID.  Individual meter points for looped system BLTs must be within the same Congestion Zone.

(3)	BLTs of Load to the ERCOT Control Area will be:

(i) 	treated as non-competitive wholesale Load in the ERCOT settlement system,

(ii) 	registered in a manner similar to that of NOIEs, and

(iii)	responsible for UFE allocations and Transmission Losses consistent with similarly situated NOIE metering points.

(4)	BLTs of Load to the ERCOT Control Area will be permitted only if such transfers will not jeopardize the reliability of the ERCOT System.  Under an ERCOT Emergency Notice, BLTs that have been implemented may be curtailed or terminated by ERCOT in order to maintain the reliability of the ERCOT System.

(5)	BLTs of Load from the ERCOT Control Area will be treated as a Resource in the ERCOT settlement system.

(6)	BLTs of Load from the ERCOT Control Area will be sent Dispatch Instructions only with the permission of the affected Non-ERCOT Control Area.  Under emergency conditions, BLTs that have been implemented may be curtailed or terminated by the Non-ERCOT Control Area in order to maintain the reliability of the Non-ERCOT system.

(7)	Restoration of service to outage customers using BLTs will be accomplished, as quickly as possible, if the transfers will not jeopardize the reliability of the ERCOT System and only under specific Dispatch Instruction from ERCOT.

(8)	The necessary Market Participant agreements, metering, and ERCOT settlement systems are in place prior to the implementation of any BLT.

(9)	Transmission BLT metering points utilized five (5) or more time per year, as monitored by the TDSP, will conform to ERCOT Polled Settlement (EPS) Metering requirements as defined in Section 10 of these Protocols and the Settlement Metering Operating Guides.  BLT metering points that are Distribution Systems or are transmission BLT metering points used less than five (5) times per year will be Revenue Quality Meters, Four (4) channel bi-directional kWh/kVARh, fifteen (15) minute Interval Data Recording (IDR) metering with remote interrogation.  ERCOT may impose additional metering requirements as deemed necessary to ensure ERCOT System reliability and integrity.

5.7.1	BLT Data Model in ERCOT Systems

Each BLT point which will transfer loads normally located in the ERCOT control area to a Non-ERCOT control area will be established as a pseudo generation facility and designated as such in ERCOT systems. Each BLT point which will transfer loads normally located in a Non-ERCOT control area to the ERCOT control area will have an ESI ID associated with it and will be treated as load in the ERCOT systems.

5.7.2	Registration of BLT Points

BLTs that block ERCOT Load into a Non-ERCOT Control Area will be treated as a Resource by ERCOT and assigned a Resource ID.  An ERCOT registered Resource Entity; with an ERCOT registered QSE affiliation must complete the applicable Asset Registration forms.  This Asset registration form along with the Metering Design Documentation will be the basis for establishing the ERCOT Data Model.

BLTs that block Non-ERCOT Load into the ERCOT Control Area will be treated as a non-competitive wholesale Load by ERCOT and assigned an ESID.  The TDSP associated to the BLT point has the responsibility for creation and maintenance of BLT ESI IDs.  Distribution BLTs points located behind NOIE metering points do not require an ESI ID.  An ERCOT registered LSE, with an ERCOT registered QSE affiliation, must be assigned to the ESI ID associated to BLT Point.

5.7.3	Scheduling & Operation of BLTs

BLTs will be treated as a Resource of the QSE associated with a BLT metering point.  However, the QSE will not be required to provide the real time data to ERCOT normally provided for Resources.  ERCOT shall confirm its availability with the Non-ERCOT Control Area or the TDSP prior to issuing any Dispatch Instructions to the QSE and the TDSP.  Any energy delivered under such a Dispatch Instruction shall be treated as an OOME Dispatch Instruction to the QSE.  For settlement purposes, the Dispatch Instruction will be treated as an instructed deviation, and the Resource Plan of the BLT Resource shall be set to zero.

Generation Resources connected to the ERCOT Region included in the BLT are under no obligation to provide Ancillary Services or any other services while that transmission area is connected to a non-ERCOT Control Area other than through a BtB Tie.

The QSE of the LSE assigned to the ESI ID associated with a BLT point will include that Load in its Balanced Schedules.

5.7.4	Settlement of BLT Points

When ERCOT load is blocked into a Non-ERCOT control area, the energy delivered to ERCOT load through a BLT will be treated as generation into the Congestion Zone in the settlement system.  The generation and dispatch instruction will be attributed to the Resource registered for that BLT point.  ERCOT customers, customer’s REPs, and REP’s QSEs served by a Non-ERCOT control area through a BLT will not be impacted by the switch to a Non-ERCOT resource.  ERCOT will settle with all parties through the ERCOT settlement process.

When a Non-ERCOT control area load is blocked into ERCOT, the energy delivered to the Non-ERCOT control area through a BLT will be treated as load in the Congestion Zone in the settlement system.  The QSE of the LSE assigned to the ESI ID associated with the BLT point load is responsible for any applicable fees and charges as described in Section 9, Settlement and Billing.

5.8	BtB Ties and BLTs with the CFE Control Area

Under Alert, EECP or other Emergency Condition which may negatively affect the reliability of the ERCOT System, it may be necessary for ERCOT to request energy to be delivered from BtB Ties and BLTs with the CFE Control Area in accordance with an agreement between CFE and ERCOT.

Similarly, when the CFE Control Area experiences certain reliability contingency or short supply conditions, it may be necessary for ERCOT to allow energy to be delivered to the CFE Control Area.

Deliveries to and from the CFE Control Area over the CFE/ERCOT BtB Ties or in the form of Block Load Transfers shall be restricted to the following conditions:

(1)	Deliveries of energy from the ERCOT Control Area to the CFE Control Area will be permitted only if such transfers do not jeopardize the reliability of the ERCOT System.  Under an Advisory, Alert, EECP or other Emergency Condition, ERCOT may curtail or terminate deliveries to CFE that have been scheduled or implemented in order to maintain the reliability of the ERCOT System.

(2)	Under Emergency Conditions, CFE may curtail deliveries to the ERCOT Control Area in order to maintain the reliability of the CFE system.

5.9	Frequency Response Requirements and Monitoring

5.9.1	Generation Resource and QSE Participation

5.9.1.1	Governor in Service

At all times a Generation Resource is on line, its turbine governor shall remain in service and be allowed to respond to all changes in system frequency.  Generation Entities shall not reduce governor response on individual Resources during abnormal conditions without ERCOT’s consent (conveyed by way of the Generation Entity’s QSE) unless equipment damage is imminent.

5.9.1.2	Reporting

Generation Entities shall conduct applicable generating governor speed regulation tests on Resources as specified in the Operating Guides.  Test results and/or other relevant information shall be reported to ERCOT and ERCOT shall forward results to the appropriate TSPs.

Resource governor modeling information required in the ERCOT Planning Criteria shall be determined from actual Resource testing described in the Operating Guides.  Within thirty (30) days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the connected TSP.

When the governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT.  The QSE shall also supply governor status logs to ERCOT upon request.

Any short-term inability of a Generation Resource to supply governor response shall be immediately reported to ERCOT.

If a Generation Resource trips Off-line due to governor response problems, the Generation Entity shall immediately report the change in the status of the Resource to ERCOT and the QSE.

5.9.2	Primary Frequency Control Measurements

For the purposes of this section, the A Point is the last stable frequency value prior to a frequency disturbance.  For a decreasing frequency event with the last stable frequency value of 60.000 Hz or below, the actual frequency is used.  For a decreasing frequency event with the last stable frequency value between 60.000 and 60.036 Hz, 60.000 Hz will be used.  For a decreasing frequency event with the last stable frequency value above 60.036 Hz, actual frequency will be used.  For an increasing frequency event with the last stable frequency value of 60.000 or above, the actual frequency is used.  For an increasing frequency event with the last stable frequency between 59.964 and 60.000 Hz, 60.000 Hz will be used.  For an increasing frequency event with the last stable frequency value of 59.964 or below, the actual frequency is used.  ERCOT shall determine the A Point frequency for each event.

For the purposes of this section, the C Point is the lowest frequency value during the first five seconds of the event.

For the purposes of this section, the B Point is the “recovery” frequency value after the C Point.   The B Point should occur after full governor response of the turbines has occurred, usually between ten (10) and thirty (30) seconds after the A Point, but not greater than sixty (60) seconds after the A Point.  ERCOT shall determine the B Point for each event.

B Point Plus Thirty Seconds: At thirty seconds following the B Point, an analysis will be performed by ERCOT with the assistance of the appropriate ERCOT subcommittee to determine if primary frequency control response is sustained.

For the purposes of this section, a “Measurable Event” is the sudden change in interconnection frequency that will be evaluated for performance compliance will have i) a frequency B Point between 59.700 Hz and 59.900 Hz or between 60.100 Hz and 60.300 Hz, and ii) a difference between the B Point and the A Point greater than or equal to +/- 0.100 Hz.

5.9.2.1	ERCOT Required Primary Frequency Control Response

The combined response of all Generation Resources interconnected in ERCOT to a Measurable Event shall be at least 420 MW / 0.1 Hz. This value should be reviewed on an annual basis by ERCOT and the appropriate ERCOT subcommittee for system interconnect reliability needs.

ERCOT will evaluate, with the assistance of the appropriate ERCOT subcommittee, primary frequency control response during Measurable Events.  The actual Generation Resource response will be compiled to determine if adequate primary frequency control participation was available.

ERCOT and the appropriate ERCOT subcommittee will review each Measurable Event, verifying the reasonableness of data.  Data that is in question may be requested from the QSE for comparison and/or individual Resource data may be retrieved from ERCOT’s database.

ERCOT’s performance will be averaged using the most recent six (6) Measurable Events to determine its rolling average contribution.

5.9.3	ERCOT Data Collection

5.9.3.1	Data Collection

ERCOT will collect all data necessary to analyze each Measurable Event.  This will include the following real-time data:

(1)	Interconnection Frequency;

(2)	Regulation Service deployed;

(3)	Responsive Reserve Service deployed;

(4)	QSE available  Responsive Reserve Service;

(5)	QSE total Generation;

(6)	QSE SCE;

(7)	QSE Bias;

(8)	QSE LaaR MW;

(9)	LaaR deployed;

(10)	QSE Responsive Reserve Service; and,

(11)	ERCOT Load and individual Resource(s) that contributed to the frequency deviation.