Texas Nodal

Market Management Systems (MMS)

Requirement Specification For RUC

Version 0.9.1

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 06/29/2006 | 0.1.0 | Initial Draft, for delivery to prospective vendor | Hailong Hui Brandon Whittle |
| 07/14/2006 | 0.2.0 | Second Draft, for delivery to prospective vendor | Hailong Hui Brandon Whittle |
| 08/04/2006 | 0.3.0 | Updated to incorporate the discussions in ERCOT/ABB RUC team during the period from 07/25/06 to 08/04/06. | Chien-Ning Yu (ABB) |
| 08/21/2006 | 0.4.0 | Revised according to the agreement reached in ERCOT/ABB RUC team during the meeting from 08/08/06 to 08/10/06 Add mathematical formulation | Chien-Ning Yu (ABB) Shu Tao (ABB) |
| 08/28/2006 | 0.5.0 | Revised according to the agreement reached in ERCOT/ABB RUC team during the meeting from 08/25/06 | Shu Tao (ABB) Art Cohen (ABB) Chien-Ning Yu (ABB) |
| 09/07/06 | 0.6.0 | Revised based on the ERCOT final review on 09/06. | Chien-Ning Yu (ABB) |
| 09/15/06 | 0.7.0 | ERCOT modifications ABB added a requirement for tie-breaking situation handling. | Brandon Whittle Sai Moorty Chien-Ning Yu (ABB) |
| 10/04/06 | 0.8.0 | Add Sections 1.7 and 1.8 per ERCOT request | Mary Nelson |
| 11/01/06 | 0.9.0 | Revised based on IDA comments Update Section 1, Version Control and Naming Conventions per ERCOT Requirements | Hailong Hui Chien-Ning Yu (ABB) Mary Nelson (ABB) |
| 11/02/2006 | 0.9.1 | Minor Changes | Chien-Ning Yu (ABB) |

Table of Contents

1.	Introduction	6

1.1	Purpose	6

1.2	Objective	6

1.3	Traceability	6

1.4	Market Management System Requirement Documents	6

2.	Reliability Unit Commitment	7

2.1	RUC Inputs and Outputs	8

2.2	RUC Solution Sequence	12

2.3	Reliability Unit Commitment (RUC) Functional Diagram	13

2.4	Preconditions and Dependencies	13

3.	Functional Requirements	15

3.1	RUC Process Objective	15

3.1.1	Execute RUC in DRUC Mode	15

3.1.2	Execute RUC in HRUC Mode	16

3.1.3	Execute RUC in WRUC Mode	16

3.2	Module: RUC Input and Initialization	17

3.2.1	Input from COP	17

3.2.2	Input from Wind-Powered Generation Resource Production Potential (WGRPP)	17

3.2.3	Input from Resource Parameters	18

3.2.4	Three-Part Offers Input	18

3.2.5	Three-Part Offers Validation	19

3.2.6	Three-Part Offers for RMR Resources	19

3.2.7	Create Three-Part Offers for Non-Bid Resources	20

3.2.8	Adjust Three-Part Offers in HRUC for QSE Request Decommitment in Adjustment Period	21

3.2.9	Create Proxy Energy Offer Curves	21

3.2.10	Mitigated Offer Cap	22

3.2.11	Load Forecast as Input	22

3.2.12	Bus Load Forecast	23

3.2.13	Input from Forced Outage Information	23

3.2.14	Input from Outage Scheduler Information	23

3.2.15	Retrieve Dynamic Rating Data	23

3.2.16	Retrieve Generic Constraints	24

3.2.17	Input from Ancillary Service Certification	24

3.3	Module: Operator Control and Override	24

3.3.1	Override Load Forecast	24

3.3.2	Pause and Review/Override Input/Output between Any Phases	25

3.3.3	Calculate Ancillary Service Insufficiency	25

3.3.4	Calculate Resource Ancillary Service Capability	25

3.3.5	Procure Ancillary Service for DAM/SASM AS Offers Insufficiency	26

3.3.6	Deselect Standard Contingencies	26

3.3.7	Review/Deselect NSM Constraint Violations	27

3.3.8	Manually Commit/Decommit Resources on MOI/UI	27

3.3.9	Manually Override SCUC Commitment/Decommitment on MOI/UI	28

3.4	Module: Initial Unit Commitment (IUC)	28

3.5	Module: Network Topology Builder	28

3.5.1	Breaker Status Projection	28

3.5.2	Initial Resource Commitment Status Determination	29

3.5.3	Resource Status Projection for HRUC	29

3.5.4	Resource Status Projection for DRUC and WRUC	30

3.6	Module: Network Security Monitor (NSM)	30

3.6.1	NSM Overview	30

3.6.2	Use of Dynamic Ratings in NSM	32

3.6.3	Identify Violated/Nearly Violated Constraints in NSM	32

3.6.4	NSM Sensitivity Cutoff Threshold	32

3.6.5	NCUC-NSM Solution Process	33

3.7	Module: Security Constrained Unit Commitment (SCUC)	34

3.7.1	Use SCUC for RUC Process	34

3.7.2	Commit Resources in SCUC	35

3.7.3	Decommit Resources in SCUC	35

3.7.4	Filter/Restrict Resource Decommitment	35

3.7.5	Constraint Penalty Function	36

3.7.6	Tie Breaking Rules for RUC Dispatch	36

3.7.7	Modeling Resource Capacity Providing Ancillary Service	37

3.7.8	Modeling Combined Cycle Resources Configuration	37

3.7.9	Modeling DC Tie Schedule	38

3.7.10	Modeling Split Generation Resources	38

3.7.11	Modeling Off-line Time Dependent Start up Cost	38

3.7.12	Resource Constraints	38

3.7.13	Additional Resource Constraints for WRUC	39

3.7.14	Transmission Constraints	39

3.7.15	Power Balance Constraints	39

3.7.16	Resource Status	39

3.7.17	Ignore Temporal Constraints Violation for QSE-Commitment intervals	40

3.7.18	RUC Startup Cost Eligibility	40

3.8	Module: RUC Output and Dispatch	40

3.8.1	RUC Commitment/Decommitment Output	40

3.8.2	Operator Confirmation RUC Decommitment	41

3.8.3	Operator Approval RUC Commitment	41

3.9	Decision Support for QSE Request Decommitment in HRUC	41

3.9.1	Active and Binding Transmission Constraints	42

3.9.2	Infeasible Ancillary Service Capacity Output	42

3.9.3	Dispatch Resource	42

3.9.4	Additional Output for WRUC	42

3.9.5	WRUC Commitment Result	43

3.9.6	Provide Necessary Information on MOI/UI	43

3.9.7	Create Suggestion Plan for Unresolved Constraints	43

3.10	Module: Save Case	44

3.10.1	Save Cases	44

3.11	RUC in Study Mode	44

3.11.1	Execute RUC in Study Mode	44

4.	Supplementary Requirements	46

4.1	Performance Requirements	46

4.1.1	Market Participant Interface Specific Performance Requirements	46

4.1.2	Market Application Specific Performance Requirements	46

5.	Use Cases	48

5.1	Actor Catalog	48

5.2	Use Case Catalog	48

5.3	Use Cases Listing	49

6.	Protocol Coverage	50

7.	Sub-Process Coverage	55

8.	Appendix: RUC Mathematical Formulation	56

9.	Appendix: Acronyms	63

Requirements Specification

(This Requirements Document is Subordinate To and Compliant with the Texas Nodal Protocols effective May, 2006.)

# Introduction

The primary authority directing the operational characteristics and behavior of the Market Management System is the Texas Nodal Protocols.  This requirements document set is provided as a supplement to assist in the implementation of this system which includes all processes, tools (hardware and software), and operations and constraints necessary for full compliance to the Texas Nodal Protocols.  The Texas Nodal Protocols with this set of requirements documents completes the System “Design To” definition for implementation, test, and operation of a fully compliant Market Management System.

This set of requirements documents consists of five (5) documents as listed in the Market Management Systems Requirement Documents section which follows.

## Purpose

The requirements for the document Texas Nodal Market Management Systems (MMS) Requirement Specification For RUC and its associated processes are described in the Texas Nodal Protocols.  This supplemental specification describes the external behavior of this specific sub-system.  The Texas Nodal Protocols (Protocols) and this document together with all applied vendor provided products’ functional specifications, describe both functional and nonfunctional requirements, design constraints, and other factors, in order to provide a complete and comprehensive description of the operational performance to be delivered.  All statements or requirements specified in this document are subordinate to the Protocols.

## Objective

The objective of this set of documents is to provide a clear, concise and unambiguous set of requirements together with the Texas Nodal Protocols which provides the complete required technical description of this Texas Nodal Sub-System to allow the developer/implementer to deliver a fully operational, compliant and robust Texas Nodal System.

## Traceability

All requirements are traceable to the Nodal Protocols, and/or regulations such as NERC and FERC.

## Market Management System Requirement Documents

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For Day-Ahead Market (DAM) and Supplemental Ancillary Service Market (SASM)

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For RUC

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For SCED and Real-Time MMS Processes

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For Constraint Competitiveness Test (CCT)

  - Texas Nodal Market Management Systems (MMS) Requirement Specification For Overall MMS System and Other Processes

# Reliability Unit Commitment

The Reliability Unit Commitment (RUC) process determines commitment of Generation Resources to match the forecasted system demand, subject to transmission constraints and Resource constraints.  The RUC process commits additional Generation capacity on top of Resources already committed in previous RUCs, Resources self-committed in the COPs and Resource capacity already committed to provide Ancillary Service. The RUC process can also decommit Resources; however, RUC may only decommit a Resource to resolve transmission constraints that are otherwise irresolvable.

There are three RUC processes used in the ERCOT nodal market implementation:

- Day-Ahead RUC (DRUC): The DRUC process runs daily after the close of the Day-Ahead Market (DAM).  The RUC Study Period for DRUC is the next Operating Day. DRUC uses Three-Part Supply Offers submitted before the DAM by QSEs that were considered in the DAM but not awarded in the DAM.

- Hourly RUC (HRUC): The HRUC process runs every hour and its Study Period for HRUC is either (1) the balance of the current Operating Day if the DRUC for the current Operating Day has not been solved or it is for (2) the balance of the current Operating Day plus the next Operating Day if the DRUC for the current Operating Day has been solved. The HRUC process executes at least one hour before the Operating Hour to fine-tune the Resource commitments using updated Load forecasts and updated Outage information.

- Weekly RUC (WRUC): The WRUC process is an eight day look-ahead planning tool.  It is used to help ERCOT to manage Generation Resources having start up times longer than the DRUC or HRUC study periods.

Figure 2-1 RUC Timeline Summary

## RUC Inputs and Outputs

This section provides a summary of inputs and outputs to the Reliability Unit Commitment (RUC). Table 2-1 lists all the required input data to RUC. The “Source” column of the input table identifies the source where the data is provided to the RUC. The Market Infrastructure (MI) listed in the table is a sub-system of the Market Management System. MI provides various functions to support QSEs data submission and validation. All the validated QSE market data are stored in the MI market database as input to RUC.

Table 2-1 RUC Inputs

| Source | Data |
| --- | --- |
| Registration | - Resource Parameters - Resource Name - Resource Type - QF status, - Minimum On-line time - Minimum Off-line time - Normal Ramp rate curve - Emergency Ramp rate curve - Hot start time - Intermediate start time - Cold start time - Maximum On-line time (Seasonal) - Maximum daily starts (Seasonal) - Hot-to-intermediate time (Seasonal) - Intermediate-to-cold time (Seasonal) - Maximum weekly starts (Seasonal) - Maximum weekly Energy (Seasonal) - Resource-QSE mapping - Resource Commercial Operation Date |
| Market Infrastructure (MI) | - COP (from QSE) - Expected On-line status - Expected Off-line status - High Sustained Limit (HSL) - Low Sustained Limit (LSL) - High Emergency Limit (HEL) - Low Emergency Limit (LEL) - Ancillary Service capacity in MW - Combined Cycle Resource Configuration identification - DC Tie Schedule (from QSE submitted in a form of COP) - Three-Part Supply Curve (from QSE) - Resource ID - QSE ID - Start Up Cost (hot, intermediate, cold) - Minimum Energy Offer - Energy Offer curve (price vs. quantity) - Percentage of FIP - Percentage of FOP - RMR Resource Three-Part Offer (from ERCOT Operators) - Resource ID - QSE ID - Start Up Offer (hot, intermediate, cold) - Minimum Energy Offer - Energy Offer curve (price vs. quantity) - Percentage of FIP - Percentage of FOP - Combined Cycle offer data (from QSE) - Start up Transition flag (Yes/No) - Shutdown Transition flag (Yes/No) - Allowed Transitions - Minimum On-Line Time for the entire Combined-Cycle plant - Maximum On-Line Time for the entire Combined-Cycle plant - Minimum Off-Line Time for the entire Combined-Cycle plant - Energy Offer curve (price vs. quantity) - Minimum Energy Offer - Start up Cost (hot, Intermediate, cold) - Three-part offers accepted in DAM - Ancillary Service Plan (from ERCOT Operator) - Total Ancillary Service quantity for each Ancillary Service class accepted in DAM and SASM - Total self-scheduled Ancillary Service quantity for each class - Previous RUC commitment schedule - Mitigated Offer Cap curve (the detailed Mitigated Offer Cap curve calculation is documented in MMS Requirement for SCED and MMS Real-Time Process.) - Mitigated Offer cap and quantity |
| Settlement System | - Ancillary Service Certifications - Verifiable start up/minimum energy costs - Generic start up/minimum energy costs - Fuel index price (FIP) - Fuel Oil price (FOP) - Verifiable heat rate curve - Verifiable O&M - Capacity Factor |
| Outage Scheduler | Outage schedule (Forced Outage data included) |
| Network Model Management System (NMMS) | - Network Model - Standard Contingency List - Unique Contingency Sequence ID - Unique Contingency Title - Station ID - Equipment ID - Equipment Type - Contingency Priority - Load Rollover definition |
| Energy Management System (EMS) | - Dynamic Ratings/Static Ratings for transmission equipment - Normal Limit - Emergency Limit - Load Shedding Limit - Generic constraints (interface import/export constraints for voltage/stability) - Pre-defined Constraints (a check list of transmission equipment) - Current Resource Commitment status - Current On-line/Off-line status - Historical Resource Commitment status - Length of time resource has been On-line/Off-line - Number of startups for the current Operating day - Load Distribution Factor - Current Breakers and switches status - Breaker or switch ID - Status (close/open) - Mid-Term Load Forecast (MTLF) - Day-ahead load forecast for DRUC - Current hourly load forecast for HRUC - Next seven day load forecast for WRUC |

Table 2-2 lists outputs from RUC to various systems. The “Destination” column of the output table identifies the destination target for the data generated by RUC.  Note that the Market Infrastructure (MI) system stores the RUC outputs listed in the table and makes them available to the following:

- QSE: MI data will be used to generate report to QSEs.

- MIS: MI data will be available for ERCOT to post in MIS Secure Area

- Settlement: MI data will be pushed to Settlement system for settlement calculation

Table 2-2 RUC Outputs

| Destination | Data |
| --- | --- |
| Market Infrastructure (MI) | - RUC time stamp - RUC cleared commitment (to Settlement, QSE, MIS) - RUC cleared decommitment and the corresponding reason code (to Settlement and QSE, MIS) - Binding transmission constraints identified in RUC process (MIS) - De-selected contingencies from the standard contingency list prior to RUC execution ( MIS) - De-selected contingencies/constraints during the NSM-SCUC iterations (MIS) - Infeasible Resource Ancillary Service Capacity (to QSE) |
| Market Operator Interface (MOI) | - A summary of RUC cleared commitment and decommitment schedule - RUC recommendation (“accept” or “reject”) on QSE’s decommitment requests. - Infeasible Ancillary Service summary display - Alarm messages for any constraints that RUC could not resolve - Resource not committed in DRUC or HRUC study period but committed in WRUC study period (for WRUC only) - Suggestion Plan for un-resolved transmission Constraints as described in FR69 |

## RUC Solution Sequence

The RUC solution sequence is comprised of seven major sub-functions to support all the scheduling functions

- Dispatch Scheduler Initialization (DSI): retrieves and prepares input data.

- Network Data Processor (NDP): sets up the electrical network data required for security assessment

- Initial Unit Commitment (IUC): determines the initial Unit Commitment solution for Network Security Monitor (NSM) sub-function to perform security assessment.

- Network Security Monitor (NSM): determines if a given dispatch schedule is secure and, if the system is not secure, generates constraint equations to be passed on to the Network Constrained Unit Commitment (NCUC) sub-function to enforce.

- Network Constrained Unit Commitment (NCUC): determines the most economical schedule given the various constraints including the constraints passed to it from NSM sub-function

- Dispatch Scheduler Publishing (DSP): disseminates the Resource commitment schedule and related data to the Market Infrastructure (MI) system.

- Save Case (SAV): saves inputs and outputs of the Dispatch Engine in save cases for future analysis

## Reliability Unit Commitment (RUC) Functional Diagram

The RUC process is used to commit additional Generation capacity on top of Resources committed in the previous RUCs, Resources self-committed in the COPs and Resource capacity already committed to provide Ancillary Service.

The RUC considers capacity requirements for each hour of the RUC Study Period with the objective of minimizing costs based on Three-Part Supply Offers where proxy Energy Offer Curves are substituted for the bid Energy Offer Curve. The proxy Energy Offer Curve is calculated in a way that minimizes the effect of the proxy Energy Offer Curves on the optimization.

Figure 2-2 provides a high-level functional diagram for RUC process.

Figure 2-2 High Level RUC Functional Diagram

## Preconditions and Dependencies

The Reliability Unit Commitment (RUC) process is a critical function that ensures enough Resource capacity is committed, in addition to the available Ancillary Service capacity to meet the system's security requirements. The accuracy of the RUC solution depends on the accuracy of the forecasted load provided by Mid-Term Load Forecast (MTLF) function and the ERCOT network model data provided by the Network Model Management System (NMMS).

The functionality and requirements specified in this document are based on the following preconditions:

- Ancillary Service Certifications are provided by the Settlement system as inputs to RUC.

- Resource Ramp Rate constraints are ignored in the RUC calculation.

# Functional Requirements

## RUC Process Objective

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(1), 5.5.2(1) |
| Traceability to Sub-Process Maps | RUC |
| Description The RUC shall be used to ensure that enough Resource capacity, in addition to Ancillary Service capacity, is committed in the right locations to reliably serve the forecasted system demand while ensuring Transmission System reliability. |  |

### Execute RUC in DRUC Mode

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(2), 5.1(3), 5.1(6), 5.3 (1) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall conduct the Day-Ahead RUC (DRUC) each day. The DRUC Study Period shall cover the next Operating Day, i.e., 24 hours for the normal day and 23 hours or 25 hours for the daylight saving time transition days. The time step for each DRUC interval shall be one hour. The DRUC shall be run after the close of DAM. The DRUC shall be executed after the QSE data submission deadline (1430). The DRUC execution shall be invoked manually by ERCOT Operators since the Operators need to review results in different stages of the execution. |  |

### Execute RUC in HRUC Mode

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(2), 5.1(5), 5.1(6) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall conduct the Hourly RUC (HRUC) before each hour of the Operating Day. The HRUC Study Period shall cover the balance of the current Operating Day if the DRUC for the current Operating Day has not been solved. The HRUC Study Period shall cover the balance of the current Operating Day plus the next Operating Day if the DRUC for the current Operating Day has been solved. The MMS shall correctly model the daylight saving time transition effect in the HRUC Study Period. The first study hour of the HRUC shall be the next Operating hour. The time step for each HRUC interval shall be one hour. The HRUC execution shall be invoked at the beginning of each hour by ERCOT Operators to ensure the HRUC results available to all QSEs in a timely manner. The MMS shall allow Operators to abort the HRUC execution when the current HRUC execution cannot be completed in time due to human delay or software errors and impacts on the next HRUC execution. |  |

### Execute RUC in WRUC Mode

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | 5.5.2(8)(j) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall conduct the Weekly RUC (WRUC). The WRUC Study Period shall cover the next seven Operating Days not including the current Operating Day (i.e., the time for which ERCOT has a COP and Load forecast). The time step for each WRUC interval shall be one hour. The WRUC execution shall be invoked manually by ERCOT Operators. |  |

## Module: RUC Input and Initialization

### Input from COP

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(e), 5.3(2), 3.9, 5.5.2(1), 5.5.2(5), |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall use the inputs data from the COP. The input data shall include the following: - The name of Resource - Expected Resource On-line Status - Expected Resource Off-line Status - High Sustained Limit (HSL) - Low Sustained Limit (LSL) - High Emergency Limit (HEL) - Low Emergency Limit (LEL) - Ancillary Service capacity in MW (Reg-Up, Reg-Down, Responsive Reserve Service and Non-Spin) - Combined Cycle Resource configuration identification |  |

### Input from Wind-Powered Generation Resource Production Potential (WGRPP)

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 3.13, 4.2.2 |
| Traceability to Sub-Process Maps | RUC |
| Description The QSEs of Wind-powered Generation Resources (WGR) shall update the HSL in COPs based on the Resource Production Potential (RPP) forecast, which is prepared by ERCOT using the information from Short-Term Wind Power Forecast (STWPF). The MMS shall incorporate the WGR RPP in the RUC scheduling by using the HSL information from the COPs submitted by QSEs. |  |

### Input from Resource Parameters

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(f), 3.7.1.1 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall use the Resource Parameter data from the Registration System. The input data shall include the following: - Resource name - Type of Resource - QF status - Normal Ramp Rate Curve - Emergency Ramp Rate Curve - Minimum On-Line time - Minimum Off-Line time - Hot start time - Intermediate start time - Cold start time - Maximum On-Line time (Seasonal) - Maximum daily starts (Seasonal) - Hot-to-intermediate time (Seasonal) - Intermediate-to-cold time (Seasonal) - Maximum weekly starts (Seasonal and for WRUC only) - Maximum weekly energy (Seasonal and for WRUC only) Note that the Normal Ramp Rate curve and Emergency Ramp Rate curve are needed for the available Ancillary Service capacity calculation as a post processing. |  |

### Three-Part Offers Input

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(4), 5.4(2), 5.1(8), 5.5.2(8)(g)&(h) |
| Traceability to Sub-Process Maps | RUC |
| Description For the DRUC study, the MMS shall only use QSE-submitted Three-Part Supply Offers that were submitted before the DAM and considered in the DAM but were not awarded in the DAM. For each HRUC study, the MMS shall use Three-Part Supply Offers submitted by QSEs before the end of the Adjustment Period. For the WRUC study, the MMS shall create Three-Part Supply Offers for all Resources following the rules specified in FR11. |  |

### Three-Part Offers Validation

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.3(3)(a)(i), 4.4.9.1 and 4.4.9.2 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall validate Three-Part Supply Offers according to NP 4.4.9.2.2, Startup Offer and Minimum-Energy Offer Validation, before RUC execution. The MMS shall reject the offer if the startup costs are more than the approved verifiable Resource-specific Startup Cost. The MMS shall reject the offer if the startup costs are more than the Resource Category Generic Startup Cost and if there is no approved verifiable Startup Cost. The MMS shall reject the offer if the Minimum-Energy Cost is more than the approved verifiable Resource-specific Minimum-Energy Cost. The MMS shall reject the offer if the Minimum-Energy Cost is more than the Resource Category Generic Startup Cost and if there is no approved verifiable Minimum-Energy Cost. Please refer to DAM Requirement ID: VA10 for detailed validation rules. |  |

### Three-Part Offers for RMR Resources

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 6.4.2(2), 6.4.3(2), 4.4.9.2.3(k), 4.4.8, NP22 Attachment F |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall allow ERCOT Operators to enter Three-Part Supply Offers for RMR Resources. (Refer to DAM Business Requirement Section – ST1-RMR for details on RMR offer input.) For the DRUC study, the MMS shall only use RMR Three-Part Supply Offers entered by ERCOT that were considered in the DAM but not awarded in the DAM. For the HRUC study, the MMS shall use RMR Three-Part Supply Offers entered by ERCOT before the end of the Adjustment Period. For the WRUC study, the MMS shall create Three-Part Supply Offers for all Resources including RMR Resources following the rules specified in FR11. |  |

### Create Three-Part Offers for Non-Bid Resources

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(6), 4.4.9.2.3, 5.5.2(8)(h), 5.6.1 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall create Three-Part Supply Offers for the following Resources: For DRUC: - A Resource which: - did not submit a Three Part Supply Offer in DAM, - is specified as Off-Line but available in the COP with Resource Status OFF, and - does not have EMR Resource Status - A Resource which: - submitted a Three Part Supply Offer in DAM and the Offer was accepted, - is specified as Off-Line but available in the COP with Resource Status OFF, and - does not have EMR Resource Status For HRUC: - A Resource which: - did not submit a Three Part Supply Offer in the adjustment period - is specified as Off-Line but available in the COP with Resource Status OFF, and - does not have EMR Resource Status For WRUC: - A Resource which: - is specified as Off-Line but available in the COP with Resource Status OFF, and - does not have EMR Resource Status For such Resources, the system shall use in the RUC process 150% of any approved verifiable startup cost and verifiable minimum-energy cost or if verifiable costs have not been approved, the applicable Resource Category Generic Startup Offer Cost and the applicable Resource Category Generic Minimum-Energy Offer Cost registered with ERCOT. The adjustment factor (150%) shall be configurable by authorized users. This approach is intended to encourage QSE to submit Three-Part Supply Offer instead of using the Verifiable/Category Generic Cost. |  |

### Adjust Three-Part Offers in HRUC for QSE Request Decommitment in Adjustment Period

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP6.4.6.2 |
| Traceability to Sub-Process Maps | RUC |
| Description The HRUC shall set the Resource’s Startup Offer to zero for the Resource requesting decommitment. The HRUC shall identify a Resource’s decommitment request if: - The Resource’s COP status changed from On-line to Off-line available during the Adjustment Period and - There was no previous HRUC decommitment instruction issued for the Resource. If a Resource is identified as requesting decommitment, then the HRUC commitment must consider the Resource’s Minimum-Energy Offer excluding the Resource’s Startup Offer from the Three-Part Supply Offer. |  |

### Create Proxy Energy Offer Curves

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(4), 4.4.9.4.1, 5.1(8) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall calculate proxy Energy Offer Curves based on the Mitigated Offer Caps, for the type of Resource, for use in the RUC to determine the projected energy output level of each Resource and to project potential congestion patterns for each hour of the RUC. The MMS shall calculate proxy Energy Offer Curves by multiplying the Mitigated Offer Cap by a configurable constant and applying the cost for all Generation Resource output between HSL and LSL. The constant shall not be more than 0.001 and shall be configurable only by authorized users. The selected constant shall be archived with each RUC solution. |  |

### Mitigated Offer Cap

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(4), 4.4.9.4.1, 5.1(8) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall retrieve the Resource Mitigated Offer Cap curves from Market Infrastructure (MI) as input. If the Resource Mitigated Offer Cap curve is not monotonically non-decreasing, the MMS shall revise the Mitigated Offer Cap curve to create a monotonically non-decreasing one using the following logic: Starting from the first Resource Mitigated Offer Cap curve segment to the last segment, if the Mitigated Offer Cap of the current segment is less than the previous segment, revise the Mitigated Offer Cap of the current segment to be the same as previous segment. The MMS shall use the revised (monotonically non-decreasing) Resource Mitigated Offer Cap curve for the RUC proxy Energy Offer Curve calculation. The detailed MMS Mitigated Offer Cap curve calculation process is documented in MMS Requirement Specification for SCED and Real-Time MMS Processes. |  |

### Load Forecast as Input

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(9)(b), 5.5.2(8)(a), 5.5.1(3), 3.12.1 and 4.5.1(5) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall retrieve the Load Forecast data from Mid-Term Load Forecast (MTLF) application from EMS. The MMS shall use the Day-Ahead forecast of the total ERCOT demand for each hour in the DRUC Study Period. The MMS shall use the current hourly forecast of the total ERCOT demand for each hour in the HRUC Study Period. The MMS shall use the next seven-day forecast of the total ERCOT demand for each hour in the WRUC Study Period. The MMS shall allow the Operators to review the forecast provided by MTLF and modify the forecast for each hour using offsets prior to executing the RUC study. |  |

### Bus Load Forecast

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(9)(b), 5.5.2(8)(a), 5.5.1(3), 3.12.1 and 4.5.1(5) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall allocate ERCOT System-wide hourly Load Forecast over Load buses using the most recent load distribution factors obtained from EMS. |  |

### Input from Forced Outage Information

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(i), 5.5.2(9), 3.1.4.5 (1), 6.4.7 |
| Traceability to Sub-Process Maps | RUC |
| Description The QSE shall update the COP and/or Outage Scheduler in the event of a Forced Outage. The COP and Outage Schedule shall reflect the Forced Outage status. The MMS shall use the COP status and the Outage Scheduler data to determine the status of Generation Resources and Transmission elements. The MMS shall impose the Outage Scheduler data on the COP if the Resource is specified as Forced Outage in the Outage Scheduler. The RUC shall not retrieve Forced Outage information from other data sources. |  |

### Input from Outage Scheduler Information

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(9) |
| Traceability to Sub-Process Maps | RUC |
| Description The RUC shall retrieve Outage information from Outage Scheduler. The RUC shall use the Outage Scheduler information to build the network topology and to determine the projected Resource status (see FR34 and FR35). |  |

### Retrieve Dynamic Rating Data

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 3.10.8; 5.5.2(8)(b), 5.5.1(4), 5.5.2(9) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall retrieve Dynamic Ratings data from the EMS for transmission equipments where available. The Dynamic Ratings shall be used in Network Security Monitor (NSM) function. The MMS shall retrieve default static ratings data from the EMS for the transmission equipments which don’t have Dynamic Ratings data available. |  |

### Retrieve Generic Constraints

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(b) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall retrieve Generic constraint definitions and limits from the EMS. The Generic constraints are the network/voltage constraints modeled as import/export energy constraints that are determined Off-Line. The MMS shall allow Operators to modify the limits of the Generic constraints. |  |

### Input from Ancillary Service Certification

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(11),4.5.2(2),6.5.9.3.3(5)&(6), 8.1.2.1 and 8.1.2.2 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall retrieve Resource Ancillary Service (AS) Certifications from Settlement as input. The Resource AS Certifications shall be displayed in the RUC MOI to assist ERCOT Operators to manually procure additional AS capacity for AS insufficiency. The Resource AS Certification shall denote if the Resource is certified/eligible to provide each of the following Ancillary Services: - Reg-Up - Reg-Down - Responsive Reserve Service - Non-Spin |  |

## Module: Operator Control and Override

### Override Load Forecast

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(9)(b), 5.5.2(8)(a), 5.5.1(3), 3.12.1 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall allow Operators to review the Load Forecast retrieved from MTLF and modify the Load Forecast for each hour using offsets prior to the RUC execution. The RUC study shall use the modified Load Forecast as input. |  |

### Pause and Review/Override Input/Output between Any Phases

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.1(9)&(11) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall allow Operators to manually execute the sub-functions of the RUC process and to pause the RUC process between any two sub-functions in order to determine the state of the solution and to alter inputs and outputs. The MMS shall continue the remaining RUC process after each pause based on the modified input data. |  |

### Calculate Ancillary Service Insufficiency

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 4.5.2 |
| Traceability to Sub-Process Maps | RUC |
| Description The RUC shall compute Ancillary Service Offer insufficiency to be the Ancillary Service Requirements specified in Ancillary Service plan minus total amount of Ancillary Service procured in DAM and SASM and the total amount of Self-Arranged Ancillary Service. The insufficient amount shall be displayed on the MOI to assist the Operators’ manual Ancillary Service Procurement. |  |

### Calculate Resource Ancillary Service Capability

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 3.18; 6.5.7.6.2.1; 6.5.7.6.2.2; 6.5.7.6.2.3; 8.1.2.2.2; 8.1.2.2.3; 8.1.2.2.4 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall compute the available Ancillary Service capacity for Resources certified to provide different types of Ancillary Services using the following formulation. - Reg-Up: MIN(5*The largest Normal Ramp Rate, HSL-LSL) - Reg-Down: MIN(5*The largest Normal Ramp Rate, HSL-LSL) - Responsive Reserve Service: MIN(10* The largest Emergency Ramp Rate, 20%*HSL, HSL-LSL) - On-line Non-Spin: MIN(30*The largest Normal Ramp Rate, HSL-LSL) - Off-line Non-Spin: MIN(30*The largest Normal Ramp Rate, HSL) The HSL and LSL information are submitted by QSEs as part of COP. The Normal/Emergency Ramp Rate curves are submitted by QSE and are part of Resource Parameter data. The Ancillary Service capability calculation shall use the largest ramp rate value in the Normal/Emergency Ramp rate curves. |  |

### Procure Ancillary Service for DAM/SASM AS Offers Insufficiency

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(11),4.5.2(2),6.5.9.3.3(5)&(6), 8.1.2.1 and 8.1.2.2 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall allow Operators to manually procure Ancillary Service (AS) in RUC if the AS Offers submitted in the DAM/SASM are insufficient to meet the requirements of the AS Plan. The MMS shall provide a summary display to assist Operators to perform the manual procurement. The summary display shall include the following information. - AS insufficiency for different classes calculated based on FR24 - Resource ID - Type of Resource (e.g., nuclear, hydraulic, etc.) - AS Certifications (Reg-Up, Reg-Down, Reserve Service, Non-spin) - Available AS Capacity calculated based on FR25. - On-line/Off-line status in COP - On-line/Off-line status determined by RUC - Energy MW dispatched by RUC - Minimum On-Line time - Minimum Off-Line time - HSL and LSL from COP The MMS shall allow Operators to manually procure available Off-Line Resources on MOI for AS Insufficiency based on Resource AS Certification. |  |

### Deselect Standard Contingencies

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.1(6) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall retrieve the standard Contingency List from NMMS. The MMS shall allow Operators to deselect certain contingencies from the standard Contingency List prior to RUC execution. A reason code shall be entered for each deselection decision made by the Operators. The deselected contingencies shall not be considered in RUC study. The MMS shall store a list of all constraints deselected from the standard Contingency List and the corresponding reason codes and make them available to MIS. |  |

### Review/Deselect NSM Constraint Violations

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.1(9); 5.5.1(11) |
| Traceability to Sub-Process Maps | RUC |
| Description The RUC shall display all network constraint violations detected by Network Security Monitor (NSM) on MOI during RUC execution. RUC shall allow Operators to deselect constraints/contingencies that are known to cause errors or result in inconclusive study output in the RUC. RUC shall support at least the following two types of de-selection: - Contingency de-selection: Once a contingency is deselected by Operators, RUC shall ignore any transmission constraint violations caused by the deselected contingency. - Constraint de-selection: A constraint is defined by a Contingency/Base Case and overloaded transmission element pair. Once constraints are de-selected by Operators, RUC shall only ignore the deselected constraint. RUC shall output a list of all constraints/contingencies de-selected during RUC execution. |  |

### Manually Commit/Decommit Resources on MOI/UI

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(1), 5.5.2(2) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall allow Operators to manually commit or decommit resources on the MOI before RUC Optimization. The manual commitment or decommitment is used to resolve some constraints that may not be correctly modeled by NSM and RUC, e.g., voltage constraints. The manual commitment or decommitment made by Operators shall be enforced in RUC commitment solution. The RUC process shall not modify the manual commitment or decommitment schedule to satisfy Resources’ temporal constraints such as Minimum Off-line and Minimum On-line time constraints. |  |

### Manually Override SCUC Commitment/Decommitment on MOI/UI

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(9)&(10), 5.3.(3)(a)(ii), 5.5.2(3) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall provide calculated Resource commitments on MOI to be reviewed by ERCOT Operators before issuing Dispatch Instructions to QSEs to commit, extend, or decommit Resources. The MMS shall allow Operators to make changes to the RUC-recommended commitments with a reason code to the changes. The RUC process shall not modify the manual commitment or decommitment schedule to satisfy Resources’ temporal constraints such as Minimum Off-line and Minimum On-line time constraints. |  |

## Module: Initial Unit Commitment (IUC)

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | RUC |
| Description The Initial Unit Commitment (IUC) shall compute the initial unit commitment schedule using the same input data as the SCUC without NSM generated transmission constraints. The MMS shall pass the IUC generation schedule to NSM to evaluate the feasibility of both the base case and a given set of contingencies. |  |

## Module: Network Topology Builder

### Breaker Status Projection

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.1(3), 5.5.2(8)I, 5.5.2(9)(a) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall determine the status of transmission breakers and switches in the following ways: For HRUC first study hour, the system shall use the current breaker status from SCADA/EMS plus changes indicated in Outage Schedule. For DRUC, HRUC remaining study hours and WRUC, the system shall use the normal breaker status plus changes indicated in Outage Schedule. The projected status of transmission breakers and switches shall be used to build transmission topology in RUC Study Period. |  |

### Initial Resource Commitment Status Determination

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall retrieve both the current Resource commitment status (On-line or Off-line) and the historical Resource commitment status of the current Operating Day from the EMS. The historical commitment status data include: - Number of start up of the Operating Day until the end of previous hour. - If the Resource was On-line, the number of hours it has been On-line until the end of previous hour. - If the Resource was Off-line, the number of hours it has been Off-line until the end of previous hour. The current EMS On-line/Off-line status shall be used for the current hour (the hour that RUC executed). The historical commitment status passed from EMS shall be used for the status before the current hour. For future hours, the commitment status indicated in COPs shall be used. HRUC shall use the historical commitment data and the On-line and Off-line status for the current Operating hour to determine the Resource’s initial condition at the beginning of the next Operating hour. DRUC and WRUC shall use the historical commitment data, the On-line and Off-line status for the current Operating hour and the COP status for remaining hours of the current Operating Day to project the initial commitment status at the beginning of the next Operating Day. The Start Up Time of Resources shall effect their eligibility to be committed as follows: - If the Resource is Off-line based on the EMS data, then the Resource shall be made unavailable for commitment from the current time to the min (current time + Start Up Time, first hour Resource scheduled on in the COP). |  |

### Resource Status Projection for HRUC

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(e), 5.5.2(9)(a), 3.9 |
| Traceability to Sub-Process Maps | RUC |
| Description For HRUC study, the MMS shall first revise the projected Resource status indicated in the COP by incorporating the Resource committed in the previous HRUC execution if the Resource status is Off-line available in the COP. If the resource was committed in previous HRUC, but unavailable according to the COP, the resource shall be treated as unavailable in current HRUC. The MMS shall use the revised status of Resources for each hour in the HRUC Study Period plus the changes indicated in Outage Schedule. |  |

### Resource Status Projection for DRUC and WRUC

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(e), 5.5.2(9)(a), 3.9 |
| Traceability to Sub-Process Maps | RUC |
| Description For DRUC and WRUC study, the MMS shall use the Resource status indicated in COP for each hour in the DRUC and WRUC Study Period plus the changes indicated in Outage Schedule. |  |

## Module: Network Security Monitor (NSM)

### NSM Overview

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | SCUC |
| Description The Security Constrained Unit Commitment (SCUC) solution engine is comprised of two major components: (1) Network Security Monitor (NSM) and (2) Network Constrained Unit Commitment (NCUC). The NSM function is used in the solution process of Day-Ahead Market Clearing Engine (MCE) and Reliability Unit Commitment (RUC). NSM evaluates the security of the network subject to the schedule provided by NCUC for both the base case (intact) system and contingencies. The network security constraints evaluated in NSM include: - Thermal constraints - Generic constraints The NSM consists of the following main components: - Network Data Update Retrieves the network model prepared by the preprocessor and imposes on it the latest NCUC generation schedule to establish the modified base case. The RUC Network topology used by NSM shall be built based on the Normal network and Outage schedules. All power flow computations shall use a lossless model while satisfying the power flow constraints. Transmission constraints shall be based on Dynamic Ratings. - Base Case Power Flow Solution Performs non-linear AC power flow solution on the modified base case prepared by Network Data Update and computes the base case flows. A failure of the AC power flow to converge automatically triggers the execution of the non-linear DC power flow. - Contingency Topology Processor Prepares the Final Contingency List, Violations Check List and Generator Allocation List for the DC Contingency Analysis. - Incremental Contingency Analysis Performs Incremental (linear) Contingency Analysis by imposing contingencies based on the lists prepared by the Contingency Topology Processor and determines the modified flows. If a Special Protection Scheme (SPS)/Remedial Action Plan (RAP) triggering condition is satisfied in a contingency, the contingency shall be ignored, i.e., it is assumed that SPS/RAP clears all constraint violations. - Constraint Data Processing Selects the critical network violated constraints and computes the shift factors (sensitivities) to be used by NCUC. Figure 3-3 shows the flow diagram of the NSM process. Figure 3-3 A Flow Diagram of the NSM Process |  |

### Use of Dynamic Ratings in NSM

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | SCUC |
| Description By default, the NSM shall use Normal Ratings to evaluate the feasibility of the commitment and dispatch schedule calculated by NCUC in Base Case analysis. By default, the NSM shall use Emergency Ratings to evaluate the feasibility of the commitment and dispatch schedule calculated by NCUC in Contingency analysis. The NSM shall allow Operators to configure the setting for the use of Dynamic Ratings, e.g., Operators are allowed to select either using Normal Ratings or using Emergency Ratings for Base Case study. |  |

### Identify Violated/Nearly Violated Constraints in NSM

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(b), 5.5.1(7)&(8)&(10) |
| Traceability to Sub-Process Maps | SCUC |
| Description The NSM shall evaluate the feasibility of the commitment or dispatch schedule calculated by NCUC for both the base case and a set of given contingencies. The NSM shall be executed for each time step of the RUC Study Period to provide constraints for NCUC. The NSM shall account for the action of SPS/RAP. The NSM shall transform each violated/nearly violated constraint into a linear function of the Resource outputs and pass it to the NCUC for enforcement. The NSM shall identify the nearly violated constraint based on the user-specified threshold, e.g., 90% loading. |  |

### NSM Sensitivity Cutoff Threshold

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | SCUC |
| Description To prevent excessive movement of the control variables for alleviating the network constraint violations, the NSM shall set to zero all shift factors whose absolute values are below the user-specified “Sensitivity Cutoff Threshold” before they are passed to NCUC for enforcement. The threshold shall be configurable only by authorized users and shall be archived with each RUC solution. |  |

### NCUC-NSM Solution Process

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | SCUC |
| Description The NCUC and the NSM shall iterate several times to find the final solution. The iterations are desired because: - NSM develops constraint equations to be passed to NCUC corresponding to violated or near violated constraints based on one operation point. New constraint equations have to be generated as the dispatch changes. - Non-linear branch flow calculations are used, the linearized constraint equations may change as the dispatch changes. The steps in the solution process shall be as follows: - Retrieve the initial base case data and superimpose on them the generation and load schedule determined by the latest NCUC (or IUC) execution - Invoke NSM for the base case at each time step in the study period to identify network constraints to be enforced in the NCUC solution. - Invoke NCUC to determine the revised generation schedule as impacted by enforcing the additional network constraints - Steps 2 and 3 iterate until convergence is reached. - SPS/RAP Triggering Test. - Using the solved NCUC generation at Step 4, invoke NSM for all contingencies to test the SPS/RAP triggering conditions (contingency specific SPS/RAP and equipment-based SPS/RAP). Any contingencies that trigger SPS/RAP shall be ignored in the subsequent NCUC-NSM iterations. - Invoke NSM for the base case and all contingencies without SPS/RAP triggering as determined at Step 5 at each time step in the study period to identify network constraints to be enforced in the NCUC solution. - Invoke NCUC to determine the revised generation schedule as impacted by enforcing the additional network constraints. - Step 6 and 7 iterate until convergence is reached. Figure 3-4 shows the flow diagram of the NCUC-NSM solution process. Figure 3-4 A Flow Diagram of the NCUC-NSM Solution Process |  |

## Module: Security Constrained Unit Commitment (SCUC)

### Use SCUC for RUC Process

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(1), 4.5.1(4), 5.5.2(8)(d), 5.5.2(1), 5.1(8), 5.5.2(8)(g)&(h) |
| Traceability to Sub-Process Maps | SCUC |
| Description The MMS shall use a Security Constrained Unit Commitment (SCUC) optimization application to minimize the total cost based on Three-Part Supply Offers subject to system capacity constraints, system power balance constraints, transmission constraints and Resource constraints. A proxy Energy Offer Curve shall be substituted for the Energy Offer Curve over the whole RUC study period. |  |

### Commit Resources in SCUC

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(1), 5.5.2(5) |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall determine commitment of Generation Resources to match MTLF forecasted system demand, subject to all transmission constraints and Resource performance characteristics. The RUC shall evaluate the need to commit additional Resources both from Off-line Resources for which a QSE has submitted Three-Part Supply Offers and other available Off-Line Resources. These are resources that are needed in addition to Resources that are planned to be On-Line during the RUC Study Period. The Resources which are Off-Line but available for commitment by RUC are only the Resources with Resource status specified as “OFF” in the COP. |  |

### Decommit Resources in SCUC

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.1(7), 5.5.2(2) |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall determine Resource decommitment. The RUC shall only decommit a Resource to resolve transmission constraints that are otherwise un-resolvable. |  |

### Filter/Restrict Resource Decommitment

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(2) |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall allow Operators to assign priorities to Resources during the decommitment process based on the category of Resources. The RUC shall decommit QFs only after all other types of Resources have been assessed for decommitment. |  |

### Constraint Penalty Function

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(1), 5.5.2(7) |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall apply penalty factors to violations of the power balance and security constraints to the SCUC objective function in addition to the offer-based cost. The penalty factors shall be configurable by the authorized Operators. The RUC shall apply different penalty factors for different types of violations: - System Deficit Generation / Surplus Generation (i.e. Under Generation / Over Generation) - Transmission Base Case Constraints - KV Level of overloaded element (for transformers, the higher kV level is used) - Transmission Contingency Constraints - KV Level of overloaded element (for transformers, the higher kV level is used) - Transmission Generic Constraints - Resource Reg-Up/Reg-Down - Responsive Reserve Service - Resource Non-spin |  |

### Tie Breaking Rules for RUC Dispatch

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | SCUC |
| Description When two or more Resources offer the same price for blocks of their price curves, then it is possible that there will be more than one optimal (least cost) RUC solutions. These solutions will have different dispatches within the equal price blocks. The Resources that can have different optimal dispatches are known as marginal Resources. The RUC shall use the following approach to generate a unique dispatch: the RUC solution Engine shall break the tie by prorating the dispatch schedules among all the marginal Resources. The proration shall be based on the size of the MW block with equal price offers. Only the part of price curves within Resources’ available region shall be used. |  |

### Modeling Resource Capacity Providing Ancillary Service

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(7), 3.9(2). 6.4.8.1.2, 6.4.8.1 |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall treat all Resource capacity providing Ancillary Service as unavailable for the RUC Study Period, unless that treatment leads to infeasibility (i.e., that capacity is needed to resolve some local transmission problem that cannot be resolved by any other means). In such cases, the RUC shall provide the information for each affected QSE of the amount of its Resource capacity that does not qualify to provide Ancillary Service, and the projected hours for which this is the case. The RUC shall compute Resources’ HASL and LASL based on the HSL, LSL, and Ancillary Service quantities from COP. The portions of Resource proxy Energy offer curves outside HASL and LASL shall be protected by assigning penalty factors (see FR45) that shall be higher than any of the proxy offer curves but lower than transmission constraint penalty factor. The penalty factors for Resource AS violation and transmission constraint violation shall be configurable by authorized users and correctly coordinated considering the impact of the associated shift factors. |  |

### Modeling Combined Cycle Resources Configuration

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 3.9, 3.7.1.1 |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall model multiple operating configurations for Combined Cycle Resources in RUC. The RUC shall not procure steam turbine alone without combustion (gas) turbine procured or self-scheduled online. The RUC shall correctly use the Startup cost, minimum energy cost and operation cost in the objective function for each CC configuration. The RUC shall respect the Resource output constraints (minimum and maximum output levels) and operational constraints (includes lead-time (start time), minimum run time, minimum down time, and configuration constraints) for the selected CC Resource's configuration. The RUC shall also respect the allow transitions between the configurations and between the configurations and the off state and the minimum run and down time for the entire CC plant. |  |

### Modeling DC Tie Schedule

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 4.4.4, 3.10.7.2 |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall retrieve the net energy schedule for the DC Tie from COP. The RUC shall treat the DC Tie as an equivalent online Resource if the net energy schedule for a DC tie shows a net import; otherwise the system shall treat the DC Tie as an equivalent Load. The DC Tie schedule shall be treated as a fixed injection or withdrawal in the RUC process. The RUC shall not modify DC Tie schedule to resolve system constraints. |  |

### Modeling Split Generation Resources

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 3.8, 3.10.7.2 |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall model Split Generation Resources. RUC shall retrieve the Resource Parameters, COP and Three Part Supply Offers for each individual Split Generation Resource in a generation facility. The RUC shall commit or decommit all individual Split Generation Resources in a generation facility together. |  |

### Modeling Off-line Time Dependent Start up Cost

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 4.4.9.2.1 |
| Traceability to Sub-Process Maps | SCUC |
| Description QSEs shall be allowed to submit hot, intermediate and cold Start up costs in the Three-Part Energy Offer. The RUC shall model the Off-line time dependent start up cost in the RUC optimization process. |  |

### Resource Constraints

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(e), 3.7.1.1, 4.5.1(4)(ii) |
| Traceability to Sub-Process Maps | SCUC |
| Description The MMS shall enforce the Resource output constraints and operational constraints in RUC optimization. The MMS shall enforce the following Resource operational constraints in RUC optimization: - Lead time (start up time) constraints including hot, intermediate and cold time - Minimum On-line time - Maximum On-line time - Minimum Off-line time - Maximum daily start up At the end of the RUC study period, the operational constraints shall be enforced assuming that Resources with unspecified commitment status are Off-line for all hours after the study period, |  |

### Additional Resource Constraints for WRUC

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 3.7.1.1 |
| Traceability to Sub-Process Maps | SCUC |
| Description The MMS shall enforce the Resource Maximum Weekly start ups and Maximum Weekly Energy in WRUC optimization. |  |

### Transmission Constraints

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(b),,4.5.1(4)(i) |
| Traceability to Sub-Process Maps | SCUC |
| Description The MMS shall enforce the transmission constraints including Thermal Constraints, Generic Constraints and Predefined Constraints for each hour of the RUC Study Period. |  |

### Power Balance Constraints

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(d) |
| Traceability to Sub-Process Maps | SCUC |
| Description The MMS shall enforce the Power Balance Constraint for each hour of the RUC Study Period. The total system generation shall equal to the total system demand. |  |

### Resource Status

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(e), 3.9, 5.5.2(1), 5.5.2(5), 5.5.2(8)(j) |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall use Resources status in the COP (QSE self-committed, DAM committed, committed in previous RUCs) and Resource capacity already committed to provide Ancillary Service as inputs. |  |

### Ignore Temporal Constraints Violation for QSE-Commitment intervals

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall ignore resource temporal constraints violated by QSE self schedules during QSE-Commitment intervals. The RUC shall not commit Resources only to satisfy the temporal constraints violated by QSE self schedules. |  |

### RUC Startup Cost Eligibility

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.6.2 |
| Traceability to Sub-Process Maps | SCUC |
| Description The RUC shall not introduce additional resource Startup Cost in the objective function if the designated start hour or last hour of the RUC instruction connects to a block of QSE-Committed Intervals that was QSE-committed before the RUC instruction was given. |  |

## Module: RUC Output and Dispatch

### RUC Commitment/Decommitment Output

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.1 diagram, 5.5.3(1), 5.5.3(2) |
| Traceability to Sub-Process Maps | RUC |
| Description The RUC shall output the cleared Resource commitments and decommitments. Resource commitments shall include the start interval and duration for which the Resource is required to be at least at LSL. Resource decommitment shall include the interval in which the Resource is required to be Off-Line, duration. For the decommitment recommended by RUC, RUC shall assign a default reason code to indicate that decommitment is decided by RUC Optimization process to resolve transmission violation. For the decommitment manually entered by Operators, the system shall allow Operators to enter different reason codes. |  |

### Operator Confirmation RUC Decommitment

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall provide flags to allow Operators to individually confirm the RUC decommitment. The MMS shall not publish the RUC decommitment instructions not confirmed by Operators. |  |

### Operator Approval RUC Commitment

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.1 diagram |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall provide an approval flag on MOI to allow Operators to approve the cleared Resource commitment schedules and confirmed decommitment schedules. If the approval flag is set to “Yes”, the RUC commitment schedules and confirmed decommitment schedules are sent to the MI for publishing. Otherwise, the RUC commitment/decommitment schedules are not published. |  |

## Decision Support for QSE Request Decommitment in HRUC

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP6.4.6.2 |
| Traceability to Sub-Process Maps | RUC |
| Description The HRUC shall identify a Resource decommitment request if: - The Resource’s COP status changed from On-line to Off-line available during the Adjustment Period - There is no previous HRUC decommitment instruction issued. The HRUC shall use the adjusted Three-part offer (see FR12) and treat the Resource to be off-line available for the hours the Resource requested for decommitment. The HRUC shall provide a summary display for Operators’ review to show the final HRUC recommendation for the commitment decisions (i.e., “accepted” or “rejected” the decommitment requests) for the Resource requested for decommitment. In addition to the normal commitment instructions, HRUC shall publish whether the QSEs’ decommitment requests are accepted or rejected. |  |

### Active and Binding Transmission Constraints

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.3(3)(b) |
| Traceability to Sub-Process Maps | RUC |
| Description The RUC shall output all active and binding transmission constraints (contingency and overloaded element pair) information. |  |

### Infeasible Ancillary Service Capacity Output

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(7), 5.3(3)(c), 5.5.2(3) |
| Traceability to Sub-Process Maps | RUC |
| Description If the resource capacity providing Ancillary Service is needed to resolve transmission constraints that cannot be resolved by any other means, the MMS shall provide the information for each affected QSE of the amount of its Resource capacity that does not qualify to provide Ancillary Service, and the projected hours for which this is the case. The MMS shall provide an infeasible Ancillary Service capacity summary display. The following information shall be provided in the display: - Infeasible Resource ID - Time stamp - Ancillary Service type - Violated MW |  |

### Dispatch Resource

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.3(3)(c), 5.5.2(3) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall issue Dispatch Instructions regarding the commitment and decommitment decisions made by RUC to notify each QSE of its Resource commitments or decommitments. |  |

### Additional Output for WRUC

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(j) |
| Traceability to Sub-Process Maps | RUC |
| Description The WRUC shall provide the following additional outputs to alert the operators of resources, which may be needed in the future, but have temporal constraints forbidding their procurement in DRUC and HRUC. Resources that are not committed in DRUC and HRUC study period, but committed in future WRUC study period, shall be highlighted to Operators. These Resources could have start up time larger than DRUC and HRUC study period. |  |

### WRUC Commitment Result

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(j) |
| Traceability to Sub-Process Maps | RUC |
| Description : The WRUC shall not send out the commitment and dispatch instructions to QSEs. |  |

### Provide Necessary Information on MOI/UI

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall provide necessary inputs and outputs of different sub-functions (i.e., DSI, NDP, IUC, NSM, NCUC, DSP and SAV) of RUC on the Market Operator Interface (MOI) for Operators’ review. The MMS shall provide application messages to indicate whether any errors occur during the different stages of RUC execution. |  |

### Create Suggestion Plan for Unresolved Constraints

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall provide the Suggestion Plan (a summary report) on the MOI for unresolved congestion/capacity constraints in RUC process. The MMS shall allow Operators to select an un-resolved constraint and list key Resources related to the selected constraints. The following information shall be included in the Suggestion Plan summary display: - Constraint Name - Study Interval - Constraint Limit - Constraint Flow - Resource Name - QSE Name - Resource Type - LSL,HSL - HASL, LASL - Shift Factor to the constraint - Resource Availability, i.e. Available/Unavailable - Resource Status, i.e. Online/Offline - Participate in other constraints (Yes/No) - Start up time - Remaining Min-Up/Min-Down time - Resource Final dispatch MW - Contribution MW to the constraint, i.e. dispatch MW*Shift Factor - Procurement Flag, i.e. if procured in RUC |  |

## Module: Save Case

### Save Cases

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5 |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall archive both approved and unapproved RUC Cases for post analysis. The Case shall include all input/output data for RUC Off-line Study Tool to be re-executed and to produce the identical results to the original run. |  |

## RUC in Study Mode

### Execute RUC in Study Mode

| Requirement ID |  |
| --- | --- |
| Source Mapping (Protocol/NERC/FERC and other binding documents Ref #) | NP 5.5.2(8)(j) |
| Traceability to Sub-Process Maps | RUC |
| Description The MMS shall allow Operators to execute RUC in a study mode. The MMS shall support the following two methods of providing input data to RUC in a study mode: - Retrieving data from a save case - Retrieving data from the on-line data sources If the RUC input data is retrieved from a save case, the Study Period will be the same as the corresponding RUC study period at the time the save case created. If the RUC input data are retrieved from on-line data sources, the Study Period will be the same as RUC executing in on-line mode. When the RUC input data are retrieved from on-line data sources, the study tool shall allow Operators to shorten the RUC Study Period by manually setting the start time and end time of the study within the normal RUC Study Period. Under this circumstance, the study tool shall set up the RUC initial condition for the time prior to the first study hour using the logic specified in FR33. The study tool shall allow users to manually execute the sub-functions of the RUC to pause at any phase in the study in order to analyze and alter the input and output of the sub-functions. The study tool shall continue the remaining RUC process after pause based on the actual or modified inputs and outputs. The study results are just for study purpose and shall not be sent to QSE for deployment. |  |

# Supplementary Requirements

## Performance Requirements

### Market Participant Interface Specific Performance Requirements

- 800 bids/offers in 5 minutes with a response time of less than 3 seconds for a single bid/offer submission.

This assumes that the 800-bids/offer submissions are a representative mix of bulk bid/offer submissions and single bid/offer submissions.

### Market Application Specific Performance Requirements

- SCED - 20 seconds

SCED is scheduled to run once every 5 minutes. The 20 second response time is to account for the fact that SCED may be rerun on demand or upon a change in system condition.

- Determination of oversold CRRs

The timing requirement for this process shall be based on the requirement of 3 seconds for performing contingency analysis of ERCOT power system model (5000 buses, 6000 branches, 3000 contingencies).

The key data aspect affecting the performance for this process is the number of distinct source-sink pairs for CRR options, number of power flow buses, number of contingencies analyzed and the number of branches to be monitored. There are no restrictions on the number of CRR obligations in determining this performance requirement.

- CRR Option Derating – 5 minutes

- DAM - 15 minutes

DAM has the capability to execute multiple iterations between Network Security Monitoring (NSM) and Network Constrained Unit Commitment (NCUC). The operator may intervene between the NSM and NCUC executions to manually modify the output of NSM.  The 15-minute requirement is measured on no manual intervention between NSM-NCUC iterations.    The DAM requirements for Linked Ancillary Service Offers, Inclusive-Exclusive Offers, and Combined Cycle Units that were further defined during Phase 1 are now understood to be unique to the ERCOT market.  The ILOG Cplex program has not been benchmarked against these requirements.   It is possible that these requirements may adversely affect the market clearing times to be over 15 minutes.

- SASM - 5 minutes

- DRUC (Day Ahead) - 15 minutes

This is similar to DAM but without Ancillary Services and hence the possible performance issues associated with Linked Ancillary Services and Inclusive-Exclusive offers are not present for RUC.  The 15-minute requirement is measured on no manual intervention between NSM-NCUC iterations.

- HRUC (Hourly) - 15 minutes

This has more steps (33) to solve than the Day-Ahead RUC (24).  However, the number of units to be committed in the Hour Ahead RUC is much less than in the Day Ahead and hence it is reasonable to assume the same execution time for both.  The 15-minute requirement is measured on no manual intervention between NSM-NCUC iterations.

- WRUC (Weekly) - 3 hours

Based on the ability to solve the 24-hour RUC in 15 minutes, the 7-day problem could be solved in 2 hours.  However, since this requirement has not been benchmarked before, it is possible that the actual execution time is greater than 2 hours.  The 3-hour requirement is measured on no manual intervention between NSM-NCUC iterations.

# Use Cases

Use cases start when the actor does something; an actor always initiates use cases.  The use case describes what the actor does and what the system does in response. It is phrased in the form of a dialog between the actor and the system.

## Actor Catalog

| # | Actor | Description |
| --- | --- | --- |
| 1 | QSE Operator |  |
| 2 | ERCOT Operator |  |
| 3 | EMS system |  |
| 4 | MMS System |  |

## Use Case Catalog

| Use Case ID | Name | Use Case Description |
| --- | --- | --- |
| RUC-UC1 | RUC Input Data Retrieval and Pre-Processing | Input data retrieval and pre-processing from various systems. |
| RUC-UC2 | RUC Load forecast data input | Retrieval and process of load forecast as input for a RUC run |
| RUC-UC3 | RUC Three-Part Offer Curve Creation for Non-Bid Resources | Creation of Three-Part offer curve for Non-Bid Resources in a RUC run |
| RUC-UC4 | RUC Proxy Energy Offer Curve Creation and Substitution | Calculation and substitution of Proxy Energy Offer Curve in a RUC run |
| RUC-UC5 | DRUC run | Execute a DRUC run |
| RUC-UC6 | HRUC run | Execute a HRUC run |
| RUC-UC7 | WRUC run | Execute a WRUC run |
| RUC-UC8 | RUC run in Study Mode | Execute a RUC run in Study Mode |
| RUC-UC9 | Run RUC Market Clearing Engine | RUC Market Clearing Engine Execution Process |
| RUC-UC10 | Run Initial Unit Commitment (IUC) in RUC | IUC execution process in RUC run |
| RUC-UC11 | Run Network Constrained Unit Commitment (NCUC) in RUC | NCUC execution process in RUC run |
| RUC-UC12 | Run Network Security Monitor (NSM) in RUC | RUC Network Security Monitor execution process |
| RUC-UC13 | RUC Result Analysis and Post-Processing | Operator Review, Analysis, and Post-Processing of RUC solution |
| RUC-UC14 | Procure Ancillary Service in RUC | Operator Procurement Additional Ancillary Services Capacity in RUC |
| RUC-UC15 | Commitment/Decommitment Manual Setup | Operator’s manual setup of Resource commitment/decommitment schedules |
| RUC-UC16 | Manual Override of RUC-Recommended Resource Commitment | Operator Manual Override RUC-recommended commitment solution |
| RUC-UC17 | Manual Override of RUC-Recommended Resource Decommitment | Operator Manual Override RUC-recommended decommitment solution |
| RUC-UC18 | Manual Override of Infeasible Resource Capacity Providing Ancillary Services | Operator Manual Override of Infeasible Resource Capacity Providing Ancillary Services |
| RUC-UC19 | HRUC Providing Decision Support for Resource Self-Decommitment Request | HRUC process of providing decision support for Resource decommitment requests |
| RUC-UC20 | RUC Creating Suggestion Plan for Unresolved Constraints | RUC Creating Suggestion Plan for Unresolved Constraints |

## Use Cases Listing

# Protocol Coverage

| Protocol Sub-Section # (To the lowest level of granularity as possible) | Description | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
| 3.1.4.5 | Management of Resource or Transmission Forced Outages or Maintenance Outages | Partial(FR17) |
| 3.7 | Resource Parameter | Partial(Section 2.1)(FR7) |
| 3.7.1.1 | Generation Resource Parameters | Full(FR7)(FR48)(FR52) |
| 3.7.1.1 | Additional Weekly Constraint for WRUC | Full(FR53) |
| 3.8 | Split Generation Modeling | Full(FR50) |
| 3.9 | Current Operating Plan (COP) | Full(Section 2.1)(FR5)(FR34)(FR35) |
| 3.9(2) | HASL and LASL Calculation based on COP | Full(FR47) |
| 3.9.3 | Combined Cycle Resource Configuration Modeling | Full(FR48) |
| 3.10.7.2 | Split Generation Modeling | Full(FR50) |
| 3.10.7.2 | DC Tie Schedule Modeling | Full(FR49) |
| 3.10.8 | Dynamic Rating | Partial(FR19) |
| 3.12 | Load Forecasting | Partial(FR16)(FR22)(FR15) |
| 3.12.1 | Mid-Term Load Forecast | Partial(FR16)(FR22)(FR15) |
| 3.18 | Resource Limits in Providing Ancillary Service | Partial(FR25) |
| 4.2.2 | RUC Input from Wind-Powered Generation Resource Production Potential | Full(FR5)(FR6) |
| 4.4.4 | DC Tie Schedule Modeling | Full(FR49) |
| 4.4.8 | RMR Offer | Partial(FR10) |
| 4.4.9.1 | Three-Part Supply Offer Validation | Partial(FR9) |
| 4.4.9.2 | Minimum-Energy Offer and Startup Offer Validation | Partial(FR9) |
| 4.4.9.2.1(c) | Off-line Time Dependent Startup Cost Modeling | Full(FR51) |
| 4.4.9.2.3 | Startup and Minimum-Energy Offer Generic Cap | Full(FR11) |
| 4.4.9.2.3(k) | RMR Resource Minimum-Energy Generic Cap | Full(FR10) |
| 4.4.9.4 | Mitigated Offer Cap Curve | Partial(FR13) |
| 4.4.9.4.1 | Mitigated Offer Cap Curve | Full(FR14) |
| 4.5.1(4)(ii) | Resource Constraints | Full(FR52) |
| 4.5.2 | Ancillary Service Insufficiency | Partial(FR26) (FR24) |
| 4.5.2(2) | Procure Ancillary Service for DAM/SASM AS Offers Insufficiency | Full(FR26) |
| 4.5.2(2) | Resource Ancillary Service Certification | Full(FR26) |
| 5.1(1) | RUC Process Objective and Definition | Full(FR1) |
| 5.1(2) | Execute RUC in DRUC and HRUC Mode | Full(FR2)(FR3) |
| 5.1(3) | Execute RUC in DRUC Mode | Full(FR2) |
| 5.1(4) | DRUC Three-Part Offer Input | Full(FR8) |
| 5.1(5) | Execute RUC in HRUC Mode | Full(FR3) |
| 5.1(6) | Execute RUC in DRUC and HRUC Mode | Full(FR2)(FR3) |
| 5.1(7) | Decommit Resource in RUC | Full(FR43) |
| 5.1(8) | Three-Part Offer Curves used in RUC Optimization Objective | Full(FR8) |
| 5.1(8) | Proxy Energy Offer Curve Substitution of Energy offer Curve | Full(FR13)(FR14) |
| 5.1(9) | Operator Review and Manual Overwrite of RUC Results | Full(FR30) |
| 5.1(10) | Operator Review and Manual Overwrite of RUC Results | Full(FR30) |
| 5.1(11) | Procure Ancillary Service for DAM/SASM AS Offers Insufficiency | Full(FR26)(FR26) |
| 5.2 | Reliability Unit Commitment Timeline Summary | Full(Section 2) |
| 5.3(1) | Execute RUC in DRUC Mode | Full(FR2) |
| 5.3(2) | RUC Input from COP | Full(FR4) |
| 5.3(3)(a)(i) | Three-Part Supply Offer Validation | Full(FR9) |
| 5.3(3)(a)(ii) | Operator Review of RUC Commitment/Decommitment Results | Full(FR30) |
| 5.3(3)(b) | Output Active and Binding Transmission Constraints used as inputs to RUC | Full(FR63) |
| 5.3(3)(c) | RUC Dispatch Instruction notification to QSE | Full(FR65) |
| 5.3(3)(c) | QSE Notification of Infeasible Ancillary Service Capacity | Full(FR65) |
| 5.4(2) | QSE submits Three-Part Offer | Full(FR8) |
| 5.5.1(diagram) | RUC Commitment/Decommitment Output | Full(FR59) |
| 5.5.1(3) | Breaker Status Projection | Full(FR32) |
| 5.5.1(3) | Bus Load Forecast Input to RUC | Full(FR16)(FR15) |
| 5.5.1(4) | Dynamic Rating Data Input to RUC | Full(FR19) |
| 5.5.1(6) | MIS Summary of Deselection on Standard Contingency List | Full(FR27) |
| 5.5.1(7) | Identify Violated/Nearly Violated Constraints in NSM | Full(FR38) |
| 5.5.1(8) | NSM models SPS/RAP in Contingency Analysis | Full(FR38) |
| 5.5.1(9) | Review/Deselect NSM Constraint Violation | Full(FR23)(FR28) |
| 5.5.1(10) | NSM models SPS/RAP in Contingency Analysis | Full(FR38) |
| 5.5.1(11) | Deselection on Standard Contingency List | Full(FR23)(FR28) |
| 5.5.2(1) | RUC Process Objective and Definition | Full(FR1)(FR5)(FR29)(FR41) (FR52) |
| 5.5.2(2) | Operator Manual Commitment/Decommitment | Full(FR29)(FR43) |
| 5.5.2(3) | RUC Dispatch Instruction notification to QSE | Full(FR64)(FR65) |
| 5.5.2(3) | Operator Review and Manual Overwrite of RUC Results | Full(FR30) |
| 5.5.2(4) | Proxy Energy Offer Curve Calculation | Full(FR13)(FR14) |
| 5.5.2(5) | RUC Input from COP | Full(FR41) |
| 5.5.2(5) | Commit Resource in RUC | Full(FR5) |
| 5.5.2(6) | Create Three-Part for Non Bid Resources | Full(FR11) |
| 5.5.2(7) | Ancillary Service Capacity Protection in RUC | Full(FR65)(FR47) |
| 5.5.2(7) | RUC Constraint Penalty Function | Full(FR45) |
| 5.5.2(8)(a) | Load Forecast Input to RUC | Full(FR22)(FR15) |
| 5.5.2(8)(a) | Bus Load Forecast Input to RUC | Full(FR16) |
| 5.5.2(8)(b) | Transmission Constraints | Full(FR54)(FR38)(FR20) |
| 5.5.2(8)(b) | Dynamic Rating Data Input to RUC | Full(FR19) |
| 5.5.2(8)(c) | Planned Network Topology | Full(FR32) |
| 5.5.2(8)(d) | Power Balance Constraints | Full(FR55) |
| 5.5.2(8)(e) | RUC Input from COP | Full(FR5)(FR34)(FR35) |
| 5.5.2(8)(f) | Input from Resource Parameters | Full(FR7) |
| 5.5.2(8)(f) | Resource Constraints | Full(FR52) |
| 5.5.2(8)(g) | Minimum-Energy Offer and Startup Offer from Three-Part Offer | Full(FR8) |
| 5.5.2(8)(h) | Resource that is offline and available but without a Three-Part Supply Offer | Full(FR8) )(FR11) |
| 5.5.2(8)(i) | Forced Outage Data Input to RUC | Full(FR17) |
| 5.5.2(8)(j) | Execute RUC in WRUC Mode | Full(FR4)(FR66) |
| 5.5.2(9) | Input from Outage Scheduler | Full(FR18)(FR17) |
| 5.5.2(9)(a) | Resource Status Projection in HRUC | Full(FR34) |
| 5.5.2(9)(a) | Resource Status Projection in DRUC and WRUC | Full(FR34) |
| 5.5.2(9)(a) | Breaker Status Projection | Full(FR32) |
| 5.5.2(9)(b) | Bus Load Forecast Input to RUC | Full(FR22)(FR16)(FR15) |
| 5.5.3(1) | RUC Commitment/Decommitment Output | Full(FR59) |
| 5.5.3(2) | RUC Commitment/Decommitment Output | Full(FR59) |
| 5.6.1 | Verifiable Costs | Partial(FR11) |
| 5.6.2 | Startup Cost Eligibility | Partial(FR58) |
| 6.4.2(2) | ERCOT submits Energy Offer Curve for Online RMR Resource | Full(FR10) |
| 6.4.3(2) | ERCOT submits Energy Offer Curve for Online RMR Resource | Full(FR10) |
| 6.4.6 | QSE-Requested Decommitment of Resources | Full(FR12(FR62) |
| 6.4.6.2(1) | Adjust Three-Part Offers in HRUC for QSE Request Decommitment in Adjustment Period | Full(FR12)(FR62) |
| 6.4.6.2(2) | Decision Support for QSE Request Decommitment in HRUC | Full(FR62) |
| 6.4.7 | Notification of Forced Outage of a Resource | Full(FR17) |
| 6.4.8.1 | Evaluation of Ancillary Service Capacity Sufficiency | Partial(FR47) |
| 6.4.8.1.2 | Replacement of Undeliverable Ancillary Service Capacity due to Transmission Constraints | Full(FR47) |
| 6.5.7.6.2.1 | Deployment of Regulation Service | Partial(FR25) |
| 6.5.7.6.2.2 | Deployment of Responsive Reserve Service | Partial(FR25) |
| 6.5.7.6.2.3 | Non-Spinning Reserve Service Deployment | Partial(FR25) |
| 6.5.9.3.3(5) | Procure Additional Ancillary Service in DRUC | Full(FR21)(FR26) |
| 6.5.9.3.3(6) | Procure Additional Ancillary Service in HRUC | Full(FR21)(FR26) |
| 8.1.2.2.2 | Regulation Service | Partial(FR25) |
| 8.1.2.2.3 | Responsive Reserve Service | Partial(FR25) |
| 8.1.2.2.4 | Non-Spinning Reserve | Partial(FR25) |

# Sub-Process Coverage

| Sub-Process ID | Sub-Process Name | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
| SP1 | RUC | Full |
| SP2 | SCUC | Full |

# Appendix: RUC Mathematical Formulation

RUC is executed to ensure Transmission System reliability and to ensure that enough Resource capacity, in addition to Ancillary Service capacity, is committed in the right location to reliably serve the forecasted load on the ERCOT system.

There are two categories of Resources in RUC:

- Pre-specified Online Resource j including Resources already self-committed in COP, Resource committed in previous RUC, Resource capacity already committed to provide Ancillary Service, and the operator manually committed Resources

- Additional Resource r that is available to be committed by RUC:

  - For DRUC

- Resource that have submitted a Three-Part Offer into DAM but was not awarded in DAM;

- Resource that did not submit a Three-Part Offer in DAM but is specified as available but Off-line, excluding Resources with a Resource Status of EMR, in its COP; ERCOT create Three-Part for this non-bid Resource;

  - For HRUC

- Resources that have submitted Three-Part Offer by end of Adjustment Period;

- Resource that did not submit a Three-Part Offer by end of Adjustment Period but is specified as available but Off-line, excluding Resources with a Resource Status of EMR, in its COP; ERCOT create Three-Part for this non-bid Resource;

  - For WRUC

- Resource that is specified as available but Off-line, excluding Resources with a Resource Status of EMR, in its COP; ERCOT create Three-Part for this Resource

Similar to DAM, the RUC market clearing problem is a Security Constrained Unit Commitment (SCUC) that is formulated as a Mixed Integer Linear Program (MILP) problem. The RUC problem is formulated as followings:

Minimize:

r,offer,tStartupCostr,t,offer+r,offer,tMingenCostr,t,offer*ResProcuredr,t,offer

+r,offer,seg,tProxyEnergyCurver,offer,seg,t*ResSegMWr,offer,seg,t

+Online Resource j,seg,tProxyEnergyCurvej,seg,t*ResDispSegMWj,seg,t

+ccunit,mod,tTransitionCostccunit,mod,t

+EnergyPenalty∗t(EnergySlackUPMWt+EnergySlackDNMWt)

+Online Resource j,astype,tClearedMWSlackj,astype,t∗ASPenaltyastype

+cTranPenaltyc∗tTranSlackMWc,t

+WeeklyEnergyPenalty∗rSlackWeeklyEnergyr

+WeeklyEnergyPenalty∗Online Resource jSlackWeeklyEnergyj

Subject To:

- Power Balance Constraints for each interval t:

Online Resource jResDispSegMWj,t+r,offer,segResSegMWr,offer,seg,t+

r,offerMinCapMWr,t*ResProcuredr,offer,t+EnergySlackUPMWt−EnergySlackDNMWt

=loadforecastt                                                                                                                      (SPdemand,t)

- Network Constraints at each interval t for both Base Cases and Contingency Cases:

Online Resource jSFj,c,t∗ClearedMWj,t++r,offerSFr,c,t∗(MinCapMWr,t*ResProcuredr,offer,t+segResSegMWr,offer,seg,t) − TranSlackMWc,t ≤ Limitc,t

(SPc,t)

- Resource Constraints for each Resource r:

ResProcuredr,offer,t−ResProcuredr,offer,t−1=ResStartupr,offer,t−ResShutdownr,offer,t

ResStartupr,offer,t+ResShutdownr,offer,t≤1

(mnuptmr−1)ResStartupr,offer,t≤ResProcuredr,offer,t+1+ResProcuredr,offer,t+2+…+ResProcuredr,offer,t+mnuptmr−1

[min(T−t,mndntmr−1)]ResShutdownr,offer,t+ResProcuredr,offer,t+1+ResProcuredr,offer,t+2+…+ResProcuredr,offer,t+min[T−t,mndntmr−1]≤min(T−t,mndntmr−1), t≤T−1

- Resource Initial Condition Constraint for Resource r

ResProcuredr,offer,t=1, t=1,mnuptmr−ResHrinitUpr if ResInitStatus=1

ResProcuredr,offer,t=0, t=1,mndntmr−ResHrinitDnr if ResInitStataus=0

t incurrentdayResStartupr,offer,t+ResNumstartupinitr≤DailyStartuplimitr

- Resource maximum daily startup Constraint for Resource r

t innextdayResStartupr,offer,t≤DailyStartuplimitr

- Resource maximum runtime Constraint for Resource r

ResHrsUpr,offer,t≤ResRuntimer, t≥1

- Down time dependent startup cost for Resource r:

StartupCostr,offer,t≤ResStartupcostOfferr,offer,t(ResHrsDnr,offer,t)

StartupCostr,offer,t≥ResStartupcostOfferr,offer,t(ResHrsDnr,offer,t) −maxstartupcost∗(1−ResStartupr,offer,t) StartupCostr,offer,t≤maxstartupcost*ResStartupr,offer,t

- Operating limits for each Resource r at interval t:

0≤ResSegMWr,offer,seg,t≤ResProxyCurveSegSizer,offer,seg,t*ResProcuredr,offer,t

0≤segResSegr,offer,seg,t≤(MaxCapMWr,t−MinCapMWr,t)*ResProcuredr,offer,t

- Operating limits for each Online Resource j at interval t:

0≤ResDispSegMWj,seg,t≤ResProxyCurveSegSizej,seg,t

ResDispMWj,t=MinCapMWj,t+segResDispSegMWj,seg,t

MinCapMWj,t≤ResDispMWj,t≤MaxCapMWj,t

- Startup Cost Eligibility for Resource r at interval t:

Assume that Resource’s self-commitment starts up the Resource at intervalt'>t,.  For each interval t before t’, set StartupCostr,offer,t=0 if ResStartupr,offer,t=1 and ResProcuredr,offer,k=1 for all k between t+1 and t’-1

- Protection of Resource Capacity Providing Ancillary Service for Online Resource j at interval t:

LASLj,t−ClearedMWSlackj,DRS,t≤ResdispMWj,t≤HASLj,t+URS,RRS,NSRSClearedMWSlackj,t

- Some Weekly Constraint for Resource r in WRUC:

tMinCapMWr,t*ResProcuredr,offer,t+seg,tResOfferSegr,offer,seg,t−SlackWeekenergyrWeeklyEnergylimitr

tResDispMWj,t−SlackWeeklyEnergyj≤WeeklyEnergylimitj

tResStartupr,offer,t≤WeeklyStartuplimitr

- Ignore Temporal Constraints Violated by Self-Commitment

Do not apply minimum up/down time in 3), maximum run time in 6),  daily/weekly startup and weekly energy constraints in 5) and 12) to the self-commitment period

- Combined Cycled Resource Configuration Constraints:

All the Resource-level constraints defined above for Resource r remain applicable for any possible configuration for Combine Cycle Generation Resource. In other words, in case of Combined Cycle Resource r represents configuration r of the Combined Cycle Resource.

The additional inter-configuration constraints for Combined Cycle Resource ccunit with multiple configurations mod at t include:

ResProcuredccunit,offer,t=modResProcuredccunit,mod,offer,t≤1,

ResMinRuntimeccunit,mod≤ResHrsUpccunit,mod,offer,t≤ResMaxRuntimeccunit,mod

ResProcuredccunit,offer,t is subjected to Combined Cycle Plant Minimum Down and Minimum Run Time

The Inter-Configuration transition is feasible between certain configurations and between certain configurations to the off state.

The transition cost associated with transition from Configuration mod' at t'  to Configuration mod at t

is TransitionCostccunit,mod,t(mod',t')

The RUC problem input parameters are

- T is the number of study intervals;

- Loadforecastt is the ERCOT total load forecast at interval t;

- MaxCapMWr,tand MinCapMWr,tare the max and min operating limits of Resource r at interval t;

- mnuptmr,t and mndntmr,t are the minimum up time and minimum down time of Resource r ;

- ResInitStatusr is the initial status of Resource rat the start of the study period, 1: Online, 0: Offline;

- ResMaxRuntimer is the maximum runtime of Resource r;

- For Combined Cycle Resource, ResMaxRuntimeccunit,mod and ResMinRuntimeccunit,mod is the maximum and minimum runtime of Configuration mod of Combined Cycle Resource ccunit;

- ResHrinitUpr is the number of intervals that Resource rhas been Online at the start of the study period

- ResHrinitDnr is the number of intervals that Resource rhas been Offline at the start of the study period;

- ResNumstartupinitr is the number of daily startups of Resource rat  the start of the study period;

- WeeklyStartuplimitr is the maximum weekly startup limit of Resource r;

- WeeklyEnergylimitr is the weekly energy limit of Resource r;

- WeeklyRuntimelimitr is the maximum weekly runtime of Resource r;

- WeeklyEnergylimitj is the weekly energy limit of Online Resource j;

- MaxCapMWj,tand MinCapMWj,tare the max and min operating limits of Online Resource j at interval t;

- HASLj,tand LASLj,tare the high and low Ancillary Service limits of Online Resource j at interval t;

- ProxyEnergyCurver,offer,seg,tis the price of MW segment seg of  the Proxy Energy Curve of Resource r with Three-Part Offer at interval t;

- ResProxyCurveSegSizer,offer,seg,t is MW size of segment seg of  the Proxy Energy Curve of Resource r with Three-Part Offer at interval t;

- ProxyEnergyCurvej,seg,tis the price of MW segment seg of  the Proxy Energy Curve of Online Resource j at interval t;

- ResProxyCurveSegSizej,seg,t is MW size of segment seg of  the Proxy Energy Curve of Online Resource j at interval t;

- ResStartupcostOfferr,offer,tis the start up cost offer of Resource r with Three-Part Offer at interval t;

- maxstartupcost is the maximum startup cost of the start up cost offers of  all Resource r;

- MineneCostr,offer,tis the minimum generation cost of Resource r with Three-Part Offer at interval t;

- Limitc,t is the NSM calculated limit of transmission constraint c at interval t. This limit represents the aggregated effect of the latest control variables on the constraint (excluding load contribution) and the violation on the constraint.;

- SFr,c,t is the Shift Factor of Resource r associated with transmission constraint c at interval t;

- SFj,c,t is the Shift Factor of Online Resource j associated with transmission constraint c at interval t;

- EnergyPenaltyis the penalty cost of violating the power balance constraint;

- TranPenaltyCostcis the penalty cost of violating the transmission constraint c;

- ASPenaltyastype is the penalty cost of violating the AS protection for AS type astype;

- WeeklyEnergyPenalty is the penalty cost of violating the resource weekly energy limit

The RUC problem decision variables are

- Integer Variables:

  - ResProcuredr,offer,tis 1 if Resource r with Three-Part Offer is online for procurement at interval t, 0 offline;

  - For Combined Cycle Resource, ResProcuredccunit,mod,offer,tis 1 if Configuration mod of Combined Cycle Resource ccunit with Three-Part Offer is online for procurement at interval t, 0 offline;

  - For Combined Cycle Resource, ResProcuredccunit,offer,tis 1 if any of the multiple Configurations  of Combined Cycle Resource ccunit with Three-Part Offer is online for procurement at interval t, 0 offline;

  - ResStartupr,offer,t is 1 if Resource r with Three-Part Offer is started up at interval t, 0 otherwise;

  - ResShutdownr,offer,t is 1 if Resource r with Three-Part Offer is shut down at interval t, 0 otherwise;

  - ResHrsUpr,offer,t is the number of intervals that Resource rhas been Online at the end of interval t;

  - ResHrsDnr,offer,t is the number of intervals that Resource rhas been Offline at the start of interval t;

- Continuous Variables:

  - ResSegMWr,offer,seg,tis the scheduled MW of segment seg of Proxy Energy offer of Resource r with Three-Part Offer at interval t;

  - ResDispSegMWj,seg,tis the scheduled MW of segment seg of Proxy Energy offer of Online Resource j at interval t

  - ResDispMWj,tis the scheduled net MW of Online Resource j at interval t;

  - StartupCostr,offer,t is the startup cost for Resource rat the start of interval t

- Dual Variables ( Shadow Prices)

  - SPdemand,t is the dual variable associated with the power balance constraint at interval t;

  - SPc,t is dual variable associated with the transmission constraint  c at interval t;

- Non-Negative Slack Variables:

  - EnergySlackUPMWtand EnergySlackDNMWt are the slack variables for the power balance constraint at interval t;

  - TranSlackMWc,t is the slack variable for the transmission constraint c at interval t

  - ClearedMWSlackj,astype,t is slack variable for protecting Online Resource j capacity for AS type astype at interval t;

  - SlackWeeklyEnergyr is the slack variable for the weekly energy constraint of Resource r;

  - SlackWeeklyEnergyj is the slack variable for the weekly energy constraint of Online Resource j

# Appendix: Acronyms

AS	Ancillary Service

COP	Current Operating Plan

DAM	Day-Ahead Market

DRUC	Day-Ahead Reliability Unit Commitment

DC Tie	Direct Current Tie

DSI	Dispatch Scheduler Initialization

DSP	Dispatch Scheduler Publishing

DSR	Dynamically Scheduled Resource

EECP	Emergency Electric Curtailment Plan

ERCOT	Electric Reliability Council of Texas, Inc.

EMS	Energy Management System

FIP	Fuel Index Price

FOP	Fuel Oil Price

HASL	High Ancillary Service Limit

HDL	High Dispatch Limit

HE	Hour Ending

HEL	High Emergency Limit

HRUC	Hourly Reliability Unit Commitment

HSL	High Sustained Limit

Hz	Hertz

IUC	Initial Unit Commitment

kV	Kilovolt

LASL	Low Ancillary Service Limit

LDL	Low Dispatch Limit

LEL	Low Emergency Limit

LFC	Load Frequency Control

LMP	Locational Marginal Price

LSL	Low Sustained Limit

MMS	Market Management System

MOI	Market Operator Interface

MTLF	Mid-Term Load Forecast

MVAr	Mega Volt-Amperes reactive

MW	Megawatt

MWh	Megawatt Hour

NCUC	Network Constrained Unit Commitment

NDP	Network Data Preparation

Non-Spin	Non-Spinning Reserve

NSM	Network Security Monitor

QF	Qualifying Facility

QSE	Qualified Scheduling Entity

RAP	Remedial Action Plan

Reg-Down	Regulation Down

Reg-Up	Regulation Up

RMR	Reliability Must-Run

RPP	Renewable Production Potential

RRS	Responsive Reserve

SAV	Save Case

SCED	Security-Constrained Economic Dispatch

SCUC	Security-Constrained Unit Commitment

SPS	Special Protection Scheme

STWPF	Short Term Wind Power Forecast

TAC	Technical Advisory Committee

WGR	Wind-Powered Generation Resource

WRUC	Weekly Reliability Unit Commitment