DWG Report to ROS, January 2007

- The last DWG meeting was November 29-30, 2006.

- The DWG asks for approval of the “Underfrequency Load Shedding 2006 Assessment and Review” report.  This report will be forwarded to ROS along with this monthly report.  Last February, ROS voted to delay the DWG’s UFLS program assessment until 2007; however, the DWG decided to do an assessment and review of the May 2003 event rather than simulations on a future base case.  We reviewed analysis that had already been done based on the belief that an actual test of a program is more useful than any simulations.  Conclusions:

  - The UFLS program effectively arrested frequency decline and the system eventually returned to normal.

  - The May 2003 event did not result in any islanding of the ERCOT transmission system, which is consistent with its design.

  - Simulation of the May 2003 event by using the standard ERCOT dynamics database did not predict the magnitude of frequency decline that occurred.  The reasons for this include an inaccurate load model and governor droop response closer to 17% than the modeled 5%.  Several efforts are underway to improve the dynamic models used in ERCOT including the combined cycle governing model development, OGRR188 which was submitted by the DWG and requires generator model validation, and the EPRI Load Modeling project.

- Of the listed 2006 DWG tasks, several are still ongoing.

  - The 2006 DWG Stability Book should be completed in the next two weeks.

  - The DWG did not submit dynamic voltage recovery criteria in 2006, but we did discuss this subject several times throughout the year.  We had several good discussions and progress was made; however, work still needs to be done to reach agreement on ERCOT-wide criteria.

  - Other tasks are long-term and will continue throughout 2007 and beyond.

- DWG has begun work on the flat start activities for the 2007 summer peak base case.

- The DWG recommends Vance Beauregard of AEP to be the 2007 DWG Chair.  Vance is currently the DWG Vice-chair.  The DWG recommends Tony Hudson of Texas-New Mexico Power to be the 2007 DWG Vice-chair.

- The next DWG meeting is scheduled for February 7-8, 2007.

DWG Tasks, 2006

| Task | Status |
| --- | --- |
| Flat start 2006 case | Complete |
| Flat start 2008 case | Complete |
| Incorporate load as responsive reserve models into dynamics database. | Complete |
| Flat start 2006 case with wind models. | Complete |
| Publish flat start book. | Working |
| Make annual determination of the number and location of dynamic monitoring devices. | Complete |
| Assist Black Start Task Force in evaluating ERCOT-wide black start plan | Complete |
| Dynamic Voltage Recovery criteria | Working |
| Review recently approved NERC Standards with respect to ERCOT Op Guides and Protocols | Working |
| Review current ERCOT criteria for proposed NERC Standards (PRC-019,PRC-024,MOD-026-1,MOD-027-1) | Complete |
| Draft OGRR(s) to comply with NERC Field Test Standards | Complete |
| Participate in ROS Ad Hoc Task Force regarding Power System Stabilizers | Working |
| Annual Procedural Manual review/update. | Complete |
| Begin 2007 flat start activities. | Working |