## Slide 1
1
2
3
4

## Slide 2
Pre-Disturbance Frequency (60.004 Hz) at 02:54:06
Lowest Point (59.691 Hz) at 02:54:55
Recovery (60 Hz) at 03:03:26

## Slide 3: December 22nd, 2006 NERC Reportable Event
1 – 165 MW LaaR deploys at 02:54:28. Frequency is 59.824 (PI shows 59.774 at 02:54:12)
2 – At 02:54:55, with frequency at 59.691 Hz, per the High-Speed Recorder, an additional 538 MW of LaaR deployed.
3 – VDI issued to deploy all LaaRs at 02:58:10
4 – 10-minute mark from VDI at 03:08:10
Between 2 and 4, an additional 335 MW of LaaR was deployed, for a total of ~1047 MW
  Note: Data latency can mask some of the response, leading some of the numbers not to add up exactly—especially when comparing to frequency at the same instant in time.

## Slide 4: December 22nd, 2006 NERC Reportable Event
EECP Step 1 declared at 03:03 Adjusted Responsive Reserve at 1751 MW
LaaRs restored at 03:58
EECP Step 1 cancelled at 04:07
Advisory issued for Adjusted Responsive Reserve below 3000 MW

## Slide 5
803 MW trip, 804 MW unit begins ramp back
130 MW unit trip
Unit on ramp back trips 561 MW, 2 units ramp back 170 MW but stay on-line

## Slide 7
~ 1880 MW generation lost
Initial total unit output ~ 1900 MW
~ 20 MW remains online

## Slide 11
Events of 12/13/06 EECP Step One Event
04:20 511 MW unit trip
06:05 100 MW unit trip
06:14 175 MW unit trip
Total Capacity Tripped above was 1100MW
Morning Peak Load As Forecasted
06:20 Advisory, Adjusted Responsive less than 3000MW
06:39 Alert, Adjusted Responsive less than 2500MW
06:52 EECP Step 1, Adjusted Responsive less than 2300MW
07:03 Adjusted Responsive 2178 MW, ERCOT Load 37189
07:09 Adjusted Responsive Reserve Started recovering
07:16 Cancelled EECP Step 1
07:30 Cancelled Alert, Responsive above 2500MW
08:40 Cancelled Advisory, Responsive above 3000MW
Summary: Loss of generation during morning load pickup

## Slide 14
Events of 12/23/06 EECP
15:52 800MW capacity lost due to forced maintenance
17:00 ERCOT load approximately 1000MW above forecast
17:10 Advisory, Adjusted Responsive less than 3000 MW
17:45 Alert, Adjusted Responsive less than 2500 MW
18:15 EECP Step #1 implemented, Responsive < 2300MW
18:18 Responsive 2206MW, ERCOT Load 33900MW
18:35 ERCOT ordered 1361MW of capacity online within the expected time frame of the emergency according to EECP Procedures.
18:50 Responsive Reserve 2325MW, ERCOT Load 34150MW
19:45 Starting to release generation that was brought on line
20:40 Responsive Reserve 2642MW, ERCOT Load 33756MW
20:45 Terminate EECP Step #1
Summary: Forced unit outage combined with higher than expected evening load pickup