## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For the Generation Subsystem, Version 0.90
S.No. | Issuing Entity (Name) | Page Number | Section | Req. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | Brazos Electric (T.Kroskey) | 6 | 1 |  |  | The Generation Subsystem includes Load Frequency Control (LFC), the Ancillary Services Capacity Monitor, and the Resource Limit Calculator, each of which are described in this Requirements Specification., Iin addition to requirements are included for Resource Qualification Testing and Inputs/Outputs | Accepted | J. Mandavilli J. Adams
2 | Brazos Electric (T.Kroskey) | 7 | 1.3 |  |  | The scope of this document is to elicit requirements for tThe Generation Subsystem to be in compliance with the Nodal Protocols published in May 2006, NERC, FERC and PUCT guidelines. … Any scope changes to this requirements specification due to alternate design proposals must be driven by Nodal Protocol Revision Request (NPRR) and channeled through the Nodal Change Control Board (CCB). | Accepted | J. Mandavilli J. Adams
3 | LCRA (G.Graham | 7 | 1.3 |  |  | Does the scope need to include capabilities for the following operational modes? 1. Constant Frequency 2. Frequency Time Error Correction | Accepted | J. Mandavilli J. Adams | Yes. ERCOT will update document to include these capabilities
4 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | All Generation Subsystem requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Functional Block Diagram that describes the Generation Subsystem. | Accepted | J. Mandavilli J. Adams
5 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | The Generation Subsystem of the Energy Management System (EMS) consists of three major constituentsfunctional components: Load Frequency Control (LFC), the Ancillary Services Capacity Monitor, and the Resource Limit Calculator, along with other functionality to manage inputs and outputs and simplify Resource qualification testing. The primary purpose of LFCLoad Frequency Control is to maintain a desired system frequency by deploying Regulation Service and, if necessary, deploying Responsive Reserve and Non-Spinning Reserve Services. LFC uses the Supervisory Control and Data Acquisition (SCADA) Subsystem of the EMS to interface with the QSEs that, in turn, interface to individual Generation and Load Resources. LFC is also responsible for transmitting the Base Points and LMPs calculated by the Security Constrained Economic Dispatch (SCED) process. The Ancillary Services Capacity Monitor determines available reserve capacity from system Resources tothat provide the ancillary services of Regulation, Responsive Reserve, and Non-Spinning Reserve. The Resource Limit Calculator calculates Resource limits and ramp rates that are used as inputs for both LFC and SCED. | Accepted | J. Mandavilli J. Adams
6 | Reliant (F.Trefny) | 8 | 2.1 |  |  | 2.1 Proposed System Scope This document defines the requirements for the Generation Subsystem. The requirements in scope for this document include: … • Storing of Generation Subsystem data needed for performance monitoring and compliance | Accepted | J. Mandavilli J. Adams
7 | Reliant (F.Trefny) | 8 | 2.1 |  |  | The following items are not in the scope of Generation Subsystem functionality: • DC tie line scheduling and curtailment of DC tie-lines are we going to have an Interchange transaction scheduler? | Clarification Provided | J. Mandavilli J. Adams | Yes, but the DC Tie scheduler is a separate subsystem within ERCOT that includes all interchange transactions.
8 | Brazos Electric (T.Kroskey) | 8 | 2.1.1 |  |  | 2.1. 1 To Be Sub-Process for the Generation Subsystem Sub-Process The Generation Subsystem of the Energy Management System (EMS) adjustsmonitors and control power system generation output to controlmaintain desired system frequency and ensures that ERCOT complies with established NERC frequency control performance requirements. … The Generation Subsystem treats each of these as separate Resource.. The Generation Subsystem collects, validates and filters this information, as well as data from SCED and computes. Computing the Area Control Error (ACE) as a function of the difference between scheduled and actual frequency deviation times ERCOT’s predetermined frequency bias., Tthe Generation Subsystem (Load Frequency Control (LFC) component) determines the Resource control action necessary to keep frequency deviation within established limits and to comply with NERC control performance measures. | Accepted | J. Mandavilli J. Adams
9 | Reliant (F.Trefny) | 8 | 2.1.1 |  |  | The Generation Subsystem of the Energy Management System (EMS) adjusts power system gGeneration Resources and Controllable Load Resources output to control frequency and ensures that ERCOT complies with established NERC frequency control performance requirements. The Generation Subsystem accomplishes these goals by utilizing the Ancillary Services of Regulation, Responsive Reserve and Non-Spinning Reserve in cooperation with the QSEs that distribute MW control requirements to individual system Resources, monitor their operation, and telemeter Resource information to ERCOT. | Accepted | J. Mandavilli J. Adams
10 | TXU (B.Spangler) | 8 | 2.1.1 |  |  | {TXU Comment: TXU has elected to offer its comments in this description section rather than in Section 3, Functional Requirements. This better suits the nature of the comments; however, it is possible that the resolution of these comments may require revisions within the functional requirements section.} | Clarification Provided* | J. Mandavilli J. Adams | Discussed in individual comments below
11 | Reliant (F.Trefny) | 9 | 2.1.1 |  |  | QSEs are responsible for acquiring Generation and Load Resource information, determining Resource sStatus that indicates Resource availability for Regulation, Responsive Reserve and Non-Spin Reserve, and telemetering this data to ERCOT. Telemetry from Generation Resources with Split Generation Meters Jointly Controlled Units [nodal protocols do not use the term “jointly” any more] and Combined Cycle Units provide ERCOT with information that represents these units as if they were individual Generation Resources. | Accepted | J. Mandavilli J. Adams | We will search and replace the correct wording throughout the document
12 | TXU (B.Spangler) | 9 | 2.1.1 |  |  | QSEs are responsible for acquiring Generation and Load Resource information, determining Resource status that indicates Resource availability for Regulation, Responsive Reserve and Non-Spin Reserve, and telemetering this data to ERCOT. Telemetry from Jointly Controlled Units {TXUComment: Jointly controlled unit is not a Nodal Protocol defined term. If this reference is to a Split Generation Resource, which is defined in the Nodal Protocols, then please revise the wording to reflect this term} and Combined Cycle Units provide ERCOT with information that represents these units as if they were individual Resources. The Generation Subsystem treats each of these as separate Resource.. | Accepted | J. Mandavilli J. Adams | We will search and replace the correct wording throughout the document
13 | Reliant (F.Trefny) | 9 | 2.1.1 |  |  | Based on Regulation participation factors for each Resource telemetered by the corresponding QSEs and taking into consideration the regulation MWs already issued but yet to be delivered not acted upon, as well as Resource limits and regulation control ramp rates, LFC determines and issues to each QSE an aggregate Regulation MW control requirement. The QSEs distribute these Regulation MWs to the regulating Resources under their direction providing Regulation Ancillary Services and ensures that the response of these Resources matches the requested MW control action over time.. | Accepted | J. Mandavilli J. Adams
14 | NRG (D.S.Mai) | 9 | 2.1.1 |  |  | Based on Regulation participation factors - note: should it be “schedules” instead of “participation factors”? - for each Resource telemetered by the corresponding QSEs and taking into consideration the regulation MWs already issued but not acted upon as well as Resource limits and ramp rates, LFC determines and issues to each QSE an aggregate Regulation MW control requirement. | Accepted | J. Mandavilli J. Adams | Yes. ERCOT will update document to include this change
15 | TXU (B.Spangler) | 9 | 2.1.1 |  |  | The QSEs distribute these Regulation MWs to the regulating Resources under their direction and ensures that the response of these Resources matches the requested MW control action. | Accepted | J. Mandavilli J. Adams
16 | Reliant (F.Trefny) | 9 | 2.1.1 |  |  | LFC also recalculates the High Ancillary Service Limit (HASL) for each Resource after the QSEs telemeter to ERCOT a revised Responsive Reserve Ancillary Service sSchedule for each affected Resource. These revised HASLs are utilized by SCED to re-dispatch Responsive Reserve Resources into the regions previously held in reserve back for Responsive Reserve capacity. | Accepted | J. Mandavilli J. Adams
17 | TXU (B.Spangler) | 9 | 2.1.1 |  |  | When the system frequency drops below a pre-specified level, when available Regulation Up energy is insufficient, or when a System Emergency has been declared, LFC or the ERCOT Operator may activate Responsive Reserve Service to correct the situation. The calculated amount of Responsive Reserve Service energy required is allocated to all Resources with a Responsive Reserve Service award, based on their Responsive Reserve participation factors telemetered by the corresponding QSEs. LFC determines and issues to each QSE an aggregate Responsive Reserve MW control requirement to distribute to their associated Responsive Reserve Resources. LFC also recalculates the High Ancillary Service Limit (HASL) for each Resource after the QSEs telemeter to ERCOT a revised Responsive Reserve schedule for each affected Resource {TXU Comment: This process seems to place a requirement on the QSE to respond in an appropriately determined time period. Otherwise, the calculation of the new HASL will be delayed. (continued in following comment) | Pending | J. Mandavilli J. Adams | See response in 18 below.
18 | TXU (B.Spangler) | 9 | 2.1.1 |  |  | (continuation of previous comment) Failure of a QSE to make a timely adjustment to its AS schedule appears to result in a forced SCED recall of the deployed Responsive Reserve which may be counter to the immediate LFC control requirement. IF this is true then the QSE interface specification needs to reflect a timing requirement for the AS updated schedule following a RRS LFC deployment. This requirement must be part of the EDS test sequence and must be subject to ongong performance monitoring. Consequently, the system must record the event sequence in such a manner as to validate the QSE performance. Additionally, how will the Generation Subsystem respond in the event there is a delay in the AS Schedule update from the QSE?} These revised HASLs are utilized by SCED to re-dispatch Responsive Reserve Resources into the regions previously held back for Responsive Reserve capacity. | Pending | J. Mandavilli J. Adams | This is a valid comment, but is not appropriate to the Generation subsystem. We have proposed a white paper that addresses part of this issue, and is expected to generate a protocol change. When such change is approved, we expect the requirement will be included in a QSE monitoring specification/ or and QSE interface document. We have added the issue to the IDA Punch list.
19 | NRG (D.S.Mai) | 9 | 2.1.1 |  |  | When the system frequency drops below a pre-specified level, when available Regulation Up energy is insufficient, or when a System Emergency has been declared, LFC or the ERCOT Operator may activate Responsive Reserve Service to correct the situation. The calculated amount of Responsive Reserve Service energy required is allocated to all Resources with a Responsive Reserve Service award, based on their Responsive Reserve participation factors - note: should it be “schedules” instead of “participation factors”? - telemetered by the corresponding QSEs. | Accepted | J. Mandavilli J. Adams | Yes. ERCOT will update document to include this change
20 | Reliant (F.Trefny) | 9 | 2.1.1 |  |  | When the available system capacity is still insufficient, such as following a disturbance, Non-Spinning Reserve Service may be initiated manually by the Operator. on an all-or-none basis. When the Non-Spinning Reserve Service is invoked, the QSEs are notified. As Non-Spin Resources become available, the QSEs telemeter to ERCOT a revised Non-Spinning Reserve Ancillary Service sSchedule for each affected Resource and LFC then recalculates new values of HASL for these Resources. | Accepted | J. Mandavilli J. Adams
21 | TXU (B.Spangler) | 10 | 2.1.1 |  |  | When the available system capacity is still insufficient, such as following a disturbance, Non-Spinning Reserve Service may be initiated manually by the Operator on an all-or-none basis {TXU Comment: As noted in Assumption 2.2(1) below, the proposal to deploy NSR on an all or nothing basis has not yet been approved by the TAC and is the subject of a WMS review. While the all or nothing deployment may be appropriate for operator response to system disturbances, there is question as to whether or not it is an appropriate response to a SCED insufficiency.}. | Clarification Provided* | J. Mandavilli J. Adams | Deleted the "all or none" phrase. The same issue is covered by #20
22 | GP&L (R.Hoeinghaus) | 9 | 2.11 |  |  | When the available system capacity is still insufficient, such as following a disturbance, Non-Spinning Reserve Service may be initiated manually by the Operator on an all-or-none basis. GP&L Comment: “all-or-none” has not been decided and we cannot find “all-or-none” in the procedure before TAC as referenced in 2.2.1 below | Clarification Provided* | J. Mandavilli J. Adams | Deleted the "all or none" phrase. The same issue is covered by #20
23 | TXU (B.Spangler) | 10 | 2.11 |  |  | When the Non-Spinning Reserve Service is invoked, the QSEs are notified. As Non-Spin Resources become available, the QSEs telemeter to ERCOT a revised Non-Spinning Reserve schedule for each affected Resource. (and a revised unit status for units coming online) LFC then recalculates new values of HASL for these Resources. This permits SCED to re-dispatch the MW levels of these Non-Spin Resources as necessary into the regions previously held back for Non-Spinning Reserve capacity. LFC monitors the response of individual Generation and Load Resources to determine whether they respond to the Non-Spinning Reserve deployment. {TXU Comment: The concerns expressed above regarding RRS deployments and HASL recalculations also apply for NSR deployment.} | Pending | J. Mandavilli J. Adams
24 | GP&L (R.Hoeinghaus) | 9 | 2.11 |  |  | When the Non-Spinning Reserve Service is invoked, the QSEs are notified. As Non-Spin Resources become available, the QSEs telemeter to ERCOT a revised Non-Spinning Reserve schedule for each affected Resource and LFC then recalculates new values of HASL for these Resources. This permits SCED to re-dispatch the MW levels of these Non-Spin Resources as necessary into the regions previously held back for Non-Spinning Reserve capacity. LFC monitors the response of individual Generation and Load Resources to determine whether they respond to the Non-Spinning Reserve deployment. GP&L Comment: If NSRS is part of the SCED basepoint, how are you going to monitor whether or not a Resource (other than a load resource) responded. The NSRS will be divided out based on the ED & SC portions of SCED without LFC’s knowledge. | Clarification Provided | J. Mandavilli J. Adams | ERCOT proposes to monitor the additional capacity provided to determine if the non-spin is provided. This seems to be compliant with the current section 8 monitoring process.
25 | Reliant (F.Trefny) | 9 | 2.1.1 |  |  | The Generation Subsystem (Resource Limit Calculator component) also provides SCED with Resource limits (Dispatch limits, HDL and LDL, in addition to High and Low Ancillary Service lLimits) and Resource ramp rates [SCED does not use ramp rates]. In turn, SCED determines new Resource Base Points and provides other Resource-specific information that the Generation Subsystem sends to QSEs. All the limit calculations are based solely on the telemetered values from QSEs, including theeach Resource’s Ancillary Service Resource sSchedules and HSL and LSLlimits. | Accepted | J. Mandavilli J. Adams
26 | TXU (B.Spangler) | 10 | 2.11 |  |  | The Generation Subsystem (Resource Limit Calculator component) also provides SCED with Resource limits (Dispatch limits in addition to High and Low Ancillary Service limits) and Resource ramp rates. In turn, SCED determines new Resource Base Points and provides other Resource-specific information that the Generation Subsystem sends to QSEs. All the limit calculations are based solely on the telemetered values from QSEs, including the Resource Ancillary Service Resource schedules and limits. {TXU Comment: Does this include telemetered ramp rate for SCED use? TXU supports the use of telemetered ramp rates as opposed to a strict use of resource parameter ramp rates. The use of telemetered ramp rates enhances the LFC control performance and the performance of the LFC/SCED interaction. While the use of telemetered ramp rates introduces the possibility of inappropriate actions by QSEs to affect resource base points, TXU believes that such actions would be discoverable by the IMM and that this will provide a sufficient restraint to such actions.} | Clarification Provided | J. Mandavilli J. Adams | No. ERCOT proposed this in one of the TPTF meetings and no consensus was reached in terms of using telemetered ramp rates. Because existing protocols specify use of the parameter ramp rates, we need TPTF consensus, and a protocol change before we specify use of the telemetered ramp rate.
27 | Reliant (F.Trefny) | 10 | 2.1.1 |  |  | The Generation Subsystem (Ancillary Services Capacity Monitor component) also calculates available capacity values for Ancillary Services (e.g., Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED) and provides this information to ERCOT Operators, QSEs, and other Market Participants. Alarms are generated when available reserves fall outside the requirement. | Accepted | J. Mandavilli J. Adams
28 | Brazos Electric (T.Kroskey) | 10 | 2.1.1 |  |  | The Generation Subsystem (Ancillary Services Capacity Monitor component) also calculates available reserve capacity values for Ancillary Services (e.g., Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED) and provides this information to ERCOT Operators, QSEs, and other Market Participants. … Additional descriptions of the To Be Sub-process for the Generation Subsystem Sub-process may be found in Appendix A. | Accepted | J. Mandavilli J. Adams
29 | Reliant (F.Trefny) | 10 | 2.1.1 |  |  | Finally, the Generation Subsystem (Resource Qualification Testing component) facilitates qualifications testing Resources that may provide for Ancillary Services Resources by sending test control Mws Base Points to QSEs, collecting each Resource’s response information, calculating the average values of each Resource’s MWs and response rates, and presenting this information to the Operator. {note: all Resource qualifications are by individual Resource] | Accepted | J. Mandavilli J. Adams
30 | Reliant (F.Trefny) | 10 | 2.1.1 |  |  | All of the data telemetered from QSEs (including each Resource’s power, status, limits, and ramp rate values), telemetered to QSEs (including Regulation & Responsive Reserve MW requirements, Non-Spin deployment status, and Resource Base Points), and exchanged with SCED (including Base Points, telemetered AS schedules, and calculated available capacity values) are saved for use by other ERCOT functions, including Settlements, Performance Monitoring and Compliance, IMM monitoring, and long-term historical storage. | Accepted | J. Mandavilli J. Adams
31 | Reliant (F.Trefny) | 11 | 2.2 |  |  | 2. Section 6.5.7.2 (3) is interpreted to mean the QSE will telemeter the RRSResponsive Reserve Ancillary Service sSchedule. | Accepted | J. Mandavilli J. Adams
32 | Reliant (F.Trefny) | 11 | 2.2 |  |  | 3. Section 6.5.7.2 (3) is interpreted to mean the HASL will be increased by the amount of the RRSResponsive Reserve energy deployment when RRSResponsive Reserve is deployed. | Accepted | J. Mandavilli J. Adams
33 | TXU (B.Spangler) | 11 | 2.2 |  |  | 4. We assumed that the NSRS telemetered amount from QSE’s to ERCOT will not be adjusted down to reflect the amount of NSRS deployed by ERCOT, but will remain constant throughout a deployment event. {TXU Comment: this assumption seems contrary to the discussion in Section 2.1.1 for NSR deployment where the deployment of NSR appears to be handled in the same manner as the RRS deployment. Additionally, this seems contrary to GS-FR22.} | Accepted | J. Mandavilli J. Adams | This assumption will be deleted
34 | LCRA (G.Graham | 11 | 2.2 |  |  | 4. We assumed that the NSRS telemetered amount from QSE’s to ERCOT will not be adjusted down to reflect the amount of NSRS deployed by ERCOT, but will remain constant throughout a deployment event. Please clarify why this assumption was made. Is it because NSRS is an all or none deployment? Since units have 30 minutes to come on-line, would it not be useful to see the remaining reserve during the 30 minute ramp-in period? | Clarification Provided* | J. Mandavilli J. Adams | This assumption will be deleted
35 | GP&L (R.Hoeinghaus) | 11 | 2.2 |  |  | 4. We assumed that the NSRS telemetered amount from QSE’s to ERCOT will not be adjusted down to reflect the amount of NSRS deployed by ERCOT, but will remain constant throughout a deployment event. GP&L Comment: Don’t understand this statement –either before the White Paper outcome or after - per the white paper outcome at the TPTF meeting, we would send the NSRS responsibility per unit and NSRS ancillary service schedule per unit. | Clarification Provided* | J. Mandavilli J. Adams | This assumption will be deleted
36 | Brazos Electric (T.Kroskey) | 11 | 2.2 |  |  | 4. It isWe assumed that the NSRS telemetered amount from QSE’s to ERCOT will not be adjusted down to reflect the amount of NSRS deployed by ERCOT, but will remain constant throughout a deployment event. | Clarification Provided* | J. Mandavilli J. Adams | This assumption will be deleted
37 | GP&L (R.Hoeinghaus) | 11 | 2.2 |  |  | In addition to the documents referred in Section 1 of this document these requirements specifications are based on ERCOT Operating Guides, dated June 1, 2006. GP&L Comment: This makes this difficult. TPTF votes whether a business requirements document is in compliance with the Protocols (Protocols are approved documents) ERCOT Nodal Operating Guides are NOT APPROVED YET and are still being rewritten. | Clarification Provided | J. Mandavilli J. Adams | ERCOT staff referred to the existing operating guides in answering some questions (example: droop setting requirement 5%). We believe this is a prudent and reasonable process.
38 | GP&L (R.Hoeinghaus) | 121 | 3.1.1 | GS-FR2 |  | Coverage of Protocol: Full (not completely full - See GP&L comment under description) Description: Based on the frequency error, LFC shall calculate Area Control Error (raw ACE) by subtracting the actual frequency in Hz from the scheduled system frequency (normally 60Hz), and multiplying the result by a frequency bias constant calculated using a TAC approved process, in MW/0.1 Hz. GP&L Comment: Left out part of 6.5.7.6.1(2) which states that after you have done the above, “The ACE algorithm then takes that product and subtracts the difference between the Real-Time output and the Base Point for all Dynamically Scheduled Resources.” | Clarification Provided* | J. Mandavilli J. Adams | This is covered as part of the next requirement GS-FR3. ERCOT will make necessary changes to the protocol references to correct the same. Section 6.5.7.6.1 (2) will be referenced for both GS-FR2 and GS-FR3 as partial coverage.
39 | Reliant (F.Trefny) | 13 | 3.1.1 | GS-FR3 |  | Description: LFC shall calculate QSE level Reg-Up or Reg-Down deployments assuming all Resources are ramping to at their last Base Points issued by SCED. | Clarification Provided* | J. Mandavilli J. Adams | ERCOT proposes changing wording to " LFC shall calculate QSE level reg-up or Reg-Down deployments assuming all resources will be at the base points last issued by SCED"
40 | GP&L (R.Hoeinghaus) | 13 | 3.1.1 | GS-FR3 |  | Description: LFC shall calculate QSE level Reg-Up or Reg-Down deployments assuming all Resources are at their last Base Points issued by SCED. LFC shall calculate the difference between the Real-Time output and the Base Point for all DSRs. This difference shall be subtracted from the ACE to produce a new control error value which is a MW-equivalent correction needed to control the actual system frequency to the scheduled system frequency value. LFC shall ensure that the total reduction will not exceed the ACE. GP&L Question: Understand this is in compliance with protocols but since ACE calculated from frequency deviation is a measure of much control action is needed to correct the deviation, why is ACE being modified as stated above?? | Clarification Provided | J. Mandavilli J. Adams | This is as required by protocol. ERCOT staff agrees that the protocol specified subtracting of the DSR difference is a reasonable adjustment to make, since the DSR's host QSE should be adjusting generation to follow this difference without regulation control.
41 | NRG (D.S.Mai) | 13 | 3.1.1 | GS-FR4 |  | Protocol Reference: Section(s) , 6.5.5.2 (6), 6.5.7.6.1 (8), 6.5.7.6.2.1 (2), 6.5.7.6.2.1 (8), 8.1.2.4.1 (3) … Note: please include the requirement from 8.1.2.4.1 (3) for the deployment of regulation service to each QSE. | Accepted | J. Mandavilli J. Adams | ERCOT must add to this requirement "ERCOT shall limit the deployment of Regulation Service of each QSE for each control cycle equal to 125% of the total amount of Regulation Service in ERCOT divided by the number of control cycles in five minutes. Regulation Service performance must be calculated only for a Resource during intervals for which the Resource shows an ONREG, ONOSREG, or ONRGL status in the COP."
42 | Reliant (F.Trefny) | 13 | 3.1.1 | GS-FR4 |  | QSE’s aggregate Reg-Up and Reg-Down bound limits shall be calculated as the sum of their gGenerators and Controllable Load Resources telemetered Reg-Up and Reg-Down Ancillary Service sSchedules respectively. | Accepted | J. Mandavilli J. Adams
43 | Brazos Electric (T.Kroskey) | 12 | 3.1.1 | GS-FR4 |  | Description: ... Load Resources telemetered Reg-Up and Reg-Down schedules respectively. QSE's Reg-Up and Reg-Down response rate limits shall be calculated as the respective bound limit/ divided by 5. Each of the above calculations shall exclude the following: 1. Resources with Reg-Up inhibit (raise blocked) telemetry when up regulation is in effect 2. Resources with Reg-Down inhibit (lower blocked) telemetry when down regulation is in effect 3. Generator Resources with a telemetered Resource status other than ONREG, ONOSREG, or ONDSRREG 4. Load Resources with telemetered Resource status other than ONRGL 5. Off-line Resource based on real-time data 6. LFC shall allocate Reg-Up and Reg-Down deployment instructions among QSEs based on respective QSE level regulation participation factors while accounting for bound limits and response rate limits as well as the amount of regulation that haswas already been requested. These Reg-Up and Reg-Down deployment instructions shall be sent to each QSE as a portfolio signal. | Pending | J. Mandavilli J. Adams
44 | Reliant (F.Trefny) | 13 | 3.1.1 | GS-FR4 |  | Each of the above calculations shall exclude the following: 1. Resources with Reg-Up inhibitHigh or Low blocks active depending on the direction of control requested telemetry when up regulation is in effect 2. Resources with Reg-Down High or Low blocks active depending on the direction of control requested inhibit telemetry when down regulation is in effect 3. Generator Resources with a telemetered Resource status other than ONREG, ONOSREG, or ONDSRREG 4. Load Resources with telemetered Resource status other than ONRGL 5. Off-line Resources based on telemetry of Resource Status real-time data 6. LFC shall allocate Reg-Up and Reg-Down among QSEs based on respective QSE Ancillary Service Responsibility level regulation participation factors while accounting for bound limits and response rate limits as well as the amount of regulation that was already requested. | Pending | J. Mandavilli J. Adams
45 | Reliant (F.Trefny) | 14 | 3.1.1 | GS-FR5 |  | Description: LFC shall continuously monitor the system frequency deviation against a pre-set Operator-entered threshold. Whenever the magnitude of the system frequency deviation is above this threshold permissive blocking shall be enforced. If ramping of a generator which is not providing regulation service to its Base Point will worsen the ACE, LFC shall issue dispatch instructions to may temporarily suspend ramping to any non-regulating Resource their Base Points by temporarily issuing a new Base Point that is equal to the current generation. When the frequency deviation returns to zero, LFC shall send normal Base Points to reset the permissive blocking. | Pending | J. Mandavilli J. Adams
46 | GP&L (R.Hoeinghaus) | 14 | 3.1.1 | GS-FR5 |  | Description: LFC shall continuously monitor the system frequency deviation against a pre-set Operator-entered threshold. Whenever the magnitude of the system frequency deviation is above this threshold permissive blocking shall be enforced. If ramping of a generator which is not providing regulation service to its Base Point will worsen the ACE, LFC shall issue dispatch instructions to temporarily suspend ramping to their Base Points by issuing a new Base Point that is equal to the current generation. When the frequency deviation returns to zero, LFC shall send normal Base Points to reset the permissive blocking. GP&L Comment: This would seem to be in conflict with FR40 – item 6 which states that a flag will be sent for the QSE to stop ramping a resource. Is this a conflict or are you doing both? If both, then the flag should also be described here as part of the permissive blocking action Note: LFC shall only block generators that are not providing Reg-Up or Reg-Down services and those that are not currently using an Emergency Base Point. GP&L Comments: Since you have a list of what not to block, seems DSR units should not be blocked either as they are following a DSR load - thus matching their output to the load. | Pending | J. Mandavilli J. Adams
47 | Brazos Electric (T.Kroskey) | 14 | 3.1.1 | GS-FR5 |  | Description: LFC shall continuously monitor the system frequency deviation against a pre-set Operator-entered threshold. Whenever the magnitude of the system frequency deviation is above this threshold permissive blocking shall be enforced. If ramping of a generator to its Base Point which is not providing regulation service to its Base Point will worsen the ACE, LFC shall issue dispatch instructions to temporarily suspend ramping to their Base Points by issuing a new Base Point that is equal to the current generation. When the frequency deviation returns to zero (or below a threshold?), LFC shall send normal Base Points to reset the permissive blocking. | Pending | J. Mandavilli J. Adams
48 | Brazos Electric (T.Kroskey) | 14 | 3.1.1 | GS-FR6 |  | Description: LFC shall deploy Reg-Up and Reg-Down necessary to maintain ERCOT System frequency to meet NERC Control Area performance criteria BAL-001, BAL-002 and ERCOT Operating Guides. | Accepted | J. Mandavilli J. Adams
49 | LCRA (G.Graham | 14 | 3.1.1 | GS-FR7 |  | Description: Based on the ACE MW correction, LFC shall issue a control signal every four seconds to each QSE providing Regulation Service. Should this finally be SCE instead of ACE – or is ACE correct for Nodal? | Clarification Provided | J. Mandavilli J. Adams | ACE is correct for Nodal
50 | Brazos Electric (T.Kroskey) | 15 | 3.1.1 | GS-FR7 |  | Description: Based on the calculated ACE MW correction, LFC shall issue a control signal every four seconds to each QSE providing Regulation Service. | Accepted | J. Mandavilli J. Adams
51 | Brazos Electric (T.Kroskey) | 15 | 3.1.1 | GS-FR8 |  | Description: LFC shall allocate Reg-Up, Reg-Down deployments to the Resources based on corresponding QSE telemetered Resource level participation factors. | Accepted | J. Mandavilli J. Adams
52 | Reliant (F.Trefny) | 15 | 3.1.1 | GS-FR9 |  | Description: LFC shall select the correct frequency measurement for control when multiple frequency measurements are available with good quality codes. The criteria for the selection will be defined during the design phase. | Accepted | J. Mandavilli J. Adams
53 | Reliant (F.Trefny) | 15 | 3.1.2 | GS-FR10 |  | Requirement Name: Manual RRSResponsive Reserve Deployment and recall conditions | Accepted | J. Mandavilli J. Adams
54 | Reliant (F.Trefny) | 15 | 3.1.2 | GS-FR10 |  | Description: The ERCOT Operator can initiate Responsive Reserve deployment under the following conditions: … 2. Available Reg-Up is lower than requiredzero | Accepted | J. Mandavilli J. Adams
55 | Reliant (F.Trefny) | 15 | 3.1.2 | GS-FR11 |  | Requirement Name: Automatic RRSResponsive Reserve Deployment and recall conditions | Accepted | J. Mandavilli J. Adams
56 | Reliant (F.Trefny) | 15 | 3.1.2 | GS-FR11 |  | Description: LFC shall automatically deploy Responsive Reserve from Generation and Controllable Load Resources when the system frequency drops below a user defined threshold (e.g. 59.91). LFC shall automatically recall deployed Responsive Reserve from Generation and Controllable Load Resources when the system frequency restores back to a user defined threshold (e.g. 59.97) Note: It is to be noted that these automatic actions from LFC can be complemented by Operator actions to make additional deployments of RRSResponsive Reserve based on the system conditions. | Accepted | J. Mandavilli J. Adams
57 | Brazos Electric (T.Kroskey) | 16 | 3.1.2 | GS-FR11 |  | Description: LFC shall automatically deploy Responsive Reserve from Generation Resources when the system frequency drops below a user defined threshold (e.g. 59.91 Hz). LFC shall automatically recall deployed Responsive Reserve from Generation Resources when the system frequency restores back to a user defined threshold (e.g. 59.97 Hz) | Accepted | J. Mandavilli J. Adams
58 | GP&L (R.Hoeinghaus) | 16 | 3.1.2 | GS-FR11 |  | Description: LFC shall automatically deploy Responsive Reserve from Generation Resources when the system frequency drops below a user defined threshold (e.g. 59.91). LFC shall automatically recall deployed Responsive Reserve from Generation Resources when the system frequency restores back to a user defined threshold (e.g. 59.97) GP&L Comment: • What about the requirement stated in Protocol 6.5.7.6.2.2(3) – “ERCOT shall deploy Responsive Reserve to respond to a frequency deviation when the power requirement to restore frequency to normal (ACE) in 10 minutes exceeds the Reg-Up ramping capability” Please notice the conditional word “when” • What about the requirement stated in Protocol 6.5.7.6.2.2(4) –“ ERCOT may deploy Responsive Reserve in response to NERC Disturbance Control Assistance requirements as specified in the Operating Guides if no additional energy is available to be dispatched from SCED as determined by the Ancillary Services Capacity Monitor.” PLEASE notice the conditional words “if no additional energy is available” | Pending | J. Mandavilli J. Adams
59 | GP&L (R.Hoeinghaus) | 16 | 3.1.2 | GS-FR11 |  | Description: LFC shall automatically deploy Responsive Reserve … … • Protocol 8.1.2.4.2 (1) states “ERCOT shall adjust the Generation Resource’s Base Point for any requested Responsive Reserve energy in the next cycle of SCED as specified in Section 6.5.7.6.2.2, Deployment of Responsive Reserve Service” - Since LFC deploys RRS, LFC recalculates HASL’s & sends to SCED, LFC triggers a SCED with a generation to dispatch that includes RRS, it would seem the RRS value will be double deployed. • Methodology stated in description is not in 6.5.7.6.2.2(2) - would seem that this methodology is in conflict with Protocols 6.5.7.6.2.2(3) and 6.5.7.6.2.2(4) and maybe 8.1.2.4.2(1) - understand that this is what is done today BUT Protocol is supposed to be guiding document | Pending | J. Mandavilli J. Adams
60 | Reliant (F.Trefny) | 15 | 3.1.2 | GS-FR12 |  | Requirement Name: RRSResponsive Reserve Deployment from Load Resources | Accepted | J. Mandavilli J. Adams
61 | Reliant (F.Trefny) | 15 | 3.1.2 | GS-FR12 |  | Responsive Reserve is available to LFC only through portfolio deployment via governors or controlled action from a Controllable Load Resources. and Responsive Reserve from lLoad Resources associated with high set under frequency relays shall be automatically initiated based on the frequency level and relay settings (no action from Operator or LFC is normally needed, although manual trip of Load Resources is possible through operator action). | Pending | J. Mandavilli J. Adams
62 | Brazos Electric (T.Kroskey) | 16 | 3.1.2 | GS-FR12 |  | Description: ERCOT MMS system facilitates deployment of Responsive Reserve through lLoad Resources. LFC shall monitor and display available Responsive Reserve through lLoad Resources. Responsive Reserve available through governor action and Responsive Reserve from lLoad Resources associated with high set under frequency relays shall be automatically initiated based on the frequency level and relay settings (no action from Operator or LFC is needed). | Accepted | J. Mandavilli J. Adams
63 | NRG (D.S.Mai) | 16 | 3.1.2 | GS-FR13 |  | Protocol Reference: Section(s) 6.5.7.6.1 (4), 6.5.7.6.2.2 (3) & (6), 6.5.9.4 | Accepted | J. Mandavilli J. Adams | ERCOT to add text to include these requirements (Note - it may be added in new requirement numbers)
64 | Brazos Electric (T.Kroskey) | 17 | 3.1.2 | GS-FR13 |  | Description: The total Responsive Reserve requirement amount to be deployed to QSEs consists of either of the following: • Amount of MW needed to restore the frequency back to the Responsive Reserve recall threshold minus the amount of available regulation that can be deployed in 10 minutes limited by 500 MW • Operator entered Responsive Reserve MW Whenever the total amount of automatic Responsive Reserve requirement is greater than 500 MW and the same is limited by 500 MW, LFC shall generate an Operator alarm. This alarm maywill assist the Operator to initiate EECP. | Accepted | J. Mandavilli J. Adams
65 | Reliant (F.Trefny) | 17 | 3.1.2 | GS-FR13 |  | Description: The total Responsive Reserve requirement amount to be deployed to QSEs consists of either of the following: … • Operator entered Responsive Reserve MW not to exceed 500 Mw unless the EECP has been initiated. | Accepted | J. Mandavilli J. Adams
66 | Reliant (F.Trefny) | 17 | 3.1.2 | GS-FR14 |  | Requirement Name: RRSResponsive Reserve allocation to QSEs | Accepted | J. Mandavilli J. Adams
67 | Reliant (F.Trefny) | 17 | 3.1.2 | GS-FR14 |  | QSE’s aggregate RRSResponsive Reserve participation factors shall be calculated proportional to the sum of their Generators and Controllable Load Resources telemetered RRSResponsive Reserve schedules respectively. QSE’s aggregate RRSResponsive Reserve deployment limits shall be calculated as the sum of Generators and Controllable Load Resources RRSResponsive Reserve schedules minus the RRSResponsive Reserve deployment through SCED. Each of the above calculations shall exclude the following: • Resources with Reg-Up Hi block telemetry or recall of Reg –Up with Low block telemetry [need similar for Reg – Down] • Resources with a telemetered Resource status ONTEST • Off-line Resource based on real-time data (with open breaker or MW output below LSL) LFC shall allocate RRSResponsive Reserve among QSEs based on respective QSE level RRSResponsive Reserve participation factors while accounting for bound limits. | Pending | J. Mandavilli J. Adams
68 | Reliant (F.Trefny) | 18 | 3.1.2 | GS-FR15 |  | Description: LFC shall issue a control signal every four seconds via ICCP to each QSE providing Responsive Reserve service, if Responsive ReserveRRSResponsive Reserve deployment is active. Deployment instructions to non-Controllable Load Resources will be sent to QSEs by MMS via XML interface. | Accepted | J. Mandavilli J. Adams | Responsive Reserve is repeated two times Needs to be adjusted
69 | Reliant (F.Trefny) | 18 | 3.1.2 | GS-FR16 |  | Description: For performance monitoring and settlements, LFC shall calculate allocation of RRSResponsive Reserve deployments to the Resources, based on the corresponding telemetered Resource level participation factors. | Accepted | J. Mandavilli J. Adams
70 | Brazos Electric (T.Kroskey) | 18 | 3.1.2 | GS-FR16 |  | Description: For performance monitoring and settlements, LFC shall calculate allocation of RRS deployments to the Resources, based on the corresponding QSE telemetered Resource level participation factors. | Accepted | J. Mandavilli J. Adams
71 | Reliant (F.Trefny) | 18 | 3.1.2 | GS-FR17 |  | Requirement Name: Recalculate HASL for RRSResponsive Reserve deployment | Accepted | J. Mandavilli J. Adams
72 | Reliant (F.Trefny) | 18 | 3.1.2 | GS-FR17 |  | Description: LFC shall increase the HASL by the Resource level RRSResponsive Reserve deployment following either manual or automatic deployment of RRSResponsive Reserve. | Accepted | J. Mandavilli J. Adams
73 | Brazos Electric (T.Kroskey) | 18 | 3.1.2 | GS-FR17 |  | Description: LFC shall increaseadjust the HASL and LASL based on the QSE telemetered resource participation facors to account forby the Resource level RRS deployment following either manual or automatic deployment or recall of RRS. | Accepted | J. Mandavilli J. Adams
74 | GP&L (R.Hoeinghaus) | 19 | 3.1.3 | GS-FR19 |  | Description: The ERCOT Operator may manually deploy Non-Spin under the following conditions: • Detection of insufficient capacity for energy dispatch during periodic checking of available capacity for future operations. • Disturbance conditions such as a unit trip, sustained frequency decay or sustained low frequency operations. • SCED not having enough energy available to execute successfully./In each situation, the ERCOT Operator makes the final decision and initiates the deployment of Non-Spin on an all-or-nothing basis. GP&L Comment: “all-or-nothing” has not been decided and we cannot find “all-or-nothing” in the procedure before TAC as referenced in 2.2.1 above The ERCOT Operator may deploy Non-Spin at any time during a selected Settlement Interval. | Accepted | J. Mandavilli J. Adams | ERCOT will delete "all-or-nothing" reference.
75 | Brazos Electric (T.Kroskey) | 18 | 3.1.3 | GS-FR19 |  | Description: The ERCOT Operator may manually deploy Non-Spin Reserve under the following conditions: • Detection of insufficient capacity for energy dispatch during periodic checking of available capacity for future operations. • To recover Responsive Reserve that has been deployed due to Ddisturbance conditions such as a unit trip, sustained frequency decay or sustained low frequency operations or other Emergency Condition. | Accepted | J. Mandavilli J. Adams
76 | Reliant (F.Trefny) | 19 | 3.1.3 | GS-FR19 |  | LFC shall trigger SCED with the Non-Spin deployment flag to deploy Non-Spin energy as required. Non-Spin deployments may be used to replace RRSResponsive Reserve deployed energy and recover RRSResponsive Reserve capacity. This can minimize the prolonged use of Responsive Reserve Energy. | Accepted | J. Mandavilli J. Adams
77 | Brazos Electric (T.Kroskey) | 19 | 3.1.3 | GS-FR19 |  | LFC shall trigger SCED with the Non-Spin deployment flag to deploy Non-Spin energy as required. Non-Spin deployments may be used to replace RRS deployed energy and recover RRS capacity. This can minimize the prolonged use of Responsive Reserve ServiceEnergy. | Accepted | J. Mandavilli J. Adams
78 | GP&L (R.Hoeinghaus) | 20 | 3.1.3 | GS-FR21 |  | Description: Once the Operator has initiated Non-Spin, a Non-Spinning Reserve Service Deployment Status notification shall be sent (once) to each QSE indicating that Non-Spin has been deployed. When Non-Spin is subsequently recalled, another Non-Spinning Reserve Service Deployment Status notification shall be sent to each QSE indicating that Non-Spin is no longer in effect and has been recalled. (Note: The Section 6.5.7.6.2.3 (10) requirement for an individual Non-Spin Dispatch Instruction for each Non-Spin Resource is not necessary.) GP&L Comment: Description would seem to be based on the white papers – understood that this requirement was to be based on the protocols until white papers were agreed to and the appropriate NPRR would be written. | Pending | J. Mandavilli J. Adams
79 | Brazos Electric (T.Kroskey) | 19 | 3.1.3 | GS-FR21 |  | Description: Once the ERCOT Operator has initiated Non-Spin, a Non-Spinning Reserve Service Deployment Status notification shall be sent (once) to each QSE indicating that Non-Spin has been deployed. | Accepted | J. Mandavilli J. Adams
80 | Brazos Electric (T.Kroskey) | 20 | 3.1.3 | GS-FR22 |  | Description: When Non-Spinning Reserve Service is invoked: 1. Generation Ssub-system shall notify each QSE providing Non-Sspinning Rreserve Service by the messaging system. 2. Each QSE with on-line DSR generators providing Non-Spin shall adjust their telemetered Resource Output Schedule by the amount of its Non-Spin award 3. Resource limit calculator shall adjust the HASL of each Resource by the amount of Nnon-Sspin Rreserve scheduled. | Pending | J. Mandavilli J. Adams
81 | Reliant (F.Trefny) | 20 | 3.1.3 | GS-FR22 |  | Description: When Non-Spinning Reserve Service is invoked: … 6. Each QSE with Load Resources providing Non-Spin will interrupt load shut them down within 30 minutes from the deployment | Accepted | J. Mandavilli J. Adams
82 | Reliant (F.Trefny) | 20 | 3.1.3 | GS-FR23 |  | Description: When Non-Spin is first awarded to an On-Line Generating Resource with an Energy Offer Curve, each QSE shall set the value of its telemetered Non-Spinning Reserve Ancillary Service Schedule to the amount of the Non-Spin award for that Resource. … When the Non-Spinning Reserve Service is invoked, LFC shall immediately calculate new value of HASL by replacing the telemetered value of the Non-Spinning Reserve Ancillary Service Schedule with zero for each On-Line Generating Resource with an Energy Offer Curve. | Accepted | J. Mandavilli J. Adams
83 | Brazos Electric (T.Kroskey) | 20 | 3.1.3 | GS-FR23 |  | Description: When Non-Spin is first awarded to an On-Line Generating Resource with an Energy Offer Curve, each QSE shall set the value of its telemetered Non-Spinning Reserve Service Schedule to the amount of the Non-Spin award for that Resource. LFC shall use this term to automatically reduce the value of the corresponding High Ancillary Service Limit = HSL – RegUp – Responsive Reserve – Non-Spinning Reserve in order to reflectreserve Non-Spin capacity reserves. When the Non-Spinning Reserve Service is invoked, LFC shall immediately calculate a new value of HASL by replacing the telemetered value of the Non-Spinning Reserve Service Schedule with zero for each On-Line Generating Resource with an Energy Offer Curve. | Accepted | J. Mandavilli J. Adams
84 | Brazos Electric (T.Kroskey) | 21 | 3.1.3 | GS-FR25 |  | Description: When Non-Spinning Reserve Service is invoked, LFC shall monitor the Resource Status of each Off-Line Generating Resource with a Non-Spin Award. LFC expects that this Off-Line Generating Resource will be on-line as soon as possible but no later than 30 minutes following Non-Spin deployment. This permits SCED to increasedispatch the generation MW level of these units as necessary. | Accepted | J. Mandavilli J. Adams
85 | GP&L (R.Hoeinghaus) | 22 | 3.1.3 | GS-FR27 |  | Description: The ERCOT Operator may manually recall Non-Spin at operator discretion when acceptable capacity reserves are established. Recall of Non-Spin is performed on an all-or-nothing basis. GP&L Comment: “all-or-nothing” has not been decided and we cannot find “all-or-nothing” in the procedure before TAC as referenced in 2.2.1 above | Pending
86 | Brazos Electric (T.Kroskey) | 22 | 3.1.3 | GS-FR27 |  | Description: The ERCOT Operator may manually recall Non-Spin at operator discretion when acceptable capacity reserves are established. Recall of Non-Spin is performed on an all-or-nothing basis. When Non-Spin is recalled, LFC shall: … 5. SCED will calculate new Base Points for these units and they will rampdispatch to their new Base Points at their Normal Ramp Rates. 6. A QSE with a Load Resource that has provided Non-Spin shall ensure that the load energy and Non-Spin capability is restored within three hours from the expiration of the Non-Spin deployment. If it is not, the Non-Spin capability shall be replaced by the QSE on other Generation or Load Resources not previously committed. In addition, when Non-Spin is recalled, a QSE with a Generation Resource that was previously off-line may be taken back off-line at the discretion of the QSE. Also, a QSE with a Load Resource that has provided Non-Spin shall ensure that the load energy and Non-Spin capability is restored within three hours from the expiration of the Non-Spin deployment. If it is not, the Non-Spin capability shall be replaced by the QSE on other Generation or Load Resources not previously committed.(this is already in item 6 above) | Pending
87 | GP&L (R.Hoeinghaus) | 22 | 3.1.3 | GS-FR27 |  | 6. A QSE with a Load Resource that has provided Non-Spin shall ensure that the load energy and Non-Spin capability is restored within three hours from the expiration of the Non-Spin deployment. If it is not, the Non-Spin capability shall be replaced by the QSE on other Generation or Load Resources not previously committed. … Also, a QSE with a Load Resource that has provided Non-Spin shall ensure that the load energy and Non-Spin capability is restored within three hours from the expiration of the Non-Spin deployment. If it is not, the Non-Spin capability shall be replaced by the QSE on other Generation or Load Resources not previously committed. GP&L Comment: The preceding paragraph is word for word (except for the 1st word of “Also” for # 6 above – did you intend this to be this way? | Pending
88 | Reliant (F.Trefny) | 22 | 3.2 | GS-FR28 |  | Description: The Ancillary Services Capacity Monitor shall use the actual Resource information from SCADA (aAncillary sService sSchedules, participation factors, and generatorResource net power telemetryoutput) in determining available Resource capacity to provide Regulation, Responsive Reserve, and Non-Spinning Reserve Services. The Ancillary Services Capacity Monitor shall effectively use the lower of the telemetered HSL for all calculations. If the and the seasonal High Capability Test is less than the telemetered in calculating reserves by rejecting as invalid any telemetered HSL and which is higher then the seasonal test results unless a no text reason explaining why it is higher HSL is provided will generate an alarm to the ERCOT and QSE operators describing such. | Pending
89 | NRG (D.S.Mai) | 22 | 3.2 | GS-FR28 |  | Description: The Ancillary Services Capacity Monitor shall use the actual Resource information from SCADA (ancillary service schedules, participation factors, and generator output and limits) in determining available Resource capacity to provide Regulation, Responsive Reserve, and Non-Spinning Reserve Services. | Pending
90 | Brazos Electric (T.Kroskey) | 23 | 3.2 | GS-FR29 |  | Description: The Ancillary Services Capacity Monitor shall monitor available capacity that can be dispatched through SCED. If the Capacity Monitor determines that there is not enough capacity available, then it shall alarm the ERCOT Operator who may manually deploy Responsive Reserve or Non-Spinning Reserve Service. The ERCOT Operator will receive an alarm if: | Pending
91 | LCRA (G.Graham | 22 | 3.2 | GS-FR30 |  | Description: The Ancillary Services Capacity Monitor shall calculate the following capacity values every 4 seconds based on SCADA telemetry (including telemetered schedules) and deployments: 1. Responsive Reserve Capacity from Generation Resources (Including Units capable of Synchronous Condenser Operations) | Pending
92 | Reliant (F.Trefny) | 23 | 3.2 | GS-FR30 |  | Description: The Ancillary Services Capacity Monitor shall calculate the following capacity values every 4 seconds based on SCADA telemetry (including telemetered schedules) and deployments: … 12 Total ERCOT Generation 13 Total ERCOT Load 14 Total ERCOT Operating Reserve 15 Black Start Capacity 16 Reliability Must Run Capacity 17 Spinning Reserve Capacity 18 Physical Responsive Reserve Capacity from Generation Resources (available capacity based only on physical limits – includes reserves which are not bid into the market) 19 Responsive Reserve service capacity on generators – sum of telemetered reserve capacity from generating units. 20. Responsive Reserve Capacity from Load Resources 21. Total Responsive Reserve Capacity from Generators and Load Resources | Pending
93 | GP&L (R.Hoeinghaus) | 23 | 3.2 | GS-FR30 |  | Description: The Ancillary Services Capacity Monitor shall calculate the following capacity values every 4 seconds based on SCADA telemetry (including telemetered schedules) and deployments: 1. Responsive Reserve Capacity from Generation Resources 2. Responsive Reserve Capacity from Load Resources 3. Non-Spinning Reserve available from On-Line Generation Resources with Energy Offer Curves … 10. Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED 11. Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED GP&L Comment: Protocol 6.5.7.5(1) has a list of 12 (not 11 as shown above) capacity values that are to be calculated. From this Protocol, 6.5.7.5(1)(c) is left out which states “Responsive Reserve Capacity from Controllable Load Resources” shall be calculated as a separate value. Also, this same protocol states that item # 2 above should contain the words “excluding Controllable Load Resources”. Bottom line, item 2 above is broken into 2 separate values per the protocol – not 1 as per the above list. | Pending
94 | Reliant (F.Trefny) | 24 | 3.2 | GS-FR30 |  | The Ancillary Services Capacity Monitor shall generate alarms as appropriate and shall provide Real-Time summaries of market reserve calculations to ERCOT Operators on Generation Subsystem displays. Market Participants can view this information on the MIS Secure Areaare provided this information on ICCP. The Capacity Monitor shall provide updates to QSE operators of these calculations every 4 seconds. Does this use ICCP outputs or MIS?? SCADA design document indicates it is ICCP. | Pending
95 | GP&L (R.Hoeinghaus) | 24 | 3.2 | GS-FR30 |  | The Ancillary Services Capacity Monitor shall generate alarms as appropriate and shall provide Real-Time summaries of market reserve calculations to ERCOT Operators on Generation Subsystem displays. Market Participants can view this information on the MIS Secure Area. The Capacity Monitor shall provide updates of these calculations every 4 seconds. GP&L Comment: Protocol 6.5.7.5 states calculations to be performed & posted every 10 seconds – if system loading is an issue, then the 4 seconds stated above can be backed off to 10 seconds. | Pending
96 | Reliant (F.Trefny) | 24 | 3.2 | GS-FR31 |  | Description: The Ancillary Services Capacity Monitor shall calculate the following every 4 seconds and provide Real-Time summaries to ERCOT: 1.Black Start Capacity 2.Reliability Must Run Capacity 3.Spinning Reserve Capacity 4.Physical Responsive Reserve Capacity from Generation Resources (available capacity based only on physical limits – includes reserves which are not bid into the market) 5.Responsive Reserve service capacity on generators – sum of telemetered reserve capacity from generating units. 6.Responsive Reserve Capacity from Load Resources 7.Total Responsive Reserve Capacity from Generators and Load Resources Why are some of the above different from those above. The intent of the AS Capacity Monitor is to provide ERCOT operators and Market Participants the same data on which to operate the system. | Pending
97 | GP&L (R.Hoeinghaus) | 24 | 3.2 | GS-FR31 |  | GP&L Comment: Don’t see how you get this list for the following capacities from 6.5.7.2(1) which covers calculating limits – not capacities. However, I do see how the list could be developed from the IRO-005-1 NERC requirement. Believe reference to protocol 6.5.7.2(1) should be removed. Description: The Ancillary Services Capacity Monitor shall calculate the following every 4 seconds and provide Real-Time summaries to ERCOT: 1. Black Start Capacity 2. Reliability Must Run Capacity 3. Spinning Reserve Capacity 4. Physical Responsive Reserve Capacity from Generation Resources (available capacity based only on physical limits – includes reserves which are not bid into the market) 5. Responsive Reserve service capacity on generators – sum of telemetered reserve capacity from generating units. 6. Responsive Reserve Capacity from Load Resources 7. Total Responsive Reserve Capacity from Generators and Load Resources | Pending
98 | Reliant (F.Trefny) | 25 | 3.2 | GS-FR32 |  | Description: The Ancillary Services Capacity Monitor shall average the requested amount of Resource-specific regulation over each SCED interval. The Capacity Reserve Monitor shall also average the Resource-specific actual generation from telemetry over each SCED interval and each settlement interval. These calculations will be performed to facilitate performance monitoring and compliance and settlement calculations. | Pending
99 | Brazos Electric (T.Kroskey) | 24 | 3.2 | GS-FR32 |  | Description: The Ancillary Services Capacity Monitor shall average the requested amount of Resource-specific regulation over each SCED interval. The Capacity Reserve Monitor shall also average the Resource-specific actual generation from telemetry over each SCED interval and each settlement interval. These calculations will be performed and results stored in the EMS database to facilitate compliance and settlement calculations. | Pending
100 | Brazos Electric (T.Kroskey) | 24 | 3.2 | GS-FR33 |  | Requirement Name: Expected governor response from Resources … Description: The Ancillary Services Capacity Monitor shall calculate and store in the EMS database one-minute and ten-minute average of the expected generator governor response for Reg-Up and Reg-Down deployments. | Pending
101 | GP&L (R.Hoeinghaus) | 25 | 3.2 | GS-FR33 |  | Description: The Ancillary Services Capacity Monitor shall calculate and store in the EMS database one-minute and ten-minute average of the expected generator governor response for Reg-Up and Reg-Down deployments. GP&L Comment: ● Where are you getting expected generator governor response value for averaging? • If EMS is calculating, would like to see method as a functional requirement • How is deadband handled - Do you have a PDC group recommendation? • What droop are you using – 5% is textbook but in real life there are probably more resources with a 6 to 8% droop than with 5% - Do you have a PDC group recommendation? ● Strike words “for Reg-Up and Reg-Down deployments” & replace with “QSE resources with a resource status of ONREG, ONOSREG, ONRGL, or ONDSRREG | Pending
102 | NRG (D.S.Mai) | 25 | 3.2 | GS-FR34 |  | Protocol Reference: Section(s) 6.5.7.8.3, 8.1.2.4.1, 8.1.2.4.2, 8.1.2.4.3, 8.1.2.4.4 … Description: The Ancillary Services Capacity Monitor shall determine if individual resources are not responding to dispatch instructions, as specified in sections 8.1.2.4.1, 8.1.2.4.2, 8.1.2.4.3, and 8.1.2.4.4 of the Protocols, and shall update a non-responding flag status for each resource. The Capacity Monitor determines whether average error between the instructed generation level and the actual generation over a period of time is greater than a set limit. | Pending
103 | GP&L (R.Hoeinghaus) | 25 | 3.2 | GS-FR34 |  | Protocol Reference: Section(s) 6.5.7.8.3 GP&L Comment: 6.5.7.8(3) … Description: The Ancillary Services Capacity Monitor shall determine if individual resources are not responding to dispatch instructions and shall update a non-responding flag status for each resource. The Capacity Monitor determines whether average error between the instructed generation level and the actual generation over a period of time is greater than a set limit. GP&L Comment: This should also include the governor response value as described under 8.1.2.4.1(1)(a)(iii | Pending
104 | Reliant (F.Trefny) | 25 | 3.2 | GS-FR34 |  | Description: The Ancillary Services Capacity Monitor shall determine if individual resources are not responding to dispatch instructions and shall update a non-responding flag status for each resource. The Capacity Monitor determines whether average error between the instructed generation level and the actual generation over a period of time is greater than a set limit. The Ancillary Services Capacity Monitor shall monitor the High and Low block telemetry on Resources providing regulation and alarm both the ERCOT and QSE operators of bocks that have been in effect for more than 5 minutes. These alarms shall be summarized and archived for review by performance monitoring and compliance. | Pending
105 | NRG (D.S.Mai) | 25 | 3.2 | GS-FR35 |  | Protocol Reference: Section(s) 8.1.2.4.1, 8.1.2.4.2, 8.1.2.4.3, 8.1.2.4.4 … Note: A/S Capacity Monitor needs to calculate Resource Error according to 8.1.2.4.1, 8.1.2.4.2, 8.1.2.4.3, and 8.1.2.4.4. | Pending
106 | GP&L (R.Hoeinghaus) | 26 | 3.2 | GS-FR35 |  | Description: The Ancillary Services Capacity Monitor shall calculate Resource error at a configurable periodicity as follows: • Calculate Generator error as the difference between the generator output and the generator obligations (Base Point plus ancillary service deployments) GP&L Comment: This does not indicate 8.1.2.4.1(1)(a)(iii) (expected governor response) is included (you calculated this element in GS-FR33) • Calculate Load Resource error as the difference between Load Resource deployment MW and the estimated Load Resource response • Calculate estimated Load Resource response based on the Load Resource telemetry, LPC, breaker status GP&L Comment: What about the calculation spelled out in 8.1.2.4.1(1)(b) – do not see it covered here The Capacity Monitor shall calculate QSE portfolio error for generators and Load Resources as sum of corresponding QSE Resource errors GP&L Comment: What about sections 8.1.2.4.2 (RRS) & 8.1.2.4.3 (NSRS) – the above items out of 8.1.2.4.1 are for REG only | Pending
107 | Brazos Electric (T.Kroskey) | 25 | 3.2 | GS-FR35 |  | The Capacity Monitor shall calculate QSE portfolio error for generators and Load Resources as the sum of corresponding QSE Resource errors. | Pending
108 | Reliant (F.Trefny) | 26 | 3.3 | GS-FR36 |  | Description: The Resource Limit Calculator shall calculate for each Resource the HASL, LASL, SURAMP, SDRAMP, HDL, Normal Ramp Rate, Emergency Ramp Rate, and LDL based on QSE’s SCADA telemetry (Reg-Up Ancillary Service sSchedule, Reg-Down Ancillary Service sSchedule, RRSResponsive Reserve Ancillary Service sSchedule, Non-Spin Ancillary Service sSchedule, HSL, and LSL) and Ramp Rate curves. If the System Emergency Flag is set, the Resource Limit Calculator shall replace HSL with HEL when calculating HASL. | Pending
109 | Reliant (F.Trefny) | 26 | 3.4 | GS-FR37 |  | Requirement Name: Regulation and RRSResponsive Reserve Qualification Testing Feature | Pending
110 | Reliant (F.Trefny) | 26 | 3.4 | GS-FR37 |  | Description: The Generation Subsystem shall facilitate qualifications testing for Ancillary Services Resources including: 1. A mechanism for the Operator to enter test parameters for an individual each Resource 2. A mechanism for triggering initiation of the test of that Resource while maintaining continued operation on the remaining Resources at the QSE. 3. Sending control signals to the QSE associated withfor the Resource being tested (via SCADA/ICCP) 4. Collecting Resource response information and calculating one-minute averages of Resource MWs and response rates 5. Presenting Resource response information to the ERCOT Ooperator in both tabular and graphical form | Pending
111 | Brazos Electric (T.Kroskey) | 26 | 3.4 | GS-FR37 |  | Description: The Generation Subsystem shall facilitate qualifications testing for Ancillary Services Resources including: 1. A mechanism for the ERCOT Operator to enter test parameters for each Resource … 5. Presenting Resource response information to the ERCOT Operator in both tabular and graphical form | Pending
112 | Reliant (F.Trefny) | 27 | 3.5 |  |  | The data interfaces with the Generation Subsystem are described in this section under the following categories: … 4. Performance Monitoring and Compliance | Pending
113 | Brazos Electric (T.Kroskey) | 27 | 3.5.1 | GS-FR38 |  | Description: The Generation Subsystem shall validate and use the following inputs from SCADA: (are the DC Tie values from QSEs?) 1. Frequency (multiple values from QSEs and from local instrumentation) 2. Resource Status for Generators and Loads (code) 3. DC Tie injection MW 4. DC Tie status | Pending
114 | LCRA (G.Graham | 26 | 3.5.1 | GS-FR38 |  | Description: The Generation Subsystem shall validate and use the following inputs from SCADA: 6. Generator breaker status – Remember that generation units can often be on-line and operating with one of the 2 Generator Breakers open. Will this cause issues or do you expect the QSE to send you a resultant single signal indicating the breaker status? | Pending
115 | Reliant (F.Trefny) | 27 | 3.5.1 | GS-FR38 |  | Description: The Generation Subsystem shall validate and use the following inputs from Generation Resources (for purposes of this section, Controllable Load Resources shall have the same telemetry at Generation Resources) provided by from SCADA: … 5. Generator net real power (gross & auxiliary and/or netmust be net as calculated by the QSE is necessary) … 15. Generator RRSResponsive Reserve participation factor 16. Generator Reg-Up Ancillary Service sSchedule 17. Generator Reg-Down Ancillary Service sSchedule 18. Generator Responsive Reserve scheduleAncillary Service Schedule 19. Generator Non-Spin scheduleAncillary Service Schedule | Pending
116 | Reliant (F.Trefny) | 28 | 3.5.1 | GS-FR38 |  | The Generation Subsystem shall validate and use the following inputs from Load Resources (for purposes of this section, Controllable Load Resources shall have the same telemetry at Generation Resources) provided by SCADA: 241. Load Resource MW 252. Load Resource relay status 263. Load Resource LPC 274. Load Resource MPC 285. Load Resource High Sustained Limit 296. Load Resource Low Sustained Limit 307. Load Resource High Emergency Limit 318. Load Resource Low Emergency Limit 329. Load Resource Normal Ramp Rate 3310. Load Resource Emergency Ramp Rate 3411. Load Resource Reg-Up participation factor 3512. Load Resource Reg-Down participation factor 3613. Load Resource RRSResponsive Reserve participation factor 3714. Load Resource Reg-Up scheduleAncillary Service Schedule 3815. Load Resource Reg-Down scheduleAncillary Service Schedule 3916. Load Resource Responsive Reserve scheduleAncillary Service Schedule 4017. Load Resource Non-Spin scheduleAncillary Service Schedule 4118. Load Resource Reg-Up inhibit status (temporarily blocked by QSE) 4219. Load Resource Reg-Down inhibit status (temporarily blocked by QSE) 4320. Load Resource DSR Output Schedule (is this possible) | Pending
117 | Reliant (F.Trefny) | 29 | 3.5.1 | GS-FR38 |  | The Generation Subsystem shall validate and use the following inputs from provided by SCADA: 441. RRSQSE total Responsive Reserve deployment amount (manual) 452.RRSQSE total Responsive Reserve deployment amount (automatic) | Pending
118 | GP&L (R.Hoeinghaus) | 28 | 3.5.1 | GS-FR38 |  | Description: The Generation Subsystem shall validate and use the following inputs from SCADA: … 22. Generation Resource DSR schedule GP&L Comment: insert “output” between DSR & Schedule … 44. RRS deployment amount (manual) GP&L Comment: Protocols state RRS Schedule – not RRS deployment amount to be sent – They do not require a distinction between auto & manual amounts 45. RRS deployment amount (automatic) GP&L Comment: Protocols state RRS Schedule – not RRS deployment amount to be sent – They do not require a distinction between auto & manual amounts 46. DSR Load GP&L Comment: Section 6.4.2.5(3)(A) “All power signals for DSR Load must be sent to ERCOT in Real-Time by telemetry; and” | Pending
119 | Reliant (F.Trefny) | 29 | 3.5.1 | GS-FR39 |  | Description: In order to ensure operational security, the Generation Subsystem shall issue the following dispatch instructions: … 3. QSE Responsive Reserve MW requirementdeployement 4. Non-Spinning Reserve Service deployment status (all or none) to all QSEs | Pending
120 | GP&L (R.Hoeinghaus) | 29 | 3.5.1 | GS-FR39 |  | Description: In order to ensure operational security, the Generation Subsystem shall issue the following dispatch instructions: … 4. Non-Spinning Reserve Service deployment status (all or none) to all QSEs GP&L Comment: “all or none” has not been decided and we cannot find “all-or-none” in the procedure before TAC as referenced in 2.2.1 above | Pending
121 | Reliant (F.Trefny) | 29 | 3.5.1 | GS-FR40 |  | Description: The Generation Subsystem shall provide the following Resource Base Point data to be sent to the associated QSEs (via SCADA). Base Point data consist of the following information: … 2. Resource status indicator selecting either Normal or Emergency Base Point [Is this by QSE or by Resource? 3. Resource status indicator providing notice of dispatch above the Resource’s HASL due to RRSResponsive Reserve 4. Resource status indicator to indicate pseudo unit dispatch (MW value is included in the Base Point) I thought we said this was not needed. … This needs to be re-worked according to the white papers as they get approved. | Pending
122 | GP&L (R.Hoeinghaus) | 30 | 3.5.1 | GS-FR40 |  | Description: The Generation Subsystem shall provide the following Resource Base Point data to be sent to the associated QSEs (via SCADA). Base Point data consist of the following information: … 6. Resource status indicator to suspend ramping to Base Point (yes/no) GP&L Comment: Item 6 would seem to be in conflict with FR5 which states that a base point equal to current generation will be sent to stop ramping a resource. Is this a conflict or are you doing both? | Pending
123 | GP&L (R.Hoeinghaus) | 30 | 3.5.1 | GS-FR41 |  | Protocol Reference: Section(s) 6.3.2 (2) GP&L Comment: believe also based on 6.5.9.2 and 6.5.9.4.2 … Description: The Generation Subsystem shall send all Resource node LMPs to QSEs (via SCADA) after they are received from SCED. The Generation Subsystem shall send SCED’s previously-solved Resource node LMPs whenever SCED does not solve. The Generation Subsystem shall not send new Resource node LMPs to SCADA when the System EECP flag is set. GP&L Comment: Section 6.5.9.4.2 states “Intermittent solutions of SCED do not set new LMPs until ERCOT declares that the EECP is no longer needed.” Believe that due to various scenarios, ERCOT could be in EECP and SCED still solving (NOT intermittently). Under these conditions in EECP, LMP’s should be sent to MP’s – last sentence in description needs to reflect 6.5.9.4.2 - not just on condition of EECP. | Pending
124 | Reliant (F.Trefny) | 30 | 3.5.1 | GS-FR41 |  | Description: The Generation Subsystem shall send allfor each QSE’s Resources the no de LMPs for that Resource’s Electrical Bus to QSEs (via SCADA) afteras they are received from SCED. The Generation Subsystem shall send SCED’s previously-solved Resource node LMPs whenever SCED does not solve The Generation Subsystem shall not send new Resource node LMPs to SCADA when the System EECP flag is set. [need to discuss] | Pending
125 | Reliant (F.Trefny) | 30 | 3.5.2 | GS-FR42 |  | Description: The Generation Subsystem shall use the following inputs from MMS (SCED): 1. SCED execution end run time stamp … 4. Scheduled MW for each DC tie ??? 5. Generator RRSResponsive Reserve scheduled MW 6. Load Resource RRSResponsive Reserve scheduled MW … 8. Load Resource Non-Spin scheduled MW Generator Base Point above HASL due to RRSResponsive Reserve deployment (flag) | Pending
126 | NRG (D.S.Mai) | 29 | 3.5.2 | GS-FR42 |  | Description: The Generation Subsystem shall use the following inputs from MMS (SCED): … 8. Load Resource Non-Spin scheduled MW 9. Generator Base Point above HASL due to RRS deployment (flag) 9.10. Generator Base Point above HASL due to pseudo unit deployment (flag) 10.11. Generator Emergency Base Point (flag) 11.12. DSR output not equal to its Base Point (flag) 12.13. Generator exceeded Ramp Rate due to instruction flag 13.14. Pseudo unit deployment MW (single value) | Pending
127 | GP&L (R.Hoeinghaus) | 30 | 3.5.2 | GS-FR42 |  | Description: The Generation Subsystem shall use the following inputs from MMS (SCED): 1. SCED run time stamp 2. Generator Base Points 3. Generator LMPs 4. Scheduled MW for each DC tie 5. Generator RRS scheduled MW 6. Load Resource RRS scheduled MW 7. Generator Non-Spin scheduled MW 8. Load Resource Non-Spin scheduled MW Generator Base Point above HASL due to RRS deployment (flag) 9. Generator Base Point above HASL due to pseudo unit deployment (flag) 10. Generator Emergency Base Point (flag) 11. DSR output not equal to its Base Point (flag) 12. Generator exceeded Ramp Rate due to instruction flag 13. Pseudo unit deployment MW (single value) GP&L Comment: • MMS requirement document “19b1_MMS Req.Spec.ForSCEDandReal-TimeMMSProc.v0.91” lists only 7 outputs to EMS. In the MMS list, # 6 does not really match up with any of the 13 items listed above. In the EMS list above, items 5, 6, 7, 8, 9, 10, & 12 do not show up in the MMS list. The two lists need to be reconciled to be sure nothing is being overlooked. •..What is the definition of the word “scheduled” in items # 6, 7, 8? | Pending
128 | Reliant (F.Trefny) | 31 | 3.5.2 | GS-FR43 |  | Description: The Generation Subsystem shall provide following outputs to MMS (SCED): … 6. Generator net MW … 8. Trigger to start SCED [if a SCED is running when this trigger is set; what happens] … 10. Generator RRSResponsive Reserve schedule [not sure what SCED does with this] 11. Generator Non-Spin schedule [not sure what SCED does with this] … 13. Generator Reg-Up and Reg-Down schedules [not sure what SCED does with this] 14. Generator Normal and Emergency Ramp Rates [not sure what SCED does with this] … 17. QSE aggregated DSR load [Does Generation Subsystem perform alarming for DSRs not following the DSR Load?] [How are these used in SCED for what purpose? 18. DSR ancillary service deployment (“Reg-Up” + RRSResponsive Reserve + “Non-Spin” – “Reg-Down”) … 20. Generator RRSResponsive Reserve Participation Factor … 32. Load Resource RRSResponsive Reserve participation factor 33. RRSResponsive Reserve deployment amount (manual) 34. RRSResponsive Reserve deployment amount (automatic) | Pending
129 | GP&L (R.Hoeinghaus) | 32 | 3.5.2 | GS-FR43 |  | Description: The Generation Subsystem shall provide following outputs to MMS (SCED): … 14. Generator Normal and Emergency Ramp Rates … 20. Generator RRS Participation Factor 21. Generator telemetered normal ramp rate 22. Generator telemetered emergency ramp rate 23. Load Resource MW 24. Load Resource breaker status 25. Load Resource relay status 26. Load Resource Responsive Reserve schedule 27. Load Resource Reg-Up schedule 28. Load Resource Reg-Down schedule 29. Load Resource Non-Spin schedule 30. Load Resource LPC 31. Load Resource MPC 32. Load Resource RRS participation factor 33. RRS deployment amount (manual) 34. RRS deployment amount (automatic) GP&L Comment: MMS requirement document “19b1_MMS Req.Spec.ForSCEDandReal-TimeMMSProc.v0.91does not show item 20 (RRS Participation Factor) or items 23 -32 (all Load Resource Parameters) as inputs into the SCED system. Additionally, cannot tell from list if MMS is expecting both items 14 and 21, 22 (ramp rates) The two lists need to be reconciled to be sure nothing is being overlooked. | Pending
130 | Reliant (F.Trefny) | 32 | 3.5.3 | GS-FR44 |  | Description: The Generation Subsystem shall support ERCOT Operator entry and the associated validation of required data that is outlined in all of these requirements. Operator entry includes but is not limited to the following: Are these the same things as the AS Capacity Monitor calculations; If not, they should be moved to that section. We do not want different numbers being used for ERCOT operators that are not also being provided to QSEs] 1. Limit on difference between the sum of the HASLs and the Total Energy Requirement 2. Limit on difference between the sum of the HSLs and the Total Energy Requirement 3. Frequency limit for Deployment/recall of Responsive Reserve 4. Responsive Reserve deployment MW 5. Deploy/recall Non-Spinning Reserve 6. Test parameters for Resource qualification testing | Pending
131 | GP&L (R.Hoeinghaus) | 32 | 3.5.3 | GS-FR44 |  | Protocol Reference: Section(s) 6.5.7.6.1 (9), 6.5.7.6.2.2 (10), 6.5.7.6.2.3 (1), 6.5.7.6.2.3 (11) … Description: The Generation Subsystem shall support ERCOT Operator entry and the associated validation of required data that is outlined in all of these requirements. Operator entry includes but is not limited to the following: 1. Limit on difference between the sum of the HASLs and the Total Energy Requirement 2. Limit on difference between the sum of the HSLs and the Total Energy Requirement 3. Frequency limit for Deployment/recall of Responsive Reserve 4. Responsive Reserve deployment MW 5. Deploy/recall Non-Spinning Reserve 6. Test parameters for Resource qualification testing GP&L Comment: • Do not see entry for your 1st protocol reference 6.5.7.6.1(9) which provides a frequency threshold & ERCOT issuing instructions to temporarily suspend resource ramping • Do not see entry for your 2nd protocol reference 6.5.7.6.2.2(10) which has to do with a controllable load resource • Items 1, 2 & 3 are not covered by listed protocol references so they must be covered by additional references?? | Pending
132 | Reliant (F.Trefny) | 32 | 3.5.4 | GS-FR45 |  | Description: The Generation Subsystem shall calculate and provide following outputs to Settlements for each applicable interval: 1. Generator Average net MW used in SCED 2. Generator Average Regulation Up and Down MW … 5. Flag to indicate RRSResponsive Reserve deployment … 8. Flag to indicate Generator Up Blocking Limit was active 9. Flag to indicate Generator Down Blocking Limit was active … 11. Average MW output of each Resource (per TWTG settlement calculation) what is TWTG? 12. Average Regulation MW deployed to each generator (per TWAR settlement calculation) What is TWAR? 13. Flag to indicate Emergency declaration occurred happened … 16. Generator current breaker status with transition timestamp This may need the result of a logic equation to determine … 20. Flag to indicate generator exceeded Ramp Rate 21. Flag to indicate frequency went above 60.05 22. Flag to indicate frequency went below 59.95 23. Flag to indicate Generator Up Blocking was active 24. Flag to indicate Generator Down Blocking was active 25. Single pseudo unit Base Point MW | Pending
133 | GP&L (R.Hoeinghaus) | 33 | 3.5.4 | GS-FR45 |  | Description: The Generation Subsystem shall calculate and provide following outputs to Settlements for each applicable interval: … 3. Generator Base Point … 17. Generator Emergency Base Point … 26. Adjusted Aggregated Base point (AABP) 27. Aggregated Emergency Base Point (AEBP) GP&L Comment: • Please explain the difference between # 3 (Generator Base Point) and # 17 (Generator Emergency Base Point) • What is the calculation for # 26 – adjusted aggregated base point • What is the calculation for # 27 – aggregated emergency base point | Pending
134 | Brazos Electric (T.Kroskey) | 31 | 3.5.4 | GS-FR45 |  | Description: The Generation Subsystem shall calculate and provide following outputs to Settlements for each applicable interval: (note that 21-24 are duplicate of 6-9) … 6. Flag to indicate frequency went above 60.05 7. Flag to indicate frequency went below 59.95 8. Flag to indicate Generator Up Blocking was active 9. Flag to indicate Generator Down Blocking was active … 21. Flag to indicate frequency went above 60.05 22. Flag to indicate frequency went below 59.95 23. Flag to indicate Generator Up Blocking was active 24. Flag to indicate Generator Down Blocking was active | Pending
135 | Reliant (F.Trefny) | 33 | 3.5.5 | GS-FR46 |  | Description: For every LFC execution [this seems too much data, I think one a minute is enough], the Generation Subsystem shall calculate or capture and save the following data for Performance Monitoring and Compliance Ppurposes: 1. Resource net MW 2. Resource MVAR 3. Generator expected governor response (MW/.1 hz) 4. Resource Ancillary Service Schedule for Reg-Up 5. Resource Ancillary Service Schedule for Reg-Down 6. Generator HSL 7. Generator LSL 8. Generator high emergency limit 9. Generator low emergency limit 10. Resource breaker status 11. Generator Normal Ramp Rate 12. Generator Emergency Ramp Rate 13.4. Other generator commitments of Ancillary Service capacity 14.5. Resource Regulation Reg-Up MW deployed 15.6. Resource Regulation Reg-Down MW deployed 16.7. Resource RRSResponsive Reserve schedule 17.8. Resource RRSResponsive Reserve MW deployed 18.9. Resource Non-Spin schedule 19.10. Resource Base Point MW 20.11. ACE 21.12. System frequency 22.13. Resource Reg-Up block limit 23.14. Resource Reg-Down block limit 24.15. Resource StatusGenerator on-line/off-line status 25.16. NERC control performance data (including clock-minute, clock-10-minute and clock-hour averages) | Pending
136 | GP&L (R.Hoeinghaus) | 33 | 3.5.5 | GS-FR46 |  | GP&L Comment: Don’t know if agree or disagree with list – Protocol references 6.5.7.6.2.2(10) does not have anything to do with this list & 8.2(2)(b)(i)(A) only has to do with item 25 in the list. Description: For every LFC execution, the Generation Subsystem shall calculate or capture and save the following data for Compliance Purposes: 1. Resource MW 2. Resource MVAR 3. Generator expected governor response (MW/.1 hz) • Expected governor response is used in section 8.1.2.4.1(1)(a)and (b) for compliance BUT the engineering units are mw’s – not mw/.1hz • Please see questions / comments in GS-FR33 on expected governor response (continued in following comment) | Pending
137 | GP&L (R.Hoeinghaus) | 33 | 3.5.5 | GS-FR46 |  | (continuation of previous comment) 4. Resource Ancillary Service Schedule for Reg-Up 5. Resource Ancillary Service Schedule for Reg-Down 6. Generator HSL 7. Generator LSL 8. Generator high emergency limit 9. Generator low emergency limit 10. Resource breaker status 11. Generator Normal Ramp Rate 12. Generator Emergency Ramp Rate 13. Other generator commitments of Ancillary Service capacity 14. Resource Regulation Reg-Up MW deployed 15. Resource Regulation Reg-Down MW deployed 16. Resource RRS schedule 17. Resource RRS MW deployed 18. Resource Non-Spin schedule 19. Resource Base Point MW 20. ACE 21. System frequency 22. Resource Reg-Up block 23. Resource Reg-Down block 24. Generator on-line/off-line status 25. NERC control performance data (including clock-minute, clock-10-minute and clock-hour averages) | Pending
138 | Reliant (F.Trefny) | 39-41 | 6.1 |  |  | Several instances of the following changes: basepointsBase Points Base pPoint basepointBase Point base point | Pending
139 | Brazos Electric (T.Kroskey) | 39 | 6.1 |  |  | Based on the raw ACE the CPS focused control logic, mentioned previously, and determines the amount of Control ACE needed to return back within the dynamic deadband limits. This value is used to determine the total amount of regulation MW to be requested from the participants as follows: … Scheduled Frequency = Nominal frequency of 60 Hz with any time error correction offsets applied Control Ace = ? Control Gain = LFC control gain in effect based on active control region (normal, assist, or emergency). | Pending
140 | Brazos Electric (T.Kroskey) | 39 | 6.1 |  |  | The regulation export(UP?) and import(Down?) bound limits for each QSE and the up and down participation factors for each QSE, are determined by summing the telemetered regulation up and down capacity schedule values, respectively, for each QSE Resource (i.e. unit, CLD-LAAR, etc.) providing regulation, excluding unavailable Resources. Unavailable Resources are defined as any Resources with a telemetered URS or DRS block determined by the QSE (as appropriate based on direction), any Resources with a telemetered Resource status other than ONREG, ONOSREG, ONDSRREG, or ONRGL, or any off-line Resource (open breaker or MW output below LOL). The up and down ramp rates (MW/Min) for each QSE are determined by dividing the export(UP?) and import(DOWN?) bound limits for the QSE by 5 (based on the 5 minute interval). | Pending
141 | Reliant (F.Trefny) | 41-43 | 6.2 |  |  | Several instances of the following changes: RRSResponsive Reserve basepointBase Point basepointsBase Points | Pending
142 | Brazos Electric (T.Kroskey) | 41 | 6.2 |  |  | Based on the real time conditions, an ERCOT system Operator can recall the manual RRS deployment by entering a zero value. | Pending
143 | NRG (D.S.Mai) | 42 | 6.3 |  |  | Off-Line Generation Resource reserved for Non-Spin … • SCED will respond to the changes in Resource Status that are received by telemetry from the QSE. A typical sequence would be from OFFNS to ONOS (with output schedule equal to actual generation until minimum load is reached) and then to ON. … • SCED will execute each time it has detected a Resource Status change for an off-line NSRS deployed Resource. • The Resource must, at a maximumminimum, provide the SCED requested deployment energy immediately afterwithin 30 minutes of the Dispatch Instruction. | Pending
144 | Brazos Electric (T.Kroskey) | 42 | 6.3 |  |  | Off-Line Generation Resource reserved for Non-Spin … • The Resource must, at a maximum, provide the SCED requested deployment energy immediately after the Dispatch Instruction but no later than 30 minutes. | Pending
145 | Brazos Electric (T.Kroskey) | 43 | 6.3 |  |  | On-Line Generation Resource with an Energy Offer Curve … • The QSE will update the Resource parameters in COP and the real-time telemetry accordingly. … Recall of Non-Spin Deployment NRSRNSRS will be dispatched or deployed in this manner for each clock hour until the HRUC capacity monitor expects a near-term sustained capacity margin of greater than 8% of the forecast load demand. | Pending
146 | Brazos Electric (T.Kroskey) | 44 | 6.4 |  |  | The Physical Reserve Capacity values are calculated based on the capacity limits (including AS capacity limits) for the Resources and theretheir current output MW values. | Pending
147 | NRG (D.S.Mai) | 45 | 6.4 |  |  | The alarming for the Total Responsive Reserve Capacity will be unique as it will consist of multiple levels of alarming and display flag settings: • System sets EECP STEP 1 FLAG if the Total of (1) Undeployed Responsive Reserve, and (2) Non-Spin Reserve that has been deployed but has not ramped to its specified output level from Resources is less than 2300 MW • System sets EECP STEP 2 FLAG if Total Undeployed Responsive Reserve from Resources is less than 1800 MW • System sets EECP STEP 3 FLAG if Total Undeployed Responsive Reserve is less than the capacity of the largest on-line generator | Pending
148 | Brazos Electric (T.Kroskey) | 45 | 6.4 |  |  | The alarming for the Total Responsive Reserve Capacity will be unique as it will consist of multiple levels of alarming and display flag settings: • System sets EECP STEP 1 FLAG if Total Responsive Reserve is less than 2300 MW • System sets EECP STEP 2 FLAG if Total Responsive Reserve is less than 1800 MW • System sets EECP STEP 3 FLAG if Total Responsive Reserve is less than the capacity of the largest on-line generator • System sets EECP STEP 4 FLAG if desired regulation can not be met and EECP STEP3 FLAG is set • System sets EECP STEP 5 FLAG if system frequency is less than 59.8 Hz and EECP STEP 3 FLAG is set For each change of state an abnormal alarm will be issued for the new state and a return to normal alarm will be issued for the previous state. (This must be updated for 3 EECP steps) | Pending
149 | Reliant (F.Trefny) | 48 | 6.6 |  |  | Several instances of the following change: basepointBase Point | Pending

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.