## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For Network Security and Stability Analysis, Version 0.90
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | TXU Energy Delivery (L.Westbrook) |  |  |  |  | a.. The software (especially stability analysis) should accommodate user-defined load models. It is not clear that it does. | Accepted | Nodal EMS NA Team | The functional requirement will be updated as follows: 5) Transient. Stability Analysis (TSA) specific data a) Transient impedances b) Control systems and load model definitions (standard and user defined) c) Type of Faults d) Fault locations e) Relay data f) Fault clearing times g) Contingency definitions (e.g. fault duration, outage duration, etc) h) Security criteria (e.g. transient stability index, voltage violations, frequency violation)
2 | TXU Energy Delivery (L.Westbrook) |  |  |  |  | b.. The sizing listed for evaluation of execution time of the CA may be exceeded (e.g., It is likely that there could be more than 30 RAPs on the ERCOT system). | Clarification Provided* | Nodal EMS NA Team | The requirements will be updated to reflect the number of RAPs to be 200 for the purpose of performance testing. However, after DRAP is implemented it is expected that the number of RAP definitions likely be reduced.
3 | Brazos Electric (T.Kroskey) | 6 | 1.2 |  |  | The objective of this requirements specification is to: ● Specify mutually exclusive and collectively exhaustive set of requirements for Network Security and Stability Analysis Subsystem and Stability | Accepted | Nodal EMS NA Team | Comment accepted as-is.
4 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | All Network Security and Stability Analysis requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Process Map that describes the Network Security and Stability applications. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
5 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | This section provides an overview of the Network Security and Stability Analysis subsystem and its major logical components. Detailed functional specifications are given in Section 3. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
6 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  |  | The main task of Contingency Analysis (CA) is to evaluate potential outage conditions within the modeled power system by disconnecting power system devices in the model and solving the resulting model. Flow and voltage violations are evaluated and the severity of the potentialpostulated outage is calculated. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
7 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  |  | Real Time Contingency Analysis (RTCA) shall simulate contingencies for the real-time network and identify all resulting security violations. The MW and KV violations and associated limits,and the constraints, shall be made available to the Transmission Constraint Management (TCM) process, where TransmissionERCOT Operator shall have the capability to deactivate, activate, manually enter, edit, and override the limits of constraints. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
8 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  |  | Also, the security violations shall be posted on the Market Information System (MIS) secure area, for access by mMarket pParticipants. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
9 | CNP | 8 | 2.1 |  |  | Voltage Stability and Transient Stability [Transient Stability is not in the “look-ahead” analysis from Fig. 2-1.]analyses shall be run in a real-time cycle (once every hour) and for look-ahead studies. As a result of the analysis, MW and KV “generic” constraints on transmission and resources induced by voltage and transient stability are determined. | Accepted | Nodal EMS NA Team | The TSA block for look-ahead analysis will be added to Fig 2-1
10 | Brazos Electric (T.Kroskey) | 9 | 2.1 |  |  | The real -time Stability Analysis shall be consistent with … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
11 | Brazos Electric (T.Kroskey) | 9 | 2.1.1 |  |  | Information about all base case and contingency violations is passed to the Transmission Constraint Management (TCM) function for display. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
12 | TXU (B.Spangler) | 9 | 2.1.1 |  |  | Information about all base case and contingency violations is passed to the Transmission Constraint Management function for display. It shall be possible for the user to approve any of these constraints for use in Security Constrained Economic Dispatch (SCED), in which case a function of NSSA shall prepare model related inputs for SCED (shift factors and limits), and thus enable SCED to re-dispatch generation to relieve the overloads. {TXU Comments: 1) Is the decision regarding the classification of the constraint as competitive or non-competitive for SCED purposes made in the MMS or in EMS. If in MMS, where is this described in the SCED MMS Business Requirements? 2) The SCED Business Requirements documentation allows SCED to be initiated by an external process. Is this EMS process the only external initiator for SCED? If SCED is externally initiated by a process other than as described here, how are the shift factors and limits determined for the externally initiated SCED?} | Clarification Provided | Nodal EMS NA Team | 1. TCM does not classify constraints as competitive or non-competitive, and the decision is not made in EMS. 2. The triggering of SCED in response to an event identified in EMS will be clarified in the conceptual design. All shift factors and limits for SCED come from TCM.
13 | TXU (B.Spangler) | 9 | 2.1.1 |  |  | A function called Dynamic Remedial Action Plan (DRAP) Calculator will execute in conjunction with NSSA to determine for each contingency with security violations if there is a generation re-dispatch within the time frame of one SCED cycle to resolve security violations {TXU Comment: 1 SCED cycle i.e. 5 mins seems overly restrictive if the security violation is against the Emergency (2-hr) rating. The intent of the Nodal Protocols is for ERCOT to allow the market to resolve reliability or security issues to the greatest extent possible before executing a command and control solution. While a solution in 2 hours may be excessive, why not consider a solution within 1 hour when addressing the correction of the emergency rating limit?}. | Clarification Provided | Nodal EMS NA Team | Once above Emergency Rating, the available time for violation resolution can be anywhere between 15 min and 2 hours. It is not certain how much time over 15 min is remaining to avoid thermal overload and ensure reliability. The 5 min time is chosen to accommodate real time sequence execution and system response to restore the reliability.
14 | Brazos Electric (T.Kroskey) | 9 | 2.1.1 |  |  | … concept widely used at ERCOT called Remedial Action Plan. (RAP). ... | Accepted | Nodal EMS NA Team | Comment accepted as-is.
15 | TXU (B.Spangler) | 9 | 2.1.1 |  |  | Handling of violations depends on whether the violations are already detected in the real-time system, or if they are anticipated due to contingency simulation. In the latter case, further considerations are the magnitude of the violation, and whether a remedial action plan specific to the contingency condition, called Dynamic RAP, is available. When Dynamic RAP is available, the user may elect to forgo a SCED pre-emptive action, {TXU edit} by not activating the constraint, in favor of a remedial action that would ensue after the contingency occurs. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
16 | Brazos Electric (T.Kroskey) | 9 | 2.1.1 |  |  | … information on violation context (base case or a contingency) … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
17 | Brazos Electric (T.Kroskey) | 9 | 2.1.1 |  |  | As illustrated on Fig. 2-2 (a), Contingency Analysis without SPS and without RAP shall report all security violations of Emergency limit and transfer these violations as with a high priority status to TCM. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
18 | Brazos Electric (T.Kroskey) | 10 | 2.1.1 |  |  | ... transmission element with 15-minute violations, along with the corresponding 15-minute ratings shall be passed to SCED for resolution. A single run of SCED calculates a preventive action (by re-dispatching of generation units) that will lower the flow on the reported transmission elements to the level at least below the 15-minute rating. In subsequent runs of NSSA, a remedial action assessment is performed to check whether DRAP could lower the flows below the Emergency limit. The points in the range between the 15-minute rating and Emergency Rating ... | Accepted | Nodal EMS NA Team | Comment accepted as-is.
19 | Brazos Electric (T.Kroskey) | 10 | 2.1.1 |  |  | Violations of Normal limits under contingency conditions that are below Emergency limit shall be displayed in CA and TCM, but neither preventive nor corrective action is expected, because it is assumed that a suitable solution will be found by the TransmissionERCOT Operator within the 2-hour time frame, if the corresponding outage indeed occurred. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
20 | Brazos Electric (T.Kroskey) | 11 | 2.1.1 |  |  | … operational treatment of the Emergency and 15-minute violations … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
21 | Brazos Electric (T.Kroskey) | 12 | 2.1.1 |  |  | … The CA function does not model the action of RAP by default, but it does check for the conditions that would activate RAP, and reports on all the activated RAP triggers. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
22 | Brazos Electric (T.Kroskey) | 12 | 2.1.1 |  |  | ... along with 15-minute rating, are passed to SCED for resolution of the violation. SCED calculates a preventive action (by re-dispatching of generation units) that attempts to lower the flow on the reported transmission lines to the level at least below the 15-minute limits. ... ... The shift factors for DRAP calculation need to reflect the effect of the RAP. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
23 | Brazos Electric (T.Kroskey) | 13 | 2.1.1 |  |  | ... Figure 2-2 (d)) illustrates … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
24 | CNP (E.John) | 15 | 2.2.1 | Table 2-1 |  | EMS Data Models: 1. Contingency Analysis definitions including: ... b. Breaker Outages c. Common Outages (i.e. several breaker and/or equipment outages for a common area that can be grouped as one equipment or facility outage) d. Load Rollover [Is ERCOT going to start studying breaker and bus contingencies along with an increased number of tower contingencies?] | Clarification Provided* | Nodal EMS NA Team | Change item to: b) Breaker Open/Close c) Common Outages Comment: No change in ERCOT philosophy related to contingency definitions is anticipated, and any changes will require protocol or guides revision approved by market participants. This requirement deals only with the functional requirements of the software.
25 | Brazos Electric (T.Kroskey) | 15 | 2.2.1 | Table 2-1 |  | EMS Data Models: 5) Transient. Stability Analysis (TSA) specific data | Accepted | Nodal EMS NA Team | Comment accepted as-is.
26 | Brazos Electric (T.Kroskey) | 15 | 2.2.1 | Table 2-1 |  | State Estimator: 1) Base case solution with all breaker/switch statuses, transmission line flows (MW, MVARvar), generation (MW, MVARvar), loads (MW, MVARvar), bus voltages (KV), transformer tap positions, and equipment ratings (including dynamic ratings where applicable). | Accepted | Nodal EMS NA Team | Comment accepted as-is.
27 | GP&L (R.Hoeinghaus) | 16 | 2.2.2 | Table 2-2 |  | TCM short term history: List of constraints with their actual values, flags (i.e. active, under review, retained, inaccurate, acknowledge), time of creations, and shift factors. GP&L Comment: “Maximum Shadow Price corresponding to each constraint” is in the list of inputs needed from the EMS TCM in the SCED Business Requirements Document (19b1_MMSReq.Spec.ForSCEDandReal-TimeMMSProc.v0.91). Microsoft Word search cannot find the word “shadow” in this document nor is shadow price in the above TCM output list. SCED list & this list need to be reconcilled to be sure nothing is being overlooked. | Pending | Nodal EMS NA Team | This is an item for Punch List. Further discussions required.
28 | Brazos Electric (T.Kroskey) | 16 | 2.2.2 | Table 2-2 |  | Power Flow (PF) output data: 1) Real (MW) and reactive (MVARvar) flow … 3) MW and MVARvar flow through …. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
29 | Brazos Electric (T.Kroskey) | 16 | 2.2.2 | Table 2-2 |  | VSA output data … 2) Other Results of the study a) Bus data (Voltage, Angle, Load (MW & MVAR), Generation (MW & MVAR), Shunt) | Accepted | Nodal EMS NA Team | Comment accepted as-is.
30 | CNP | 16 | 2.2.2 | Table 2-2 |  | VSA output data: 2. Other Results of the study … h. Base case loading and critical contingency case loading | Clarification Provided* | Nodal EMS NA Team | The comment accepted and the formulation is rephrased to reflect the comment as shown below. 2) Other Results of the study (base case and contingency at the critical point) a) Bus data (Voltage, Angle, Load (MW&MVAR), Generation (MW&MVAR), Shunt) b) Generator data (MW & MVAR ) c) LTC tap data (tap position) d) Tap Changer/Phase Shifter data (position and angle) e) Switched Shunt data (values) f) Economic Dispatch Results (MW & MVAR). 3) P-V curves for selected busses
31 | CNP | 16 | 2.2.2 | Table 2-2 |  | TSA output data: Generic MW constraints Critical Clearing time, generator phase angle curves, contingency severity rank | Clarification Provided* | Nodal EMS NA Team | The TSA output will be used to produce "generic constraints" which will be verified by business process. 1. Generic Constraint: The term and the requirement come from the protocol. Generic constraints are resource and transmission MW limits resulting from VSA and TSA studies. (This definition will be inserted into the text, after Fig 2-1 instead of "As a result of the analysis, MW and KV “generic” constraints on transmission and resources induced by voltage and transient stability are determined. ") 2. All these are valid outputs from TSA and can be made available to an analyst, however these outputs are not required by any other subsystem.
32 | TXU (B.Spangler) | 17 | 3 |  |  | {TXU Comment: All references to Section 3.19, Constraint Competitiveness Tests, are inappropriate for inclusion within the functional requirements for the real-time specification for Network Security and Stability Analysis and should be removed from this document. If needed, they should be placed in the CCT Business requirements documentation. The Section 3.19 analysis is intended to be off-line analysis that requires an operator or user decision before such results are used in any application. To include requirements related to the CCT in this documentation is confusing and inappropriate.} | Accepted | Nodal EMS NA Team | All references to 3.19 and protocol mapping will be removed.
33 | Brazos Electric (T.Kroskey) | 17 | 3 | SA-FR1 |  | … main requirements for Power Flow (PF), which is expected … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
34 | TXU (B.Spangler) | 18 | 3 | SA-FR2 |  | {TXU Comment: Remove the 3.19 reference and any specific sub-requirement identified below that applies solely to the reference.} | Accepted | Nodal EMS NA Team | All references to 3.19 and protocol mapping will be removed.
35 | Brazos Electric (T.Kroskey) | 18 | 3 | SA-FR2 |  | … main requirements for Voltage Stability Analysis (VSA), which is expected … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
36 | CNP (E.John) | 18 | 3 | SA-FR2 |  | VSA shall automatically apply a series of step increases to user selectable: system load, area load, zone loads and bus loads[VSA should be capable of performing Generation scaling studies as well?] to a selected base case and, for each step, shall calculate the resulting bus voltages. The increase shall be carried out until at least one of the bus voltages collapses. The point of collapse in terms of the variable that changes shall be noted and reported on appropriate displays, as well as the collapsed bus, and value of voltage at the collapse point. These calculations shall be performed for the base case and for each harmful contingency. | Clarification Provided* | Nodal EMS NA Team | VSA shall automatically apply a series of load and generation step increases according to user defined scenarios, e.g. system load, area load, zone loads, bus loads, and generation step changes.
37 | Brazos Electric (T.Kroskey) | 18 | 3 | SA-FR2 |  | 1. Generating unit voltages/MVARars ... 4. Synchronous condenser voltage/MVARvar | Accepted | Nodal EMS NA Team | Comment accepted as-is.
38 | TXU (B.Spangler) | 19 | 3 | SA-FR3 |  | {TXU Comment: Remove the 3.19 reference and any specific sub-requirement identified below that applies solely to the reference.} | Accepted | Nodal EMS NA Team | All references to 3.19 and protocol mapping will be removed.
39 | Brazos Electric (T.Kroskey) | 19 | 3 | SA-FR3 |  | … main requirements for Transient Stability Analysis (TSA), which is expected … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
40 | Brazos Electric (T.Kroskey) | 19 | 3 | SA-FR3 |  | … The TransmissionERCOT Operator should also be able to designate one or more specific contingencies for full processing. … intervention of a TransmissionERCOT Operator, e.g., to arm/disarm … …The TransmissionERCOT Operator shall be able to pause and resume … In addition, the TransmissionERCOT Operator shall be able to display … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
41 | Brazos Electric (T.Kroskey) | 20 | 3 | SA-FR4 |  | Ranking shall be determined by calculation of severity indices derived from the following categories of contingency violations or base case deviations: 1) Branch flow (MW,. Amps, MVARvar) limit violations. 2) Interface flow (MW,. Amps, MVARvar) limit violations. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
42 | Brazos Electric (T.Kroskey) | 22 | 3 | SA-FR6 |  | It shall be possible for the Operator to start VSA / TSA on demand manually. | Accepted | Nodal EMS NA Team | Will be updated to read "for the ERCOT Operator"
43 | TXU (B.Spangler) | 22 | 3 | SA-FR7 |  | {TXU Comment: Remove the 3.19 reference and any specific sub-requirement identified below that applies solely to the reference.} | Accepted | Nodal EMS NA Team | All references to 3.19 and protocol mapping will be removed.
44 | TXU (B.Spangler) | 23 | 3 | SA-FR7 |  | There shall be an option to switch to the distributed load bus reference from a single bus reference during shift-factor calculation. {TXU Comment: This sub-requirement appears to be aimed at meeting the Section 3.19 provisions related to the ECI calculation. If this is incorrect please clarify the need for this requirement. If this is correct, TXU proposes that this requirement is inappropriate for this Business Requirement and this paragraph should be deleted from this document. The Section 3.19 analysis is intended to be off-line analysis that requires an operator or user decision before such results are used in any application. In any event, the Section 3.19 needs should be addressed separately from the need to generate the appropriate collection of shift factors to support the real time SCED functions.} | Clarification Provided* | Nodal EMS NA Team | Distributed slack bus does not refer to Section 3.19; the reference to 3.19 will be removed. Distributed slack bus is numerical method of more accurately computing shift factors than a single slack bus method.
45 | Brazos Electric (T.Kroskey) | 23 | 3 | SA-FR8 |  | 5. A Triggering Condition may be: ... b. Flow on a piece of branch equipment exceeds a specified percentage of the current rating ... ... d. The aggregated sum of the flows on a set of branches exceeds the sum of each of the branch limits adjusted by thea percentage | Accepted | Nodal EMS NA Team | Comment accepted as-is.
46 | TXU (B.Spangler) | 24 | 3 | SA-FR9 |  | {TXU Comment: Remove the SA-FR9 from this documentation.} Description: During the simulation of a contingency involving generator outage, the loss of the MW generating capacity shall be replaced by other units based on participation factors. These participation factors of the other units shall be re-calculated (formulas will be provided by ERCOT later at the design stage) and made available to downstream market applications | Clarification Provided* | Nodal EMS NA Team | The reference to 3.19 was erroneous. However, the SA-FR9 should remain in the requirement document. The new reference will be provided.
47 | TXU (B.Spangler) | 25 | 3 | SA-FR11 |  | {TXU Comment: Remove SA-FR11 from this documentation.} Description: The MVA limits of the real time constraints on EMS side shall be converted into MW limit to be used by SCED. | Clarification Provided* | Nodal EMS NA Team | The reference to 3.19 was erroneous. However, the SA-FR11 should remain in the requirement document. The new reference is provided.
48 | TXU (B.Spangler) | 26 | 3 | SA-FR14 |  | {TXU Comment: Remove the 3.19 reference and any specific sub-requirement identified below that applies solely to the reference.} | Accepted | Nodal EMS NA Team | All references to 3.19 and protocol mapping will be removed.
49 | Brazos Electric (T.Kroskey) | 26 | 3 | SA-FR14 |  | 3) It shall also be possible … c) Current load (sum of all generations minus the tie-line flows … | Accepted | Nodal EMS NA Team | Comment accepted as-is.
50 | CNP | 26 | 3 | SA-FR15 |  | Description: There will be certain bus mismatches as part of the SE solution available for Contingency Analysis. Since these SE results are used as the base case for implementing the contingencies, there will be inaccuracies in the Contingency Analysis solution. To eliminate or minimize the difference between estimated bus injections from SE and Contingency Analysis base case power flow, the bus mismatches from SE shall be used as pseudo injections at the corresponding bus. ERCOT Engineer shall have capability to manually enable or disable this feature in real time (e.g. a check box in SE configurable parameter list) [This requirement appears to be propagating a known error in zero-injection bus modeling or SE solution algorithm. Zero injection buses should never have significant mismatches that need to be propagated. If there are issues with modeling zero injection measurements, those should be addressed directly.] | Clarification Provided | Nodal EMS NA Team | 1. This is not referring to zero-injections 2. The mismatches are the inherent product of SE calculation and telemetry errors.
51 | TXU (B.Spangler) | 27 | 3 | SA-FR15 |  | ... ERCOT Engineer shall have capability to manually enable or disable this feature in real time (e.g. a check box in SE configurable parameter list) {TXU Comment: This operator action enable/disable should be captured, recorded and posted to MIS.} | Accepted | Nodal EMS NA Team | Make the change as per the comment. "This operator action enable/disable shall be captured, recorded and posted to MIS"
52 | TXU (B.Spangler) | 28 | 3 | SA-FR17 |  | Description: The following shall be features related to displays within TCM: … ... {TXU Comment: Will the information described in the above be captured, recorded and made available to the Market Praticipants?} | Clarification Provided* | Nodal EMS NA Team | The FR-18 will be modified to provide the details of MIS posting (the output type data from FR-17)
53 | Brazos Electric (T.Kroskey) | 27 | 3 | SA-FR17 |  | Description: The following shall be features related to displays within TCM: 1. Provide the Ooperator the ability to manually enter constraints based on offline studies. ... 3. Provide ... Ooperator ... a. Flag the constraints ... iv. Inaccurate; determined as inaccurate by the Ooperator v. Acknowledge; Constraints less likely to be activated by the Ooperator | Accepted | Nodal EMS NA Team | Will be updated to read "the ERCOT Operator"
54 | Brazos Electric (T.Kroskey) | 27 | 3 | SA-FR17 |  | Description: ... 3. Provide capability to the Ooperator the ability to do and display the following: | Accepted | Nodal EMS NA Team | Will be updated to read "the ERCOT Operator"
55 | Brazos Electric (T.Kroskey) | 27 | 3 | SA-FR17 |  | 8. …. in a contingency conditioin …. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
56 | CNP (E.John) | 28 | 3 | SA-FR21 |  | These repetitions shall be continued up to a configurable level initially set to 3.[Some configurable amount of acceptable load shed should also be arequirement depending how you define cascade. If a small amount of load is shed by removing overloaded equipment with no further security violations, then the contingency should not be classified as cascading.] | Clarification Provided* | Nodal EMS NA Team | 1. Add to FR21 a note: "ERCOT is requesting a vendor to provide a method for identifying cascading contingencies that will support NERC's IROL requirement. The details will be worked out during the design phase." 2. Also, add to FR-21: "Cascading contingencies identification shall be a configurable feature, activated on demand due to heavy calculations." 3. Change the reference from IRO 002-0 to IRO-004, IRO-0005.
57 | Brazos Electric (T.Kroskey) | 30 | 3 | SA-FR22 |  | Input for DRAP shall include: 1) State Estimator solution: ... e. Generators statuses | Accepted | Nodal EMS NA Team | Comment accepted as-is.
58 | Brazos Electric (T.Kroskey) | 30 | 3 | SA-FR23 |  | … contingencies and power flow cases. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
59 | CNP (E.John) | 31 | 4.1 | SA-SR3 |  | Description: A complete run of Contingency Analysis shall not exceed 1 minute for the ERCOT network model assuming the following sizing: … ● Load Rollovers -- 30.[This value is too small. CNP alone has more than 100 automatic load rollover combinations.] | Clarification Provided* | Nodal EMS NA Team | Will be updated to real "Load Rollovers -- 500"
60 | CNP (E.John) | 31 | 4.1 | SA-SR3 |  | TSA performance requirement is missing in the document (Additional item that requires discussion, but not directly related to any TPTF comments) | Clarification Provided* | Nodal EMS NA Team | Proposal: TSA shall complete all calculations within 25 min for ERCOT system with 100 contingencies

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.