## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For SCADA, Version 0.90
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | Reliant (F.Trefny) | 3 |  | Table of Contents |  | 6. 2 TDSPTSP Data Exchange | Accepted | F.Kendall B. Blevins | All references to TDSP have been changed to TSP throughout the specification.
2 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | All SCADA requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Functional Diagram that describes SCADA. | Accepted | F.Kendall B. Blevins
3 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | Supervisory Control and Data Acquisition (SCADA) is a sub-system of the Energy mManagement System (EMS). … | Accepted | F.Kendall B. Blevins
4 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | ... It consists of several subsystems which transfer, display and control data between the ERCOT memberMarket Participant systems and ERCOT in accordance with ERCOT nodal protocols, PUCT rules and NERC standards. … | Accepted | F.Kendall B. Blevins
5 | Reliant (F.Trefny) | 8 | 2 |  |  | …PUCT rules and NERCand NERC standards. … | Accepted | F.Kendall B. Blevins
6 | Reliant (F.Trefny) | 8 | 2 |  |  | SCADA data will be used as inputs to ERCOT operator displays of SCADA data including one-line graphical displays of all SCADA data and summary displays as required, the State Estimator application, Alarming application, Load Frequency Control, Security Constrained Economic Dispatch, the Dynamic Ratings Subsystem, Network Security Analysis, and Reliability Unit Commitment (RUC). | Accepted | F.Kendall B. Blevins
7 | NRG (D.S.Mai) | 8 | 2 |  |  | SCADA data will be used as inputs to the State Estimator application, Alarming application, Load Frequency Control, Security Constrained Economic Dispatch, the Dynamic Ratings Subsystem, Network Security Analysis, Load Forecasting, and Reliability Unit Commitment (RUC). | Accepted | F.Kendall B. Blevins
8 | Reliant (F.Trefny) | 8 | 2 |  |  | All future telemetry for both SCADA inputs and outputs must be provided from and to QSEs and TSPs using ICCP. ERCOT currently monitors approximately 20,000 analog measurements, and 28,000 status measurements. It is expected that compliance with nodal protocols will require the expansion of SCADA telemetered points to over 200,000 analog measurements and 160,000 status measurements. This seems unrealistic. Does ERCOT have any studies to come up with this size? | Clarification Provided | F.Kendall B. Blevins | The quantities estimated for SCADA system capacity was determined through an analysis of the current network model, and the potential increase due to the Nodal market. A large increase in digital points is because of the potential number of switches required to be modeled. Protocol section 3.10.7.1.3 Transmission Breakers and Switches. The objective of the analysis was to err on the high side. The quantities included in this specification are intended to ensure that the SCADA system is adequately sized for present and future requirements.
9 | Reliant (F.Trefny) | 8 | 2 |  |  | ERCOT currently sends to QSEs approximately 700 analog values using SCADA. | Accepted | F.Kendall B. Blevins
10 | Reliant (F.Trefny) | 8 | 2 |  |  | This number will increase to approximately 6900 analog values, after implementing the zonal market change to send dynamic ratings to the market participants, before Texas Nodal ?? is this a requirement to send to TSPs or QSEs?. | Clarification Provided | F.Kendall B. Blevins | There is a project in Zonal to have ERCOT calculate limits based on TSP dynamic rating information. The limits are stored in the real-time database and made available to the TSPs via ICCP. Additionally analogs are expected to increase to QSEs so the term market participants is used to account for additional analogs sent to both TSPs and QSEs.
11 | Reliant (F.Trefny) | 8 | 2 |  |  | With Texas Nodal, ERCOT will initially be sending approximately 7900 analog values. Does ERCOT have any studies to come up with this size? | Clarification Provided | F.Kendall B. Blevins | See response to S.No. 8.
12 | Reliant (F.Trefny) | 8 | 2.1 |  |  | This document/provides information to assist the SCADA provider in understanding the requirements for SCADA and is intended to supplement the Nodal Protocols. In case of conflict, the protocols govern. The requirements in scope for this document include: ● TSP input data (including breaker status, switch status, line flows, transformer taps, transformer flows, dynamic ratings... | Accepted | F.Kendall B. Blevins
13 | Reliant (F.Trefny) | 8 | 2.1 |  |  | ● TSP input data ... dynamic ratings along with temperature and weather zone information, Block Load Transfer data) and associated quality codes for each input. ( does ICCP specifications provide for a convention on flow direction? Is + flow into a bus and – flow out of a bus? Are all QSEs and TSPs ICCP communications the same? Should this specification require such?? | Clarification Provided | F.Kendall B. Blevins | Under Zonal there is a convention for flow direction (1) MW or VAR flow out of the bus and into the line is considered to be positive (+) flow. (2) MW or VAR flow into the bus and out of the line is considered to be negative (-) flow. This SCADA requirements specification does not address a power flow direction convention. SCADA will acquire and store in the real-time database values following any desired convention. Similar to Zonal, future documents, such as the Operating Guides Section 1and Section 8 Attachment 8A, NERC Data Dictionary for Electric System Security Data, etc., are expected to establish all conventions needed.
14 | Reliant (F.Trefny) | 8 | 2.1 |  |  | This document/provides information to assist the SCADA provider in understanding the requirements for SCADA and is intended to supplement the Nodal Protocols. In case of conflict, the protocols govern. The requirements in scope for this document include: . . . ● QSE input data to LFC and other applications (including Resource Status) and associated quality codes of each data element. ● ERCOT data override capabilityManual Replacement with ERCOT operator entries of data and appropriate setting of quality codes. (continued in following comment) | Accepted | F.Kendall B. Blevins
15 | Reliant (F.Trefny) | 8 | 2.1 |  |  | (continued from previous comment) ● Outputs to QSEs (outputs from LFC). ● Alarming including status change detection, high and low limit monitoring, return to normal, and message categorization to facilitate routing of alarms to assignable work functions. Does ERCOT alarm on MVA or MW? You may not want to do both so that you can reduce the number of alarms. [continued in following comment] | Clarification Provided | F.Kendall B. Blevins | Agree that ERCOT will need to alarm on MW and other flow limits. It is expected to be configured using the high and low limit alarming feature.
16 | Reliant (F.Trefny) | 8 | 2.1 |  |  | (continued from previous comment) ● Summary displays of all data elements for each defined quality code showing the name of the SCADA point and a time and date stamp when the data element obtained the quality code. ● Stale data detection as established by ERCOT SCADA system loss of communication from a Market Participant ● Stale data detection as may be provided by a Market Participant to ERCOT indicating the Market Participant loss of communication with its field equipment. ● Database modificationsmodifications?? | Accepted | F.Kendall B. Blevins | Assign to Punch list. It is expected that stale data information will be valuable information and should be supported. An ICCP reference to better define Stale Data Detection functionality needs to be developed so that this functionality is correctly implemented. ERCOT is undertaking an effort to clarify and standardize the semantics of ICCP quality codes and their mapping from the Market Participant's system, the ICCP message, and into the ERCOT EMS. Once completed all requirements referencing quality codes will be updated to conform to the quality code scheme and be self consistent
17 | Reliant (F.Trefny) | 9 | 2.2.1 |  |  | As shown in Figure 1, the SCADA ICCP communication function will be provided by four ICCP servers at each of ERCOT’s two control centers. One server pair will provide ICCP communication with TSPs while the other pair will provide ICCP communication with QSEs. Each server pair provides redundancy for failover functions to meet the minimum failover time requirements of the protocols. Is the failover time performance specified in this document to meet protocol requirements? | Accepted | F.Kendall B. Blevins | The description of the hardware configuration is provided for understanding and not intended to specifically site failover performance requirements. See SCD-FR15 and protocol clause 3.10.7.4 (4)(a) for the failover performance requirement.
18 | Reliant (F.Trefny) | 9 | 2.2.1 |  |  | Two Time Receivers are included in the configuration at each ERCOT control center to provide Frequency and Time Error values to applications. SCADA will provide functionality to read all four Time Receivers and place the frequency and time error values with appropriate quality codes in the real-time database. | Accepted | F.Kendall B. Blevins
19 | Reliant (F.Trefny) | 10 | 2.2.2 |  |  | The SCADA application will receive both status and analog data and associated Market Participant quality codes via ICCP, ERCOT operator manually entered data, and data from external processes. For the purposes of this document, communication services are considered as part of SCADA. When an analog measurement is received; SCADA will check data against reasonability limits, check time receipt for identification of stale data, check measurements against limits, check data for Market Participant quality codes, send alarms and notices to ERCOT operators, summarize data elements for display by associated quality code, and save data into the real-time database for use by other applications. When a status measurement is received, SCADA checks the new state against the previous state, and alarms operators if a status change is noted; SCADA also supports basic calculations | Accepted | F.Kendall B. Blevins
20 | Reliant (F.Trefny) | 12 | 3.1 | SCD-FR16 |  | Description: Telemetered data shall be collected from the computer systems of Market Pparticipants utilities connected to the ERCOT WAN. These systems use the IEC 870-6-503 TASE.2 protocol (ICCP). | Accepted | F.Kendall B. Blevins
21 | Reliant (F.Trefny) | 12 | 3.1 | SCD-FR16 |  | In addition to telemetered data, the SCADA system shall support the following data: 1. Non-telemetered data entered by the user including scheduled data from entities?? without computer systems.????? What protocol requires this? Is this a security problem? | Clarification Provided* | F.Kendall B. Blevins | This clause will be changed to simply require that the SCADA system be capable of handling manually entered data and other non-telemetered data. Protocol 6.5.7.1.5 Topology Consistency Analyzer states ERCOT may override SCADA telemetry as required to correct erroneous breaker and switch status before that information is processed by the Network Security Analysis for the next SCED interval.
22 | Reliant (F.Trefny) | 12 | 3.1 | SCD-FR16 |  | 2. Calculated data generated by programs that periodically and aperiodicallyperiodically produce database values. Programs that are part of the data acquisition function and other EMS application functions will generate calculated data. | Clarification Provided* | F.Kendall B. Blevins | The phrase "periodically and aperiodically" is used to provide for both periodic and non periodic changes of calculated data. ERCOT suggest striking the words periodically and aperiodically for clarification.
23 | Reliant (F.Trefny) | 12 | 3.1 | SCD-FR17 |  | Description: Prior to storage in the database, status data shall be processed to convert the input data to a physical state, and to identify and report changes in state and update summary displays on detection of a change in a quality code. | Rejected | F.Kendall B. Blevins | The result of state change processing is covered in the statement "identify and report" which generically refers to all state change processing.
24 | Reliant (F.Trefny) | 13 | 3.1 | SCD-FR18 |  | Description: For measured values, multiple pairs of limits (high limit, low limit) shall be supported that allow increasing levels of severity to be defined. At least three pairs of limits shall be provided. If the limits are the same, the analog data processing system will alarm only once with the highest level of alarm. Alarm messages to ERCOT operators shall include the data base element name, the alarm type, the current analog value and the alarm threshold causing the alarm. The system shall also support reasonability limits and rate-of-change limits. | Rejected | F.Kendall B. Blevins | ERCOT intends to purchase the vendor's standard SCADA functionality as much as possible. Configurable alarming features as suggested will be addressed in the detail design specifications if required.
25 | Reliant (F.Trefny) | 14 | 3.1 | SCD-FR19 |  | Description: Calculated points shall be derived from pre-defined algorithms supplied with the SCADA system. This Requirements Document assumes that calculations will be performed periodically and that the periodicity of calculations willmail be assigned on a per-point basis. An implementation that triggers a calculation whenever any of the arguments of the calculation change is also acceptable. | Clarification Provided* | F.Kendall B. Blevins | This Requirements Document assumes that calculations will be performed both periodically and aperiodically. Periodically assignment of calculations will be on a per-point basis. Aperiodic implementation will trigger a calculation whenever any of the arguments of the calculation change.
26 | Reliant (F.Trefny) | 14 | 3.1 | SCD-FR20 |  | Description: The quality code of the calculated value shall be the quality code of the input data point with the most severe quality code. Results of calculations that are manually overridden by the ERCOT operator users shall be denoted with a quality code that can be differentiated from the propagation of a manual entry quality code from one its component values. | Accepted | F.Kendall B. Blevins
27 | Reliant (F.Trefny) | 15 | 3.1 | SCD-FR22 |  | As part of the tag placement process, the SCADA system shall prompt the user to enter alphanumeric comment information to be stored with the tag. The comment field shall be at least sixty characters in length. It shall be possible to modify the tag comment information. Tags shall be individually removed by user command. Each tag placement and removal shall be recorded as an event. A summary display shall be made available to the ERCOT operator allowing the operator to view all tags by type on data elements showing the date and time the tag was entered and type of tag, and operator comment. | Accepted | F.Kendall B. Blevins
28 | Reliant (F.Trefny) | 15 | 3.1 | SCD-FR23 |  | ● SetpointSet point control | Accepted | F.Kendall B. Blevins
29 | Reliant (F.Trefny) | 16 | 3.1 | SCD-FR24 |  | Description: Data exchanges shall use the IEC 870-6-503 TASE.2 communications protocol. The SCADA system shall be fully compliant with the protocol Version 2000-04, Conformance Blocks 1,2, and 4. Do any of these specifications state the sign convention for transmission flows? | Clarification Provided | F.Kendall B. Blevins | See S.No. 13.
30 | Reliant (F.Trefny) | 16 | 3.2 | SCD-FR1 |  | Input data from TDSPTSPs | Accepted | F.Kendall B. Blevins
31 | Reliant (F.Trefny) | 16 | 3.2 | SCD-FR1 |  | Description: SCADA shall receive available telemetry from TDSPTSPs for use by Nnetwork Aapplications. Data from TDSPTSPs is described in detail in Section 6.2, TDSPTSP Data Exchange. | Accepted | F.Kendall B. Blevins
32 | Reliant (F.Trefny) | 16 | 3.2 | SCD-FR2 |  | … SCADA shall receive rResource-related telemetry … | Accepted | F.Kendall B. Blevins
33 | Reliant (F.Trefny) | 16 | 3.2 | SCD-FR3 |  | Description: SCADA shall calculate the net interchange for each Block Load Transfer Point. Do we want to also calculate the actual flow between major areas of the ERCOT System, i.e. North to south, etc. for each “generic” flow constraint that is specified for use in ERCOT applications? | Clarification Provided | F.Kendall B. Blevins | There will be several non-protocol specified calculations that will be important to build. These will be created using the tools and methods specified by SCD-FR25 and SCD-FR19.
34 | Reliant (F.Trefny) | 17 | 3.2 | SCD-FR4 |  | Description: SCADA shall calculate the load (generation minus net interchangeflow into or out of an area) withinfor each weather zone. | Accepted | F.Kendall B. Blevins | The term interchange is deleted as ERCOT is a single control area and it is more appropriate to use the terms suggested..
35 | Brazos Electric (T.Kroskey) | 16 | 3.2 | SCD-FR6 |  | Description: SCADA shall calculate MVA for each MW/MVAR pair received for all breakers (?), lines, transformers, and reactors. | Rejected | F.Kendall B. Blevins | The referenced protocol clause 6.5.7.1.13 (1) (a) (ii) does not state that MVA be calculated for breakers, therefore it is not included in this requirements statement. The SCADA calculation processor shall be configured to calculate MVA for any MW/MVAR pair regardless of data source.
36 | GP&L (R.Hoeinghaus) | 16 | 3.2 | SCD-FR6 |  | Description: SCADA shall calculate MVA for each MW/MVAR pair received for all lines, transformers, and reactors. GP&L Comment: Generally Reactors do not have a MW reading from which MVA can be calculated. | Clarification Provided | F.Kendall B. Blevins | Protocol clause 6.5.7.1.13 (1) (a) (ii) includes reactors so it is included here. The requirement is included in the SCADA specification to capture the protocol requirement.
37 | Reliant (F.Trefny) | 17 | 3.2 | SCD-FR6 |  | Description: SCADA shall calculate MVA for each MW/MVAR pair received for all lines, transformers, and reactors. Does the alarm processor only alarm the MVA? | Clarification Provided | F.Kendall B. Blevins | See S.No. 15.
38 | Reliant (F.Trefny) | 18 | 3.3 | SCD-FR7 |  | Description: LFC produces a list of data items unique to each QSE to be sent to the respective QSEs every 4 seconds. The content of the list will vary depending on the execution cycle times of the various AGCgeneration sub-system applications. SCADA shall send the list of data to each respective QSE using either the Set Data Set Element Values or Set Data Value service of ICCP. Every value in the list shall have quality attributes applied. (Note that ERCOT must proactively write generation, regulation and other AGC-related signals to QSEs, so the “SET…” functions of ICCP Conformance Block 1 are required.????) | Rejected | F.Kendall B. Blevins | (1)Agree to change the term AGC to generations subsystem. (2) The SCADA vendor understands the meaning of ICCP Conformance Block 1, according to IEC 870-6-503 TASE.2 protocol (ICCP standard footnoted at bottom of page).
39 | Reliant (F.Trefny) | 19 | 3.4 | SCD-FR9 |  | Description: SCADA shall provide a summary display showing the time and date of detection for each of the following: | Accepted | F.Kendall B. Blevins
40 | Reliant (F.Trefny) | 19 | 3.4 | SCD-FR9 |  | Description: SCADA shall provide a summary display... a. Suspect status points?? b. Suspect analog points ?? . . . Each of these displays shall have sorting and filtering tabs. All summary tables shall be archived. GP&L Comment: Please map the above points to the quality codes in FR14 for clarification | Pending | F.Kendall B. Blevins | Move to Punch List. ERCOT is undertaking an effort to clarify and standardize the semantics of ICCP quality codes and their mapping from the Market Participant's system, the ICCP message, and into the ERCOT EMS. Once completed all requirements referencing quality codes will be updated to conform to the quality code scheme and be self consistent.
41 | Reliant (F.Trefny) | 19 | 3.4 | SCD-FR9 |  | Description: SCADA shall provide a summary display ... . . . d. Manual Replaced disabled by Market Participant points e. Manual Replaced by override pointsERCOT operators f. Abnormal breaker and switch status g. Limit violations h. Base Points | Clarification Provided* | F.Kendall B. Blevins | List will be changed to: d. Manual Disabled by Market Participant e. Manual Disabled by ERCOT Operator f. Manual Replaced by Market Participant g. Manual Replaced by ERCOT Operator h. Manual Disabled i. Manual Replaced j. Abnormal breaker and switch status k. Limit violations l. SCED Base Points
42 | Brazos Electric (T.Kroskey) | 18 | 3.4 | SCD-FR9 |  | Description: SCADA shall provide a summary display for each of the following: … h. SCED Base Points | Accepted | F.Kendall B. Blevins
43 | GP&L (R.Hoeinghaus) | 18 | 3.4 | SCD-FR9 |  | Description: SCADA shall provide a summary display for each of the following: a. Suspect status points b. Suspect analog points c. Stale points d. Manual disabled points e. Manual override points f. Abnormal breaker and switch status g. Limit violations h. Base Points Each of these displays shall have sorting and filtering tabs. All summary tables shall be archived. GP&L Comment: Please map the above points to the quality codes in FR14 for clarification | Pending | F.Kendall B. Blevins | See S.No. 40.
44 | Reliant (F.Trefny) | 19 | 3.4 | SCD-FR10 |  | Description: SCADA shall provide ICCP link availability statistics. EMS displays shall be provided to show hourly, daily, and monthly availability statistics for each ICCP link. Availability statistics shall exclude planned outages how do you do this?. Availability statistics shall be archived. | Clarification Provided | F.Kendall B. Blevins | It is the SCADA vendor's responsibility to meet the requirement according to their system design. That said, there are a number of ways to filter the statistics including inhibiting statistics accumulation with special "out of service" techniques, post-processing with outage logs, etc.
45 | Brazos Electric (T.Kroskey) | 19 | 3.4 | SCD-FR12 |  | Description: Market pParticipants will associate … | Accepted | F.Kendall B. Blevins
46 | GP&L (R.Hoeinghaus) | 19 | 3.4 | SCD-FR12 |  | Description: Market participants will associate every telemetered value transferred via ICCP with a time stamp having at least a 1 second resolution. SCADA shall use the time stamp to determine if the value received is “stale”. Each point in the real-time database shall have an attribute indicating whether “stale” data processing is to be applied to the value, and the number of seconds elapsed (the “stale time” attribute) before the value is considered to be “stale”. A second attribute shall be associated with every point indicating whether the value is or is not stale. For points designated to have “stale” processing applied, the received value’s time stamp shall be compared with the current system time to determine whether the value has exceeded its “stale time” attribute. Values exceeding “stale time” shall be marked “stale”. Values not exceeding “stale time” shall be marked “not stale”. GP&L Comment: concerned about the items listed in the ERCOT Note below as well as processing requirements on MP end - understand the 1 second time stamp is just the real time value of time at the time of sending the data – has nothing to do with the time of any type of event impacting the values quality flag – is this correct? | Pending | F.Kendall B. Blevins | See S,No. 16.
47 | Reliant (F.Trefny) | 20 | 3.4 | SCD-FR12 |  | Description: Market participants will associate every telemetered value transferred via ICCP with a time stamp having at least a 1 second resolution. SCADA shall use the time stamp to determine if the value received is “stale”. Each point in the real-time database shall have an attribute indicating whether “stale” data processing is to be applied to the value, and the number of seconds elapsed (the “stale time” attribute) before the value is considered to be “stale”. A second attribute shall be associated with every point indicating whether the value is or is not stale. For points designated to have “stale” processing applied, the received value’s time stamp shall be compared with the current system time to determine whether the value has exceeded its “stale time” attribute. Values exceeding “stale time” shall be marked “stale”. Values not exceeding “stale time” shall be marked “not stale”. This seems incorrect. The Market Participant does not know if ERCOT has received the ICCP data. Seems like ERCOT’s system must check if it has not received an update from a Market Participant after some established time interval, then ERCOT’s SCADA system must mark all data from that MP as stale. (continued in following comment) | Pending | F.Kendall B. Blevins | See S,No. 16.
48 | Reliant (F.Trefny) | 20 | 3.4 | SCD-FR12 |  | (continued from previous comment) MPs will also be sending a quality code with each point if the MP looses communication with its field device. This “stale” quality code needs also to be processed. Please explain how all this works and ERCOT systems keeps track of which “stale” quality code it is processing. | Clarification Provided* | F.Kendall B. Blevins | See S,No. 16.
49 | TXU Energy Delivery (E.Clark) | 19 | 3.4 | SCD-FR12 |  | Note: ERCOT intends that the vendor assess the impact of this requirement on the processing requirements including any conflicts with reporting by exception or non-telemetered data being exchanged via ICCP. [This is a very important note. Systems that use report by exception to gather data from their RTUs may have time stamps that reflect the last change in the value. For switching devices, these values could be months old. It seems to be more important to send ICCP data with the proper quality codes than with time stamps. The quality codes will allow SCADA to determine the quality of the data, and will allow the State Estimator application to determine the “staleness” of the data it uses.] | Clarification Provided* | F.Kendall B. Blevins | See S,No. 16.
50 | Reliant (F.Trefny) | 20 | 3.4 | SCD-FR13 |  | Description: There shall be the capability for the ERCOT operators to Manually Replaceoverride SCADA telemetry from one-line diagrams and station tabular displays to correct erroneouschange breaker and switch status before that information is processed by the Network Security Analysis for the next SCED interval. Summary dispalys of all entries are provided according to above. | Accepted | F.Kendall B. Blevins
51 | Reliant (F.Trefny) | 21 | 3.4 | SCD-FR14 |  | Description: Per the TAC approved Telemetry Standards Document, SCADA shall process the following quality codes associated with ICCP status and analog data: … 6. Manually Replaced by ERCOT operator SCADA shall produce alarms for any change in quality code as well as return to valid alarms. This can overload the alarm processor and well as the ERCOT operators. Suggest only putting them in the summary display. | Pending | F.Kendall B. Blevins | See S.No. 40. Agree with comment 2 that this can be an issue that might overload the alarm system therefore the feature should be provided as a configurable one.
52 | Reliant (F.Trefny) | 21 | 3.4 | SCD-FR14 |  | … condition codes from each TDSPTSP and QSE … | Accepted | F.Kendall B. Blevins
53 | GP&L (R.Hoeinghaus) | 20 | 3.4 | SCD-FR14 |  | SCADA shall convert data condition codes from each TDSP and QSE in a consistent manner for all applicable ERCOT applications. GP&L Comment: ERCOT & the Market Participants (MP’s) will need to discuss the conversion or mapping of MP’s ICCP quality codes as there are more (at least in some systems) codes in the MP’s system than the above 5 and they are not necessarily converted on a 1 to 1 basis. There needs to be reconciliation between the above definitions and the definitions in the MP’s system to both ERCOT & the MP’s agreement. | Pending | F.Kendall B. Blevins | See S.No. 40.
54 | Reliant (F.Trefny) | 21 | 3.4 | SCD-FR15 |  | Description: SCADA failover time shall not exceed five minutes. Each TSP and QSE shall use fully redundant data communication links (ICCP or RTU) between its control center systems and ERCOT systems such that any single element of the communication system can fail and: (a) For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and (b) For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT’s control centers with updates of all data continuing at a 30 second or less scan rate. | Accepted | F.Kendall B. Blevins
55 | Reliant (F.Trefny) | 22 | 4 | SCD-SR1 |  | Description: SCADA shall perform all data processing within the applicable scan interval according to the following processing times: ● 2-second data: 1 second ● 4-second data: 1 second ● 10-second data: 52 seconds [no data is allowed to be provided at less than 10 second scan rate] ● 5-minute data: 30 seconds ● 10-minute data: 30 seconds ● 60-minute data: 60 seconds | Rejected | F.Kendall B. Blevins | There are data points that are to be calculated at different time intervals and made available to market participants. Those include 5 minute SCED, 10 minute Dynamic Rating and 60 minute data. The SCADA system should be updated periodically (5, 10 60 Minutes) by the calculation process of the SCADA system within the time specified. SCD-SR1 should stand as written.
56 | Reliant (F.Trefny) | 22 | 4 | SCD-SR2 |  | Description: SCADA shall monitor the availability of ICCP links. The cumulative availability in percentage shall be calculated for each hour, day and month. SCADA shall alarm the ERCOT operator assigned maintenance funcationality messaging if the availability falls below the pre-set monthly threshold. Availability thresholds shall be configurable by ERCOT Analysts. Initially these thresholds shall be configured as follows: | Accepted | F.Kendall B. Blevins
57 | Reliant (F.Trefny) | 22 | 4 | SCD-SR2 |  | ● TDSPTSP ICCP linkscommunication using both primary and secondary systems shall achieve a monthly availability of ninety-eight (98%) percent, excluding approved planned outages. Ninety eight percent is way to low. This allows the data link to be down over 15 hours a month. Not acceptable to meet nodal requriements. I suggest ICCP must me up at least 99.8% which still alows 6 hours a month failure. We have totally redundant communication paths in nodal and this should be achievable. ● QSE ICCP linkscommunciation using both primary and secondary systems shall achieve a monthly availability of ninety-nine point ninety-nine (99.99%) percent, excluding approved planned outages. | Accepted | F.Kendall B. Blevins
58 | Reliant (F.Trefny) | 22 | 4 | SCD-SR2 |  | Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data. A link will be considered as available when at least the predefined percent (configurable by an ERCOT Analyst and initially set to eighty-five (895%)) of the data defined on that link is successfully transferred to ERCOT with a valid or manual quality code. (continued in following comment) | Accepted | F.Kendall B. Blevins
59 | Reliant (F.Trefny) | 22 | 4 | SCD-SR2 |  | The current and previous month’s availability data shall be stored in EMS database and shall be viewable through EMS user interface. This data must be provided to the perfomance monitoring requiremnts in section 8.3 of the protocols and posed on the MIS for any failures to perform (secition 8.4). Has the TAC approved “TAC-approved TSP Monitoring Program referenced below been developed? This “monitoring program may influence technical requrements of this specifition. (continued in following comment) | Clarification Provided | F.Kendall B. Blevins | This SCADA specification is attempting to link to availability performance criteria. ERCOT has suggested the setting be configurable by an analyst which will address this issue.
60 | Reliant (F.Trefny) | 22 | 4 | SCD-SR2 |  | (continued from previous comment) 8.3 TSP Performance Monitoring and Compliance (1) ERCOT shall develop a TAC-approved TSP Monitoring Program to be included in the Operating Guides for TSPs. The metrics developed by ERCOT must include the following elements of transmission system planning, operations and maintenance: (a) Transmission Element rating calculations; (b) Real-Time data: (i) Meeting telemetry standards, including the installation of new measurement equipment and the accuracy of measurements; (ii) Communications system availability; and 8.4 Non-Compliance (1) Reports of all activities that do not meet the performance criteria in this Section and in the Operating Guides must be provided to TAC, the ERCOT Board, the PUCT and to the NERC Board as appropriate. Non-compliance reports must be posted on the MIS Secure Area on delivery. | Clarification Provided | F.Kendall B. Blevins | See S.No. 59.
61 | Reliant (F.Trefny) | 23 | 4 | SCD-SR4 |  | Description: SCADA shall interface to existing ERCOT custom applications (such as RTMONI)?? What is this? Is it required in the protocols? in the new system. (Please note that our current load forecast is dependent upon RTMONI calculations to support the weather zone calculations.) | Clarification Provided* | F.Kendall B. Blevins | This requirement will be rewritten to require a "backward compatible" real-time database access API without referring to existing ERCOT-developed applications.
62 | Reliant (F.Trefny) | 24 | 4 | SCD-SR10 |  | Description: The SCADA function shall provide on-line editing tools and screens to allow an EMS Analysts to add, remove, and edit data points telemetered from QSEs and TDSPTSPs. Are these then avaliable on a summary page so that they eventually get fixed? Who at ERCOT is responsible for oversight of TSPs and QSEs who are sending bad data to ERCOT? | Clarification Provided | F.Kendall B. Blevins | This supplemental requirement calls for the database editing tool. It is the means by which the analyst may fix errors without requiring a offline change to be propagated to production.
63 | Brazos Electric (T.Kroskey) | 23 | 4 | SCD-SR10 |  | Description: The SCADA function shall provide on-line editing tools and screens to allow an EMS Analysts to add, remove, and edit data points telemetered from QSEs and TDSPs with an audit log of changes made. | Accepted | F.Kendall B. Blevins
64 | Reliant (F.Trefny) | 25 | 4 | SCD-SR11 |  | Description: Communication between ERCOT and market participants is provided by redundant communication links. One link traverses ERCOT’s Frame Relay network, and the other link traverses ERCOT’s DACS network. The DACS network acts as a backup to the Frame Relay network. If communication with a market participant is lost on the primary link, SCADA shall automatically establish (or otherwise activate) communication over the backup link. Will be be providing a use case to test the true redundancy of these links? | Clarification Provided | F.Kendall B. Blevins | Yes (Several Use Cases will need to be developed which are part of project scope and several testing phases will be required for both ERCOTsystems and with market participants )
65 | Brazos Electric (T.Kroskey) | 27 | 6 |  |  | The tables below specify the data exchange requirements known as of the May 2006 protocols. The data includes information specifically identified in the protocols, and other data presently exchanged and/or expected to be needed to support operation under the TNPNodal protocols. ... | Accepted | F.Kendall B. Blevins
66 | Reliant (F.Trefny) | 29 | 6 | Table 1 |  | Number of TDSPTSPs | Accepted | F.Kendall B. Blevins
67 | Reliant (F.Trefny) | 29 | 6 | Table 1 |  | . . . . . . . . | Clarification Provided | F.Kendall B. Blevins | See S.No. 8.
68 | Reliant (F.Trefny) | 29 | 6.1.1 | Table 2 |  |  | Accepted | F.Kendall B. Blevins
69 | Reliant (F.Trefny) | 30 | 6.1.1 | Table 3 |  |  | Clarification Provided* | F.Kendall B. Blevins | All changed accepted except for the "Emergency Basepoint" change. The "Emergency Basepoint" flag is set to tell the QSE that the Base Point provided is an emergency base point.
70 | NRG (D.S.Mai) | 28 | 6.1.1 | Table 3 |  |  | Accepted | F.Kendall B. Blevins
71 | Reliant (F.Trefny) | 30 | 6.1.1 | Table 4 |  |  | Rejected | F.Kendall B. Blevins | Only one value is exchange per bus or load zone. The recommended change would imply multiple values are exchanged and would thus be ambiguous in this database sizing table.
72 | Reliant (F.Trefny) | 30 | 6.1.2 | Table 6 |  |  | Clarification Provided | F.Kendall B. Blevins | See protocol clause 6.5.5.2 (2) c.
73 | GP&L (R.Hoeinghaus) | 28 | 6.1.2 | Table 6 |  |  | Clarification Provided | F.Kendall B. Blevins | RBE means Report By Exception. Will add this acronym to the Energy Management System requirements specification listed acronyms.
74 | Brazos Electric (T.Kroskey) | 28 | 6.1.2 | Table 7 |  | Generation Resource MVARvar | Accepted | F.Kendall B. Blevins
75 | Reliant (F.Trefny) | 30 | 6.1.2 | Table 7 |  |  | Accepted | F.Kendall B. Blevins
76 | Reliant (F.Trefny) | 30 | 6.1.2 | Table 7 |  |  | Clarification Provided* | F.Kendall B. Blevins | Changes accepted except for the addition of "Resource Responsibility". This item is not specified in the protocols.
77 | Reliant (F.Trefny) | 30 | 6.1.2 | Table 7 |  |  | Clarification Provided* | F.Kendall B. Blevins | Changes to the Inhibit Reg flag and transformer tap position entries are accepted. As this table pertains to SCADA sizing, it is not clear as to any additional clarification the commenter is requesting.
78 | Reliant (F.Trefny) | 32 | 6.1.2 | Table 8 |  |  | Clarification Provided* | F.Kendall B. Blevins | Changes accepted except for the addition of "Resource Responsibility". This item is not specified in the protocols. To be consistent with the protocols "RBE" is being removed from the tables. However, a new supplemental requirement will be added to the specification requiring the SCADA vendor to support RBE. Eliminating the use of RBE in the new system will impose an immense load on the EMS. Zonal was forced to implement RBE to the greatest extent possible in order to meet its performance requirements. Removing RBE will also impact Market Participant systems. We know that in practice, RBE must be used for the system to function properly. Also be aware that RBE is the preferred way to reliably receive via ICCP all state changes of automatic reclosers.
79 | Reliant (F.Trefny) | 32 | 6.1.2 | Table 8 |  |  | Accepted | F.Kendall B. Blevins
80 | Reliant (F.Trefny) | 33 | 6.2 | Tables 10-20 |  | Several instances of the following change throughout Section 6.2: TDSPTSP | Accepted | F.Kendall B. Blevins
81 | Brazos Electric (T.Kroskey) | 30 | 6.2 | Tables 11-14, 16,17 |  | Several instances of the following change throughout Section 6.2: MVARvar | Accepted | F.Kendall B. Blevins
82 | Reliant (F.Trefny) | 33 | 6.2 | Table 12 |  |  | Clarification Provided* | F.Kendall B. Blevins | The references to 3.10.7.4.2 will be added. The reference to 6.5.7.1.13 (1) (a) (ii) will not be deleted.
83 | TXU Energy Delivery (E.Clark) | 29 | 6.2 | Table 12 |  | Line Flow MVA (calculated) [This should be calculated by ERCOT. Some TSPs that rate lines based on current flow may not have this value. Instead of using bandwidth to send this value, it should be calculated at ERCOT.] | Clarification Provided | F.Kendall B. Blevins | Comment is correct. See SCD-FR6.
84 | Reliant (F.Trefny) | 33 | 6.2 | Table 13 |  |  | Clarification Provided* | F.Kendall B. Blevins | See S.No. 82.
85 | TXU Energy Delivery (E.Clark) | 30 | 6.2 | Table 13 |  | Shunt Flow MVA (calculated) [This should be calculated at ERCOT if needed.] | Clarification Provided | F.Kendall B. Blevins | See S.No. 83.
86 | Reliant (F.Trefny) | 34 | 6.2 | Table 14 |  |  | Clarification Provided | F.Kendall B. Blevins | Protocol calls for "flow of all modeled transmission elements." As a sizing table, the SCADA specification is accounting for circuit breakers that may be modeled and provide flow. Keep in mind that these tables are for SCADA sizing. They make no attempt to specify the actual data exchange required between ERCOT and Market Participants.
87 | TXU Energy Delivery (E.Clark) | 30 | 6.2 | Table 14 |  | Breaker Status (with normal status indicator) [Normal/abnormal status indication is usually a function of the SCADA data base that is displaying the information, in this case the ERCOT data base.] | Clarification Provided | F.Kendall B. Blevins | Protocol clause 6.5.7.1.13 (1) (a) (iv) calls for "normal breaker and switch status", so it is included parenthetically in the sizing table for consistency with the protocols. We realize that Market Participants won't be transmitting this as the normal state will be permanently defined in the ERCOT database.
88 | Reliant (F.Trefny) | 34 | 6.2 | Table 15 |  |  | Clarification Provided* | F.Kendall B. Blevins | See S.No. 78.
89 | TXU Energy Delivery (E.Clark) | 30 | 6.2 | Table 15 |  | Switch Status (with normal status indicator) [Normal/abnormal status indication is usually a function of the SCADA data base that is displaying the information, in this case the ERCOT data base.] | Clarification Provided | F.Kendall B. Blevins | See S.No. 87.
90 | Reliant (F.Trefny) | 34 | 6.2 | Table 16 |  |  | Accepted | F.Kendall B. Blevins
91 | Reliant (F.Trefny) | 34 | 6.2 | Table 17 |  |  | Clarification Provided* | F.Kendall B. Blevins | See S.no. 78.
92 | Reliant (F.Trefny) | 34 | 6.2 | Table 18 |  |  | Clarification Provided* | F.Kendall B. Blevins | See S.no. 78.
93 | GP&L (R.Hoeinghaus) | 32 | 6.2 | Table 20 |  |  | Rejected | F.Kendall B. Blevins | Although the GP&L comment is true these tables are included in the specification to provide the SCADA vendor with information needed to properly size the system.
94 | Brazos Electric (T.Kroskey) | 32 | 6.2 | Table 20 |  |  | Accepted | F.Kendall B. Blevins
95 | NRG (D.S.Mai) | 32 | 6.3 | Table 21 |  | Table 21 - Data Available for Reading by All Market Participants (via MIS Secure Area and ICCP) | Rejected | F.Kendall B. Blevins | This is a sizing table for the SACDA vendor. The addition of the MIS does not add clarification to this table.
96 | GP&L (R.Hoeinghaus) | 32 | 6.3 | Table 21 |  |  | Rejected | F.Kendall B. Blevins | This is a SCADA sizing table and the Protocol section 6.5.7.5 (1) (a) and (b) do not include the word "Available". Therefore it is not included in this table because it does not add clarification.
97 | Reliant (F.Trefny) | 36 | 6.3 | Table 21 |  |  | Accepted | F.Kendall B. Blevins

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.