## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For Voltage Support Services, Version 0.90
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | All Voltage Support Services requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Process Map (Fig. 2-1) that describes the Voltage Support Services applications. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
2 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | (added linespace between paragraphs) All Voltage Support Services requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Process Map (Fig. 2-1) that describes the Voltage Support Services applications. These requirements are based on the May 2006 version of Nodal Protocols and NERC, FERC, and PUCT requirements approved as of May 2006. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
3 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  |  | (added space between "base" and "case") The main requirements in the scope of VSS include: ● Establish a corrective plan for base case constraints violations | Accepted | Nodal EMS NA Team | Comment accepted as-is. Spelling changed to "base case" and "save case" throughout the document.
4 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  |  | The first set of users includes ERCOT transmission system operators. System operators will use this tool as a part of the real-time sequence to recommend preventive actions to avoid voltage violations, or post-contingency voltage violations, usually by switching reactive devices, tapping transformers, or adjusting generator voltage set points. Since none of these actions affect energy dispatch, they are separate from the Security Constrained Economic Dispatch (SCED) market functions. Occasionally a voltage violation may be intractable tonot be corrected through control by reactive devices alone. In these cases, the VSS functionality may generate a constraint which may be passed to the Transmission Constraint Manager (TCM)/SCED functions for resolution. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
5 | Brazos Electric (T.Kroskey) | 9 | 2.1 |  |  | (deleted period after "Regulators") The controls that the program uses to satisfy the operating constraints are reactive power sources that can be either switched on or off, as is the case with switched capacitors and reactors, or that can be continuously adjusted as is the case with generator Automatic Voltage Regulators., LTC, SVC, and FACTs devices. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
6 | Brazos Electric (T.Kroskey) | 9 | 2.1 |  |  | The flow of computations and creation of the specific outputs shall be governed by the Operator through the options he/shethat can be entered through a user interface. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
7 | CNP (E.John) | 8 | 2.1 |  |  | CNP Comment: Section 2.1 talks about this process being used by Real Time Operations as well as Operational Planning. On the Planning side it discusses that this program will be used to develop generator voltage profiles. Currently ERCOT sends out proposed PSSE cases to the TDSPs for their review and comments when ERCOT is studying the seasonal voltage profile settings. Will this VSS be able to generate either a .sav or .raw file for TDSPs to review. | Clarification Provided* | Nodal EMS NA Team | When VSS is used in operations planning, then it is run in a study mode (STNET), and it is possible to generate PSSE case and raw files. Modify the paragraph to the following: The second set of users includes ERCOT Operations Engineers responsible for establishing ERCOT generator voltage set points for short term studies (several days ahead). This set of users will use the VSS functions in a study mode to recommend voltage set points for each generator which eliminate or minimize post-contingency voltage violations.
8 | CNP (E.John) | 8 | 2.1 |  |  | It also states that VSS computations will be based using a solved power flow model from which the module will adjust reactive devices until it eliminates all voltage and MVAR constraints. It mentions generator AVRs which can be continuously adjusted. Currently ERCOT requires generators to have these devices on and in voltage control mode but I don’t believe there is a requirement to actually monitor if this is the case. | Clarification Provided* | Nodal EMS NA Team | At present, there is no verification for AVR being in service and regulating voltage. The following sentence to be added in the text: "The assumption is that AVR is always on when the unit is in service."
9 | CNP (E.John) | 8 | 2.1 |  |  | After VSS solves an optimization problem, how will ERCOT communicate the operational results of the VSS recommendations where this shows what reactive devices are switched on and off as well as what adjustable devices will be changed? | Clarification Provided* | Nodal EMS NA Team | The following changes/edits to be made in FR14 to reflect that the results will be communicated via MIS. FR14: Voltage Profile MIS Posting (title change) FR14: The voltage set points across the ERCOT system “Voltage Profile” and the on/off status of reactive sources from a selected case shall be made available for posting in the MIS secure area. The Operator shall be able to manually trigger the transfer to the MIS of the voltage profile and on/off status of reactive sources.
10 | Brazos Electric (T.Kroskey) | 10 | 2.2.1 |  |  | VSS function uses save cases as the source of most of its data, as specified in Table 2-1. The following data from a save case shall be used in VSS; - Static network model, - Load MW and MVAR - Generation, MW and MVARvar output - Bus KV limits, - MVARr limits of reactive sources, - Tap limits of LTCs, ... | Accepted | Nodal EMS NA Team | Comment accepted as-is.
11 | Brazos Electric (T.Kroskey) | 10 | 2.2.1 |  |  | Table 2-1 lists inputs to Voltage Support Services tofrom various systems. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
12 | Brazos Electric (T.Kroskey) | 10 | 2.2.1 | Table 2-1 |  | g) Units (MVARar) | Accepted | Nodal EMS NA Team | Comment accepted as-is.
13 | Brazos Electric (T.Kroskey) | 10 | 2.2.1 | Table 2-1 |  | (added space between "base" and "case") 1) Base case | Accepted | Nodal EMS NA Team | Comment accepted as-is.
14 | CNP (E.John) | 12 | 3 | VS-FR1 |  | Description: Voltage Support shall use the following controls, subject to their switching priorities: … 2. Setpoints for local control of capacitor banks [TDSPs will have to determine the thresholds for using these devices.](Voltage to switch on / Voltage to switch Off) | Clarification Provided* | Nodal EMS NA Team | Add sentence in the FR1. ERCOT in coordination with TSP shall determine the actual controls based on the VSS results. (Note: ERCOT has a responsibility on establishing voltage control setpoints for capbanks where applicable).
15 | Brazos Electric (T.Kroskey) | 12 | 3 | VS-FR1 |  | 8) Units (MVARar) | Accepted | Nodal EMS NA Team | Comment accepted as-is.
16 | Brazos Electric (T.Kroskey) | 14 | 3 | VS-FR5 |  | (added "-" between "Real" and "Time") The Special Protection Scheme (SPS) models shall be incorporated as part of the Voltage Support for Real -Time and Study Mode. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
17 | GP&L | 14 | 3 | VS-FR5 |  | Description: The Special Protection Scheme (SPS) models shall be incorporated as part of the Voltage Support for Real Time and Study Mode. The vendor shall propose a method of incorporating SPS in VSS, subject to ERCOT approval. GP&L Comment: Should Remedial Action Plans also be included here? | Clarification Provided | Nodal EMS NA Team | In general RAPs are much slower than SPS and for voltage control are considered to be inadequate.
18 | Brazos Electric (T.Kroskey) | 14 | 3 | VS-FR6 |  | (added "-" between "Real" and "Time") The load rollover functionality shall be correctly interpreted by Voltage Support Services for Real -Time and Study Mode. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
19 | CNP (E.John) | 15 | 3 | VS-FR8 |  | Description: Upon each execution of the Voltage Support function, a save case shall automatically be created if the corresponding status of Operator entered flag is true. An ERCOT defined naming convention shall be used to automatically create savecases[Will this save case be readable using PSSE?], which will allow to easily distinguish the cases by creation date. | Clarification Provided | Nodal EMS NA Team | The VSS savecase will not be readable by PSSE since it is entirely different format.
20 | Brazos Electric (T.Kroskey) | 15 | 3 | VS-FR9 |  | (added "-" between "Real" and "Time", deleted space before “in” in bullet 2 ) The Real -Time Voltage Support shall be triggered as part of the Real -Time Sequence when any of the following conditions are detected: 1) Constraints violations in the State Estimator base case 2) Constraints violations in any of the contingencies of real -time Contingency Analysis. .... | Accepted | Nodal EMS NA Team | Comment accepted as-is.
21 | CNP (E.John) | 15 | 3 | VS-FR9 |  | Description: The Real Time Voltage Support shall be triggered [What are the consequences of these sections once the VSS has been triggered? Will ERCOT be providing control action recommendations?]as part of the Real Time Sequence when any of the following conditions are detected: 1) Constraints violations in the State Estimator base case 2) Constraints violations in any of the contingencies of real time Contingency Analysis. 3) Forced outage critical element. 4) Manual | Clarification Provided | Nodal EMS NA Team | ERCOT will directly communicate the control action recommendations to TSP.
22 | Brazos Electric (T.Kroskey) | 16 | 3 | VS-FR12 |  | (added "-" between "Real" and "Time") Generator MW controls, if any, are suggested as part of the preventive action and accepted by Operator, shall be transferred automatically to the Transmission Constraint Management function when VSS runs in real -time mode. | Accepted | Nodal EMS NA Team | Comment accepted as-is.
23 | CNP (E.John) | 16 | 3 | VS-FR14 |  | Description: The seasonal voltage set points across the ERCOT system “Voltage Profile” and the on/off status of reactive sources from a selected case shall be made available for posting in the MIS secure area[Can this also include the case that the VSS was run on?]. The Operator shall be able to manually trigger the transfer to the MIS of the voltage profile and on/off status of reactive sources. | Clarification Provided* | Nodal EMS NA Team | The save case will not be posted on MIS. However, the functional requirement will be added to VSS to post save case on MOTE, which shall be available to all TSP and QSE.
24 | CNP (E.John) | 17 | 3 | VS-FR15 |  | Description: Operator shall be provided with displays for each of the following. 1) List of Corrective Actions for the base case 2) List of Preventive Actions considering base case and all contingency violations simultaneously. 3) A composite display showing a summary of all Corrective and Preventive Action plans. [? Will ERCOT be providing control action recommendations or action plans?] | Clarification Provided | Nodal EMS NA Team | ERCOT will post control action recommendations on MIS, and action plan will be carried out through direct communication with the TSP.
25 | Brazos Electric (T.Kroskey) | 18 | 4.1 | VS-SR1 |  | (added "-" between "Real" and "Time", added period after “network”) Description: Real- Time and study Voltage Support triggered under FR-9 and FR-10 shall be able to complete the solution within 1 minute for 100 post contingency voltage violations for ERCOT power network. | Accepted | Nodal EMS NA Team | Comment accepted as-is.

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.