## Outage Evaluation
| Document Name: |  |  |  | Texas Nodal TN.EMS Requirements Specification For Outage Evaluation, Version 0.90
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Description | Response | Reviewer | Reason / Comment
1 | CNP | 8 | 2.1 |  | ERCOT must use reasonable efforts, consistent with Good Utility Practice, to approve in a timely manner all the requested outages that, when implemented, are not expected to cause either system reliability issues or an avoidable excessive cost (? – will there be a scale of excessive costs versus the costs incurred by an outage being cancelled/rescheduled?). | Clarification Provided | Nodal EMS NA Team | The tool will provide the cost, but not a threshold, i.e. the scale of excess costs. That judgment will be guided by the Business process definition.
2 | CNP | 8 | 2.1 |  | Outage Evaluation, which is the subject of this specification, is used for processing outages that require approvals. Outage Evaluation shall be capable of modeling and simulating the ERCOT power system during the times covered by the requested outages. OE shall be able to reflect the requested outages in the model of the ERCOT system; it shall be able to commit MW and MVAr resources necessary to meet the load, reserve and VAR requirements, and it shall determine a generation profile that meets ERCOT security criteria. Outage Evaluation shall also have the capability to calculate an expected cost of production with all outages accommodated, as well as provide sensitivities of this cost to each of the planned outages (does this apply to both resource and TSP outages?). For cases in which overloads can not be avoided with all the requested outages being accommodated, Outage Evaluation shall determine sensitivities of flow violations to the outages. | Clarification Provided* | Nodal EMS NA Team | Yes. To reflect the clarification, we are suggesting a wording change of the bolded sentence to the following: "Outage Evaluation shall also have the capability to calculate an expected cost of production with all outages accommodated, including transmission and resource, as well as provide sensitivities of this cost to each of the planned outages."
3 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  | OE shall be able to reflect the requested outages in the model of the ERCOT system; and it shall be able to commit MW and MVARr resources necessary to meet the load, reserve and VAR requirements, and it shall determine a generation profile that meets ERCOT security criteria. | Accepted | Nodal EMS NA Team
4 | CNP | 9 | 2.2 |  | 2.2 OE Scope The Outage Evaluation function relies on running, manually or automatically, a sequence of power flow type studies to determine if any of the planned outages places ERCOT into an insecure operating state. OE shall also have a function to commit and dispatch MW and MVAR resources to satisfy ERCOT security criteria. If for some reason the automatic program does not succeed in finding a secure operating state, OE shall produce a set of sensitivities relating the remaining overloads to the outages, and thus enable the Scheduler to assess which of the outage requests are the candidates for rescheduling (will there be levels of rescheduling criteria and will the criteria be based solely on sensitivity or will the project impact/importance/cost play a role in the decision ?). | Clarification Provided | Nodal EMS NA Team | An outage request will be rejected if it doesn't meet ERCOT and NERC reliability standards or has a high cost that can may reduced if scheduled at a better time. The ERCOT Outage Coordinators will work with the outage requester at correcting the problem and or rescheduling the outage.
5 | CNP | 9 | 2.2.1 |  | 2.2.1 Functional Requirements Overview • Provide a repository for all data required for the OE study cases. Examples of this data include full network models, transmission element constraints, loads, generation, unit commitment and dispatch preferences, expected temperatures, load distribution factors, and program run options. Applications external to OE are responsible for preparing, validating and uploading to the OE database (1) complete breaker level network models, (2) associated lists of contingencies and (3) Dynamic Ratings Static Table (RLT), which is a table of transmission element ratings as a function of ambient temperature. OE shall provide other functions needed to collect and assemble the remaining data, as is specified further in this document. Are RAP’s and SPS schemes included? | Clarification Provided | Nodal EMS NA Team | Yes, RAP's and SPS schemes are part of contingency analysis.
6 | NRG (D.S.Mai) | 8 | 2.2.1 |  | · Provide a capability to upload a file with typical price curves created from Note: is this the Typical Price Calculator? a source outside the OE. | Clarification Provided* | Nodal EMS NA Team | The requirement was written with the assumption that this will be an external function. However, changes to the OE requirements are proposed to include functionality for Typical Price Calculation.
7 | CNP | 9 | 2.2.1 |  | · Provide a contingency analysis function that can be configured to run on multiple time intervals (different time intervals may have different parameters) in a single execution and to rank contingencies according to severity. The contingency analysis function shall provide a valid solution for every condition that is physically plausible, even if prolonged operation in some of these post-contingency conditions is not viable. | Clarification Provided | Nodal EMS NA Team | Each study will consist of multiple power flow cases, one case per time interval. Each study case will have its own parameters.
8 | ERCOT | 9 | 2.2.1 |  | ● Provide functionality to automatically commit generation MW and MVAr resources without considering startup and shutdown costs, and without using inter-temporal constraints. --------------------------------------------- ● Provide functionality to automatically commit generation MW and MVAr resources without considering startup and shutdown costs, and without using inter-temporal constraints. | Accepted | Nodal EMS NA Team
9 | Brazos Electric (T.Kroskey) | 9 | 2.2.1 |  | · Provide functionality to automatically commit generation MW and MVARr resources without considering startup and shutdown costs, and without using inter-temporal constraints. | Accepted | Nodal EMS NA Team
10 | NRG (D.S.Mai) | 10 | 2.2.1 |  | · For cases with a failure of the underlying power flow engine to solve, an automatic change of the convergence criteria, a number of iterations, or a similar technique shall be used and a rerun attempted to produce an approximate solution, along with an indication of the quality of that solution. All the calculations that require a solved power flow case shall be able to use the approximate solution as a starting point, and associate with the results an indicator of the quality of the starting point, i.e. a solved case or a relaxed solved case. | Accepted | Nodal EMS NA Team
11 | Brazos Electric (T.Kroskey) | 11 | 2.2.1 |  | One of the most critical computational components in OE is computation of secure states. Figure 2-2 depicts a conceptual diagram of computational flows involved in computing secure states. The block labeled “Secure MW and MVAR Profile” in Figure 2.1 provides the main computational capability for blocks “Find Secure MW and MVARr profiles for base case”, “Contingency Specific RAPs”, and “Preventive Actions” of Figure 2-2. | Accepted | Nodal EMS NA Team
12 | Brazos Electric (T.Kroskey) | 16 | 2.2.2.1 |  | 2.2.2.1 Inputs From NMMS: Breaker oriented network models, Contingency definitions consistent with each full network model, SPS and RAP, and Dynamic Ratings Static Table. | Accepted | Nodal EMS NA Team
13 | Brazos Electric (T.Kroskey) | 16 | 2.2.2.1 |  | From Mid and Long Term Load Forecasts: Hourly load forecast (for the mid term), and daily load forecast, with daily high and low, for the long term. | Accepted | Nodal EMS NA Team
14 | NRG (D.S.Mai) | 16 | 2.2.2.1 |  | From Market note: is this Market Interface (MI)?Database: The generation in/out–of-service status. | Clarification Provided* | Nodal EMS NA Team | Proposed new wording: Instead of "From Market Database", we are proposing a new wording, "From Market Management System (COP)".
15 | Brazos Electric (T.Kroskey) | 16 | 2.2.2.1 |  | From EMS: Load Distribution Factors. | Accepted | Nodal EMS NA Team
16 | Brazos Electric (T.Kroskey) | 16 | 2.2.2.1 |  | From Typical Price Calculator: Averaged Energy Offer (AEO) curves for all generators. | Accepted | Nodal EMS NA Team
17 | NRG (D.S.Mai) | 16 | 2.2.2.1 |  | From Typical Price Calculator: Averaged Energy Offer (AEO) curves for all generators Note: where is the Typical Price Calculator function described? | Clarification Provided | Nodal EMS NA Team | We are proposing to extend the OE requirement to include a description of the functionality for computing AEO.
18 | ERCOT | 12 | 2.2.2.1 |  | Various File Uploads: Active power generation profile for all generators; Averaged Energy Offer (AEO) curves for all generators; Seasonal load profiles; Average daily high temperatures (for use in predicting dynamic schedules beyond 21 days), and DC tie schedules. ----------------------------------------------------- Various File Uploads: Active power generation profile for all generators; Averaged Energy Offer (AEO) curves for all generators; Seasonal load profiles; Average daily high temperatures (for use in predicting dynamic schedules beyond 21 days), and DC tie schedules. | Accepted | Nodal EMS NA Team
19 | NRG (D.S.Mai) | 16 | 2.2.2.1 |  | Various File Uploads: Active power generation profile for all generators; Averaged Energy Offer (AEO) curves for all generators; Seasonal load profiles; Average daily high temperatures (for use in predicting dynamic schedules note: which schedules are these? beyond 21 days), and DC tie schedules. | Clarification Provided* | Nodal EMS NA Team | Suggest a revised wording (w/o the word "schedule") "(for use in predicting dynamic ratings beyond 21 days)"
20 | CNP | 16 | 2.2.2.1 |  | Various File Uploads: Active power generation profile for all generators; Averaged Energy Offer (AEO) curves for all generators; Seasonal load profiles; Average daily high temperatures (for use in predicting dynamic schedules beyond 21 days (it would seem that temperatures vary too widely across the state to use one average temperature to determine dynamic ratings)), and DC tie schedules. | Clarification Provided | Nodal EMS NA Team | The temperatures will be provided per weather zone.
21 | NRG (D.S.Mai) | 16 | 2.2.3 |  | The OE tool consists of the following main functions, as depicted in Figure 2-1: • Case Setup • Power Flow • Contingency Analysis • Priority List Unit Commitment • Secure Generation Profile • Outage Sensitivity Analysis • Outage Cost Calculation • Save Case Management • Display Information Management | Accepted | Nodal EMS NA Team
22 | ERCOT | 13 | 2.3 |  | b. OE shall be based on the simulation of static power system models. Hence, no voltage collapse or transient stability assessments analysis will be made as part of the OE task ------------------------------------------ b. OE shall be based on the simulation of static power system models. Hence, no voltage collapse or transient stability assessments analysis will be made as part of the OE task. | Accepted | Nodal EMS NA Team
23 | CNP | 17 | 2.3 |  | b. OE shall be based on the simulation of static power system models. Hence, no voltage collapse or transient stability assessments analysis will be made as part of the OE task.(Could a solution fail due to voltage collapse? and will there be a distinction made between max iterations and “blown up” cases?) | Clarification Provided | Nodal EMS NA Team | Yes, the solution could fail due to voltage collapse. There should be a distinction between max iterations and the case failing to solve.
24 | NRG (D.S.Mai) | 17 | 2.3 |  | d. It is assumed that the Average Energy Offer curves will be derived through a process external to the OE tool being specified in this document note: where is the derivation described?. OE shall provide a capability to upload this information, and support editing of this data. | Clarification Provided* | Nodal EMS NA Team | Functionality for AEO will be included, and the reference to "outside process, application, etc.) will be removed.
25 | ERCOT | 15 | 3 |  | This section describes detailed functional requirements for OE. These functions correspond to processes P-1 and P-2 of the Level 3 Outage Evaluation diagram (Figure 3-1). Accordingly, the description of required OE functions is divided into two groups that correspond to these two processes. ---------------------------------------------------- This section describes detailed functional requirements for OE. These functions correspond to processes P-1 and P-2 of the Level 3 Outage Evaluation diagram (Figure 3-1). Accordingly, the description of required OE functions is divided into two groups that correspond to these two processes. | Accepted | Nodal EMS NA Team
26 | ERCOT | 15 | 3 |  | Within these groups, a further grouping of functions is performed according to a partition of the OE functionality into logical components as presented in Figure 2-1. As a consequence of these choices, level 2 headings in this section correspond to the blocks of Figure 3-1, and level 3 headings to the blocks of Figure 2-1. -------------------------------------------------------------------------------- Within these groups, a further grouping of functions is performed according to a partition of the OE functionality into logical components as presented in Figure 2-1. As a consequence of these choices, level 2 headings in this section correspond to the blocks of Figure 3-1, and level 3 headings to the blocks of Figure 2-1. | Accepted | Nodal EMS NA Team
27 | ERCOT | 15 | 3 |  | As noted in Section 2.1, the OE implementation does not have to follow this exact model partition for as long as all the specified functions are provided. -------------------------------------------------------------------------------- As noted in Section 2.1, the OE implementation does not have to follow this exact model partition for as long as all the specified functions are provided. | Accepted | Nodal EMS NA Team
28 | CNP | 18 | 3 | Figure 3-1 | Please define “short term” in the statement above? | Clarification Provided* | Nodal EMS NA Team | The "short term" note will be removed.
29 | ERCOT | 16 | 3.1.1 | OS-FR1 | The Case Setup module of the OE function shall be responsible for coordinating the activities required to assemble all study cases in the Study Case Repository that are needed to run outage evaluation over the specified time intervals. ... 1. ... The user (Scheduler) controls the resolution of the study intervals, i.e. several hours per day, or just one, by specifying the desired study dates and hours. --------------------------------------------------- The Case Setup module of the OE function shall be responsible for coordinating the activities required to assemble all study cases in the Study Case Repository that are needed to run outage evaluation over the specified time intervals. ... 1. ... The user (Scheduler) controls the resolution of the study intervals, i.e. several hours per day, or just one, by specifying the desired study dates and hours. | Accepted | Nodal EMS NA Team
30 | Brazos Electric (T.Kroskey) | 19 | 3.1.1 | OS-FR1 | 1. Support analysis of different time periods by providing a capability for the user (Scheduler) to specify desired dates and hours of the study. The studies may extend beyond 100 days into the future. The user (Scheduler) controls the resolution of the study intervals, i.e. several hours per day, or just one, by specifying the desired study dates and hours. | Accepted | Nodal EMS NA Team
31 | Brazos Electric (T.Kroskey) | 19 | 3.1.1 | OS-FR1 | 2. Using the ERCOT mandated technology for interconnecting computer systems, Case Setup shall acquire the data it is responsible for acquiring from the source systems, and store it in the Study Cases repository. After study intervals are specified, Case Setup shall assemble and incorporate into study cases all the data required to support the study., and label the cases in a user meaningful way, at a minimum identifying the intended day and hour of the study, and the time the case was created. | Accepted | Nodal EMS NA Team
32 | LCRA (G.Graham) | 16 | 3.1.1 | OS-FR1 | 4. Case Setup component of OE interacts with the following systems: a. NMMS: NMMS updates validated full network models, associated contingencies, and Dynamic Ratings Static Tables to the Study Case Repository, whose data is then used by OE. b. Outage Scheduler: OE imports from the outage scheduler all approved or accepted Resource Outages submitted more than 8 days ahead of time do not require “approval” but are accepted by ERCOT per Protocols) outages and the outages requested for approval in the desired time intervals. The OE database shall maintain the outage type and the outage’s unique identification to cross reference it to the Outage Scheduler. The detailed information on the outage is maintained in Outage Scheduler and shall be accessible through the outage unique identifier linkage. | Clarification Provided* | Nodal EMS NA Team | Rephrase Item b as follows: "Outage Scheduler: OE imports transmission and resource outages from the outage scheduler that are approved, accepted, or requested to be approved in the desired time intervals."
33 | NRG (D.S.Mai) | 20 | 3.1.1 | OS-FR1 | 4. ... d. EMS: import Load Distribution Factors for the studies within 21 days. Note: State Estimator calculates the Load Distribution Factors for today and tomorrow, according to the SE Requirements document. Which function calculates the Load Distribution Factors from beyond tomorrow to 20 days into the future? | Clarification Provided | Nodal EMS NA Team | Load distribution factors are updated after each SE run. Different distribution factors are computed for week days, for weekends, or holidays. Once computed, they are used for any future studies, i.e. there are no separate participation factors that are computed for days before or and for days after 20 days into the future.
34 | ERCOT | 17 | 3.1.1 | OS-FR1 | f. ….. Beyond this date, to get produce hourly temperatures, OE shall interpolate high and low daily temperatures using seasonal temperature profiles.) ------------------------------------------------------ f. … Beyond this date, to get produce hourly temperatures, OE shall interpolate high and low daily temperatures using seasonal temperature profiles.) | Accepted | Nodal EMS NA Team
35 | CNP | 20 | 3.1.2 | OS-FR2 | 3. Facilities for purging cases from the repository shall be provided (what is the minimum time study cases will be kept?) | Clarification Provided | Nodal EMS NA Team | The duration will be a part of the business rules, and it will not change the OE functional requirements.
36 | NRG (D.S.Mai) | 21 | 3.1.2 | OS-FR2 | 3. Facilities for purging cases from the repository shall be provided | Accepted | Nodal EMS NA Team
37 | Brazos Electric (T.Kroskey) | 20 | 3.1.2 | OS-FR2 | 3. Facilities for purging cases from the repository shall be provide. | Accepted | Nodal EMS NA Team
38 | CNP | 21 | 3.2.1 | OS-FR5 | Description: Multi-case Executive shall have the capability to coordinate outage evaluation tasks required to conduct an analysis for one or multiple time steps, and using a combination of the following major components: • Power Flow • Contingency Analysis • Priority List Unit Commitment (PLUC) • Secure Generation Profile • Outage Cost Calculator (do outage costs and sensitivities apply to both resources and TSP’s?) • Overload Sensitivity Calculator • Outage Cost Sensitivity Calculator. | Clarification Provided | Nodal EMS NA Team | Yes, they apply to both.
39 | CNP | 21 | 3.2.1 | OS-FR5 | It shall also automatically analyze study results in order to extract a summary of the results, identifying: • All time intervals with unresolved security issues • All outages completely contained within intervals that can be accommodated without any violations • Sensitivities of overloads to outages • The expected cost for each of the intervals • Sensitivities of the cost to the outages (ditto above question) • The impact of each outage on the violations, when these can not be avoided. | Clarification Provided | Nodal EMS NA Team | Yes, they apply to both.
40 | Brazos Electric (T.Kroskey) | 21 | 3.2.1 | OS-FR5 | A typical sequence of computations using these components is shown in Figure 2-2 Multi-case Executive shall automatically configure execution sequences appropriate to the data available for each selected interval. For example, for intervals where the unit resource commitment status is available from the Current Operating Plan it may not be necessary to run Priority List Unit Commitment, and hence on these intervals PLUC shall not be selected by default. However, a user interface shall be provided to display the selected execution options for each selected interval, and to allow a change of the options that are consistent with available data. For example, normally Priority List Unit Commitment and Secure Generation Profile will be used to set up the generation profile, but occasionally Scheduler may wish to run Power Flow, to validate or make changes in the case. | Accepted | Nodal EMS NA Team
41 | Brazos Electric (T.Kroskey) | 21 | 3.2.1 | OS-FR5 | A typical sequence of computations using these components is shown in Figure 2-2 Multi-case Executive shall automatically configure execution sequences appropriate to the data available for each selected interval. For example, for intervals where the resource commitment status is available from the Current Operating Plan it may not be necessary to run Priority List Unit Commitment, and hence on these intervals PLUC shall not be selected by default. However, a user interface shall be provided to display the selected execution options for each selected interval, and to allow a change of the options that are consistent with available data. For example, normally Priority List Unit Commitment and Secure Generation Profile will be used to set up the generation profile, but occasionally Scheduler may wish to run Power Flow, to validate or make changes in the case. | Accepted | Nodal EMS NA Team
42 | ERCOT | 19 | 3.2.1.2 | OS-FR4 | Study Contingency Analysis (CA) shall evaluate network security by evaluating the effect of potential outage/innage conditions (“contingencies”) within the modeled power system by disconnecting/connecting reconfiguring power system devices according to the contingency specification, and by solving the resulting network model. Flow and voltage violations shall be evaluated, and the severity of the postulated analyzed contingencies shall be ranked beside based on a suitable reliability ranking criterion. ... -------------------- Study Contingency Analysis (CA) shall evaluate network security by evaluating the effect of potential outage/innage conditions (“contingencies”) within the modeled power system by disconnecting/connecting reconfiguring power system devices according to the contingency specification, and by solving the resulting network model. Flow and voltage violations shall be evaluated, and the severity of the postulated analyzed contingencies shall be ranked beside based on a suitable reliability ranking criterion. ... | Accepted | Nodal EMS NA Team
43 | ERCOT | 19 | 3.2.1.2 | OS-FR4 | CA shall use the cases for one or more pre-specified time intervals. CA shall model and solve for SPS, RAP, load shedding, and load rollover, if the latter ones are triggered, in the simulations to find the post-contingency states. ---------------------------------------------------------------- CA shall use the cases for one or more pre-specified time intervals. CA shall model and solve for SPS, RAP, load shedding, and load rollover, if the latter ones are triggered, in the simulations to find the post-contingency states. | Accepted | Nodal EMS NA Team
44 | ERCOT | 19 | 3.2.1.3 | OS-FR6 | Description: The Priority List Unit Commitment (PLUC) function shall commit energy resources that can supply expected load requirements plus pre-specified reserves for a user-defined study period. The objective of the PLUC function shall be to minimize the total system production cost based on the average energy offer curves. Unit startup/shutdown costs, minimum up/down times, and inter-temporal constraints do not need to be considered. ----------------------------------------------------- Description: The Priority List Unit Commitment (PLUC) function shall commit energy resources that can supply expected load requirements plus pre-specified reserves for a user-defined study period. The objective of the PLUC function shall be to minimize the total system production cost based on the average energy offer curves. Unit startup/shutdown costs, minimum up/down times, and inter-temporal constraints do not need to be considered. | Accepted | Nodal EMS NA Team
45 | Brazos Electric (T.Kroskey) | 24 | 3.2.1.4 | OS-FR7 | · To satisfy base case security criteria. It shall not be necessary to provide an initial generation profile, but if one is provideds, it shall be used. | Accepted | Nodal EMS NA Team
46 | NRG (D.S.Mai) | 24 | 3.2.1.4 | OS-FR7 | • To satisfy security criteria following a given critical contingency. Note that other functions within the OE are responsible for identifying what contingencies are critical, and for providing appropriate models of constraints. In this case the starting point is the generation profile of the secure base case. Generating resources shall be allowed to move from this base case value within a ramp limited range corresponding to a configurable time horizon, initially 15 minutes note: what is the granularity of functions (Unit Commitment, Cost Calculator etc.) supporting OE with a study time period - is it hourly?. | Clarification Provided | Nodal EMS NA Team | Hourly, with the following understanding: the user is able to specify all the dates/hours that comprise an OE study; no temporal coupling exists between the cases, i.e. each of the functions, Unit commitment, Cost Calculation, etc. operates on each of the cases independent of the other cases in the study.
47 | LCRA (G.Graham) | 20 | 3.2.1.4 | OS-FR7 | How are “average energy offers” created for Dynamically Scheduled Generators? | Clarification Provided* | Nodal EMS NA Team | A description of the "Typical Price" calculator function will be added to the OE requirements document.
48 | Brazos Electric (T.Kroskey) | 24 | 3.2.1.4 | OS-FR7 | This function shall also be able to commit VARr resources needed to keep voltages within pre-specified boundaries. | Accepted | Nodal EMS NA Team
49 | ERCOT | 21 | 3.2.1.4 | OS-FR7 | An initial generation profile shall be provided to this program. A user provided time interval, 15 minutes by default, shall be used to compute the bounds on generation (Ramping capability) within which the program shall seek a secure solution. --------------------------------- An initial generation profile shall be provided to this program. A user provided time interval, 15 minutes by default, shall be used to compute the bounds on generation (Ramping capability) within which the program shall seek a secure solution. | Accepted | Nodal EMS NA Team
50 | ERCOT | 20 | 3.2.1.5 | OS-FR8 | Description: Outage Cost Calculator shall calculate the combined cost of accommodating all outages. The cost of outages shall be a difference of two production costs, one obtained for a secure system with all the requested outages accommodated, and the other for a secure system without any of the requested outages but including approved outages. without any of the requested outages. -------------------------------------------------- Description: Outage Cost Calculator shall calculate the combined cost of accommodating all outages. The cost of outages shall be a difference of two production costs, one obtained for a secure system with all the requested outages accommodated, and the other for a secure system without any of the requested outages but including approved outages. without any of the requested outages. | Accepted | Nodal EMS NA Team
51 | Brazos Electric (T.Kroskey) | 24 | 3.2.1.5 | OS-FR8 | Description: Outage Cost Calculator shall calculate the combined cost of accommodating all outages. The cost of outages shall be a difference of twothe production costs, one obtained for a secure system with all the requested outages accommodated, and the production costother for a secure system without any of the requested outages but including approved outages. without any of the requested outages. | Accepted | Nodal EMS NA Team | The stricken part removed.
52 | ERCOT | 21 | 3.2.1.6 | OS-FR9 | Duplicate Requirement ID - see Sec. 3.2.1.7; change Sec. 3.2.1.6 Requirement ID to OS-FR12 | Accepted | Nodal EMS NA Team
53 | Brazos Electric (T.Kroskey) | 25 | 3.2.1.7 | OS-FR9 | Description: Outage Cost Sensitivity Calculator shall calculate sensitivities of the outage cost to each of the approved and requested outages that are analyzed outages approved and requested outages. A summary of results shall be created. It shall be possible to display this summary in a descending order of the impact of outages on the cost. | Accepted | Nodal EMS NA Team
54 | CNP | 25 | 3.2.1.7 | OS-FR9 | Description: Outage Cost Sensitivity Calculator shall calculate sensitivities of the outage cost to each of the analyzed outages approved and requested outages. A summary of results shall be created. It shall be possible to display this summary in a descending order of the impact of outages on the cost. If the cost sensitivity of a previously approved outage is increased by a requested outage - will the approved outage ever be denied in favor of a requested outage? | Clarification Provided | Nodal EMS NA Team | This is a business process consideration. See Protocol 3.1.5.6 (3)
55 | ERCOT | 22 | 3.2.2 | OS-FR10 | 1. … a. For all edits, an “undo” function, or an equivalent means of recovering the starting data shall be provided. ---------------------------------------------- 1. … a. For all edits, an “undo” function, or an equivalent means of recovering the starting data shall be provided. | Accepted | Nodal EMS NA Team
56 | Brazos Electric (T.Kroskey) | 25 | 3.2.2 | OS-FR10 | 1. ... a. For all edits, an “undo” function, or an equivalent means of recovering the starting data shall be provided | Accepted | Nodal EMS NA Team
57 | ERCOT | 22 | 3.2.2 | OS-FR10 | 2. OE shall perform an analysis of the contingency results from all study intervals ... a. The means to organize results by different criteria, including by study interval, by the cost of production, by the magnitude of unresolved security problems, by sensitivity of costs to outages, by the sensitivity of overloads to outages, by solution success or issues, by the number and magnitude of security violations per outage - shall be provided. ------------------------------------------------------- 2. OE shall perform an analysis of the contingency results from all study intervals ... a. The means to organize results by different criteria, including by study interval, by the cost of production, by the magnitude of unresolved security problems, by sensitivity of costs to outages, by the sensitivity of overloads to outages, by solution success or issues, by the number and magnitude of security violations per outage - shall be provided. | Accepted | Nodal EMS NA Team
58 | ERCOT | 23 | 3.2.2 | OS-FR10 | 3. Displays to allow the use of OE results for managing outages shall be provided: a. It shall be possible to assign notes to any of the outages shall be provided. --------------------------------------------- 3. Displays to allow the use of OE results for managing outages shall be provided a. It shall be possible to assign notes to any of the outages shall be provided. | Accepted | Nodal EMS NA Team
59 | CNP | 26 | 3.2.2 | OS-FR10 | 4. The results of the OE shall be available for review, modifications, and navigation to outage details from an OE Dashboard display summary. Will Resources and TSP’s be able to view results via MOTE? | Clarification Provided | Nodal EMS NA Team | The TSP will be able to use the MOTE system. Resources will not have the capability, the information in a study case contains market sensitive information.
60 | CNP | 27 | 3.2.3 | OS-FR11 | Description: ERCOT posts on the MIS Secure Area (when are outages going to be moved from the public to the secure area only?) outages which are pending as well as the ones that are approved, accepted, and rejected based on the outage status in the Outage Scheduler. | Clarification Provided | Nodal EMS NA Team | Not quite sure about the question: the information is posted on the MIS Secure area (not the public area).
61 | ERCOT | 24 | 3.3.1 | Table 3-1 | Mid and Long Term Load Forecast: Mid-Term Hourly (i.e. 24 per day) load forecast (MW) for the period of 8 days. Long-Term Daily load forecast (one per day) for the time period greater than 9 9 days and beyond ----------------------------------------------- Mid and Long Term Load Forecast: Mid-Term Hourly (i.e. 24 per day) load forecast (MW) for the period of 8 days. Long-Term Daily load forecast (one per day) for the time period greater than 9 9 days and beyond | Accepted | Nodal EMS NA Team
62 | ERCOT | 26 | 4.1 | OE-SR1 | Description: A complete run of OE for one time interval, including computation of a Priority List unit commitment and secure economic dispatch base case evaluation shall take no longer than 1 minute.15 seconds. The run time does not include an update of the model by NMMS, but it does include the steps of reading the necessary data from the Study Cases Repository, doing the computations, storing the results back to the Study Cases Repository, and producing any required displays and reports. ... ------------------------------------------ Description: A complete run of OE for one time interval, including computation of a Priority List unit commitment and secure economic dispatch base case evaluation shall take no longer than 1 minute.15 seconds. The run time does not include an update of the model by NMMS, but it does include the steps of reading the necessary data from the Study Cases Repository, doing the computations, storing the results back to the Study Cases Repository, and producing any required displays and reports. ... | Accepted | Nodal EMS NA Team
63 | NRG (D.S.Mai) | 29 | 4.2 | OE-SR2 | Description: The Study Cases repository shall be sized to support at least 100 OE specific static network models, and at least 426 cases note: is this the MOTE?. | Clarification Provided | Nodal EMS NA Team | No, this is an OE internal data repository.

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.