## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For Wind Power Forecasting, Version 0.90
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | TXU Energy Delivery (L.Westbrook) |  |  |  |  | The WGR forecasts should be made available for short-term operations planning. I assume they are, but it is not clear. | Pending | Bill Blevins | Will add statement that the WGR forecasts will be used in both operating and planning horizons where appropriate.
2 | Brazos Electric (T.Kroskey) | 6 | 1 |  |  | The requirements for Texas Nodal market implementation are described in the Texas Nodal Protocols. This document focuses on elaborating the requirements for the Wind Power Forecasting (WPF)Renewable Production Potential (RPP) forecasting process of the Energy Management System. | Pending | Bill Blevins | Agree these requirements refer to the Wind Power Forecasting service. (add to punch list to update EMS requirements documents to update the name from RPP to WPF.)
3 | Brazos Electric (T.Kroskey) | 6 | 1 |  |  | … The WPFRPP is one of these systems. ... … The RPPWPF requirements are documented … | Accepted | Bill Blevins | See S. No 2 reason
4 | Brazos Electric (T.Kroskey) | 6 | 1.1 |  |  | … the external behavior of the RPP forecastingWPF process. … | Accepted | Bill Blevins | See S. No 2 reason
5 | Brazos Electric (T.Kroskey) | 6 | 1.2 |  |  | … set of requirements for the RPP forecastingWPF process … | Accepted | Bill Blevins | See S. No 2 reason
6 | Brazos Electric (T.Kroskey) | 7 | 1.3 |  |  | … requirements for the RPP forecastingWPF process … | Accepted | Bill Blevins | See S. No 2 reason
7 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | All RPPWPF functional requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Process Map that describes the RPP forecastingWPF process. | Accepted | Bill Blevins | See S. No 2 reason
8 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | 2. RenewableWind Power Production Potential The RPPwind power forecasting process is a new ERCOT process that utilizes a combination of ERCOT systems and an external system (wind power production forecasting service) to produce the Short-Term Wind Power Forecasts (STWPF) and derive the Wind-Powered Generation Resource Production Potential (WGRPP). ... | Accepted | Bill Blevins | See S. No 2 reason
9 | Wind Coalition (W. Reid) | 8 | 2 |  |  | The RPP forecasting process is a new ERCOT process that utilizes a combination of ERCOT systems and an external system (wind power production forecasting service) to produce the Short-Term Wind Power Forecasts (STWPF) and derive the Wind-Powered Generation Resource Production Potential (WGRPP). The Long-Term Wind Power Forecasts (LTWPF) are provided by Wind-Powered Generation Resources (WGR) to ERCOT. | Accepted | Bill Blevins | See S. No 2 reason
10 | Wind Coalition (W. Reid) | 8 | 2 |  |  | ... Thus, ERCOT will have an “expected” wind profile for any day of the next year provided by the facility owner, and will have the STWPF for the next 48 hours. … | Accepted | Bill Blevins | Correction of Typo.
11 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | Similarly, the WGRPP is a forecast for the next 48 hours of potential wind power output. Unlike the STWPF however, the WGRPP is not the “expected” wind power, but the facility power output we arewith a 80% confidentce factor the facility will exceed. Mathematically, this condition is described as: | Clarification Provided* | Bill Blevins | The addition of the "potential" term is not needed. The fact that this is a forecast implies that it is only the potential output. The second sentence does add clarification and is accepted.
12 | Wind Coalition (W. Reid) | 8 | 2 |  |  | … ERCOT expects providers facility operators to analyze historic wind speeds for each month to provide a statistical “normal” daily profile for each month, but the methodology used for the LTWPF is outside the scope of this document. | Pending | Bill Blevins | The term used in protocols is "WGR Entities". Add to punch list to change to the "WGR Entities" term used .
13 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | … The RPPWPF process is compromised of several sub-processes:… … The RPPwind power forecasting process requires ... … The RPPwind power forecasting process ... … The RPPwind power forecasting process checks for… | Accepted | Bill Blevins | See S. No 2 reason
14 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | Operational (real-time) data from all generator types is receivedprovided by QSE’s through telemetry byto the ERCOT Energy Management System (EMS). The RPPwind power forecasting process will require additional operational data from wind generators through telemetry. | Accepted | Bill Blevins | First change add clarity. Second change See S. No2 reason.
15 | Wind Coalition (W. Reid) | 8 | 2 |  |  | Operational (real-time) data from all generator types is received through telemetry by the ERCOT Energy Management System (EMS). The RPP forecasting process will may require additional operational data from wind generators through telemetry. Required operational data are will be listed below in Table 1 by the wind-power production forecasting service. | Rejected | Bill Blevins | The RPP forecasting process needs to be changed to WPF (See S. No 13). Second the Wind power production forecasting service has determined what information they will need and it is listed in Table 1 therefore the suggested wording is not correct.
16 | Wind Coalition (W. Reid) | 9 | 2 |  |  | All the aforementioned data inputs (specification data, operational data and unit availability) are provided by ERCOT to the wind power production forecasting service for utilization along with their additional meteorological information. The wind-power production forecasting service will strive to produce the most accurate hourly forecast of total ERCOT wind-power production (minimum dispersion of the probability distribution for each hour), The forecast will consist of two components, a probabilistic hourly forecast of the Total ERCOT wind-power production for each of the next 48 hours and distribution factors for each individual WGR for each of the next 48 hours. The cumulative probability distribution table shall consist of at least 20 points from 5% confidence to 95% confidence that the total ERCOT wind-power production will exceed. It shall not be assumed to be a normal distribution. The distribution factors for each WGR shall be that WGRs proportion of the total ERCOT wind power production for that hour. ERCOT shall use the total ERCOT probabilistic forecast and the WGR distribution factors (which shall total to one) to calculate the STWPF and the WGRPP for each WGR. ... | Rejected | Bill Blevins | This recommendation goes beyond what protocols require and it is not supported further by any specific functional or supplemental requirements. The requirements as written have performance criteria sufficient to require the wind power forecasting service to provide accurate forecast while allowing for flexibility by the service in producing the forecast. It is ERCOT staff opinion that as written the requirements align with the Wind Coalitions comments regarding the forecasting services performance and flexibility requirements.
17 | Wind Coalition (W. Reid) | 9 | 2 |  |  | ... These forecasts are shared with the market as appropriate. A QSE representing a WGR must enter a High Sustainable Limit (HSL) value in their Current Operating Plan that is less than or equal to the amount for that wind farm from the most recent WGRPP provided by ERCOT. The HSL values in the Current Operating Plan provided by QSE’s are inputs to the Reliability Unit Commitment processes. ERCOT shall use the wind-power production forecasting service’s forecast as the basis for inputs to the Reliability Unit Commitment (RUC) process. The WGR inputs to the RUC process may alter the HSL for all WGRs to a different default confidence level or a confidence level selected by the operator. | Rejected | Bill Blevins | Protocol 3.9.1.7 require that ERCOT use the HSL provided by the QSE. A QSE representing a Wind-Powered Generation Resource (WGR) must enter an HSL value that is less than or equal to the amount for that Resource from the most recent Wind-Powered Generation Resource Production Potential (WPGRPP) provided by ERCOT. If there is a need to use the WGR forecasted output then a Protocol Revision can accomplish this change. Operating experience will dictate.
18 | Brazos Electric (T.Kroskey) | 9 | 2.1 |  |  | 2.1 RPPWPF Inputs and Outputs This section provides a summary of inputs and outputs to the Renewable Production Potential forecastingWind Power Forecasting process. Table 1 lists all the required input data from ERCOT to the RPP forecasting WPFprocess. The “Source” column of the input table identifies where the data is provided to the RPPWPF process. ... Table 1 : RPPWPF Process Inputs ... Table 2 lists outputs from the RPP forecastingWPF process to various systems. The “Destination” column of the output table identifies the target for the data generated by the RPPWPF process. ... ... Table 2 : RPPWPF Process Outputs | Accepted | Bill Blevins | See S. No 2 reason
19 | LCRA (G.Graham) | 9 | 2.1 | Table 1 |  | Energy Management System (EMS): 1. Most recent Resource (wind farm) status with date/time 2. Most recent MW output of wind farm with date/time 3. Most recent wind speed and direction at hub height from one meterological tower with date/time 4. Temperature and barometric pressure at 2 m above ground level on the meterological tower Which of these data points is required to be supplied by the QSE? | Clarification Provided* | Bill Blevins | all these values are provide by the QSE to ERCOT.
20 | Wind Coalition (W. Reid) | 10 | 2.1 | Table 1 |  | Energy Management System (EMS): 3. Most recent wind speed and direction at hub height from one meterological tower with date/time (if required by the wind-power production forecasting service) 4. Temperature and barometric pressure at 2 m above ground level on the meterological tower (if required by the wind-power production forecasting service) | Rejected | Bill Blevins | The Forecasting Service Vendor has indicated these points are required. Put on punch list to add a comment that the table 1 data is based upon vendor requirements and that it could be modified based upon the services needs in the future.
21 | Wind Coalition (W. Reid) | 10 | 2.1 | Table 2 |  | Market Information System (MIS): 1. Aggregated STWPF for Total ERCOT wind-power probabilistic production forecast– (Secured Area) 2. STWPF for each WGR (Certified Area) 3. WGRPP for Total ERCOT wind-power production used as the basis for the WGRPP – (Secured Area) 4. WGRPP for each WGR (Certified Area) 5. Total ERCOT wind-power production used as the basis for the RUC – (Secured Area) | Rejected | Bill Blevins | The Table 2 information follows what ERCOT protocols state. Additional information could be provided by the service based upon stakeholder needs but the current protocols state as a minimum the information as written will be provided.
22 | Wind Coalition (W. Reid) | 10 | 2.1 | Table 2 |  | Data Archive (EDW): 1. Aggregated STWPF for ERCOT Total ERCOT wind-power production forecast 5. Actual wind speed, temperature, barometric pressure, and power output from each WGR (if required by the wind-power production forecasting service) | Rejected | Bill Blevins | See S. No 21 reason. Will add a comment that the table 2 data is based upon vendor requirements and that it could be modified based upon the services needs in the future.
23 | TXU (B.Spangler) | 10 | 2.1 | Table 2 |  | {TXU Comment: The RPP process outputs described above do not describe how the WGR information is passed to the RUC and Settlement processes that rely on this data input.} | Clarification Provided | Bill Blevins | The protocol (3.9) states the process where ERCOT gets the information to calculate HASL for RUC is the COP . Protocol 3.9.1.7 requires that ERCOT use the HSL provided by the QSE. A QSE representing a Wind-Powered Generation Resource (WGR) must enter an HSL value that is less than or equal to the amount for that Resource from the most recent Wind-Powered Generation Resource Production Potential (WPGRPP) provided by ERCOT. ERCOT receives the WGR forecast and the WGRPP. The QSE will take this information and update the COP.
24 | Brazos Electric (T.Kroskey) | 10 | 2.2 |  |  | 2.2 RPPWPF Functional Diagrams | Accepted | Bill Blevins | See S. No 2 reason.
25 | Brazos Electric (T.Kroskey) | 11 | 2.2 | Figure 1 |  | Figure 1 Brief description: … Qualified Scheduling Entities representing Wind Generating Resources shall provide to ERCOT the unit availability information through the Current Operating Plan and the Outage Scheduler and operational data from wind farms into the Energy Management System. | Accepted | Bill Blevins | Add clarification
26 | Wind Coalition (W. Reid) | 11 | 2.2 | Figure 1 |  | Figure 1 Brief description: ... The STWPF and WGRPP total ERCOT wind-power probabilistic production forecasts and the WGR distribution factors are calculated by the wind power production forecasting service and sent to ERCOT, who calculates the STWPF, the WGRPP, and the inputs to RUC and makes the forecasts available to RUC the MIS and for archive. The LTWPF information is provided by WGRs to ERCOT and then archived. [PLEASE NOTE – CHANGES TO DIAGRAM ARE REQUIRED TO REFLECT THE ABOVE CHANGES] | Rejected | Bill Blevins | See S. No 16 reason.
27 | Brazos Electric (T.Kroskey) | 12 | 2.2 | Figure 2 |  | Figure 2 Brief description: The Wind Power Production Forecast SystemService (WPPFS) shall ingest the regional weather data, WGR operational data, WGR specification data and WGR de-rating and scheduled outage data. … | Accepted | Bill Blevins | Adds clarification. The diagram description will need to be updated to reflect this language change.
28 | Wind Coalition (W. Reid) | 11 | 2.2 | Figure 2 |  | Figure 2 Brief description: …The regional weather data and the WGR data shall be used to generate the total ERCOT probabilistic production forecast and the WGR distribution factors used by ERCOT to calculate the STWPF and WGRPP forecasts through the use of physics-based and statistical atmospheric models as well as a WGR output model. A 7-year archive of WPPFS forecast data shall be maintained. . [PLEASE NOTE – CHANGES TO DIAGRAM ARE REQUIRED TO REFLECT THE ABOVE CHANGES] | Rejected | Bill Blevins | See S. No 16 reason.
29 | Brazos Electric (T.Kroskey) | 12 | 2.3 |  |  | ERCOT use of the STWPF hourly wind generation forecasts, LTWPF, and WGRPP forecasts depends on the following: ... ● Availability of specification data from registration and operational data from SCADAtelemetry and plans from QSE’s | Accepted | Bill Blevins | Add clarification
30 | Wind Coalition (W. Reid) | 12 | 2.3 |  |  | ERCOT use of the STWPF hourly wind generation forecasts, LTWPF, and WGRPP forecasts depends on the following: ● Changes to the EMS database, registration process, and the Outage Scheduler to include the new operational and meteorological data (if required by the wind-power production forecasting service) | Rejected | Bill Blevins | This will be addressed by completing S. No 20.
31 | Brazos Electric (T.Kroskey) | 13 | 3.1 | RPP-FR1 |  | Description: The RPPwind power forecasting process … … The following shall be used as inputs to the RPPwind power forecasting process … | Accepted | Bill Blevins | See S. No 2 reason
32 | Wind Coalition (W. Reid) | 14 | 3.1 | RPP-FR1 |  | Description: The RPP forecasting process shall produce and update the STWPF (expected valuethe most likely outcome, or center of probability distribution) hourly. Each forecast shall include a probabalistic forecast of hour-ending total ERCOT wind-power MWh output for each of the next 48 hours and distribution factors for each wind farm for each of the next 48 hours. and the aggregate output of all wind farms. The hourly distribution factors are each WGRs proportion of the total ERCOT production for that hour. The sum of all the WGR distribution factors for each hour shall total to 1.0000. | Rejected | Bill Blevins | See S. No 16 reason.
33 | Brazos Electric (T.Kroskey) | 13 | 3.2 | RPP-FR2 |  | Description: The RPPwind power forecasting process shall produce … | Accepted | Bill Blevins | See S. No 2 reason
34 | Wind Coalition (W. Reid) | 14 | 3.2 | RPP-FR2 |  | Description: The RPP process shall produce and update a WGRPP, which is a hourly forecasted power production estimate that has an 80% probability of exceedance (i.e. 80% confidence factor) from the STWPF. Each WGRPP forecast shall be produced by selecting the appropriate total ERCOT confidence forecast (currently 80%) and then multiplying by the WGR distribution factors . The WGRPP forecast shall include an hour-ending MWh value for each of the next 48 hours for each WGR and the aggregate of all WGR’s total ERCOT wind-power production. | Rejected | Bill Blevins | Note: The RPP process needs to be changed to WPF (See S. No 33). Second see S. No 16 reason.
35 | Brazos Electric (T.Kroskey) | 14 | 3.3 | RPP-FR3 |  | Description: The RPPwind power forecasting process shall accept … | Accepted | Bill Blevins | See S. No 2 reason
36 | Brazos Electric (T.Kroskey) | 14 | 3.4 | RPP-FR4 |  | 3.4 RPPWPF Data Posting ... Description: The RPPWPF process shall make available … | Accepted | Bill Blevins | See S. No 2 reason
37 | Wind Coalition (W. Reid) | 15 | 3.4 | RPP-FR4 |  | Description: The RPP process shall make available the following data to QSEs and for posting on the MIS: ● STWPF for each WGR to each associated QSE (MIS Certified Area) ● Total ERCOT wind-power probabilistic production forecasts (cumulative progability table for each hour of the next 48 hours) Aggregated STWPF for ERCOT (MIS Secured Area) ● WGRPP for each WGR to each associated QSE (MIS Certified Area and Messaging System) ● Aggregated WGRPP for Total ERCOT wind-power production used as the basis for the WGRPP ERCOT (MIS Secured Area) ● Total ERCOT wind-power production used as the basis for the RUC – (Secured Area) | Rejected | Bill Blevins | The RPP process needs to be changed to WPF (See S. No 36). Second see S. No 16 reason.
38 | Brazos Electric (T.Kroskey) | 14 | 3.5 | RPP-FR5 |  | Description: The RPPWPF process shall make available … | Accepted | Bill Blevins | See S. No 2 reason
39 | Wind Coalition (W. Reid) | 16 | 3.5 | RPP-FR5 |  | Description: The RPP process shall make available for archive the actual hourly wind generation and actual hourly meterological data used for the forecast as well as the actual hourly meterological data of each WGR site (if required by the wind-power production forecasting service) for at least 7 years. | Rejected | Bill Blevins | The RPP process needs to be changed to WPF (See S. No 38). Secondly this data is to be archived according to protocols requirements therefore no change in wording is required.
40 | LCRA (G.Graham) | 14 | 3.5 | RPP-FR5 |  | Description: The RPP process shall make available for archive the actual hourly wind generation and actual hourly meterological data of each WGR site for at least 7 years. Who is expected to supply this data? | Clarification Provided* | Bill Blevins | The RPP process needs to be changed to WPF (See S. No 38). Secondly ERCOT will store the data that it receives for each WGR site. The supplier of "actual" data is the QSE via telemetry from the WGR site. The provider of "forecasted" data is the Wind Power Forecasting service.
41 | Brazos Electric (T.Kroskey) | 15 | 3.6 | RPP-FR6 |  | 3.6 RPPWPF Forecasts Archive ... Description: The RPPWPF process shall make available | Accepted | Bill Blevins | See S. No 2 reason
42 | Wind Coalition (W. Reid) | 16 | 3.6 | RPP-FR6 |  | Description: The RPP process shall make available for archive all total ERCOT probabilistic production data, WGR distribution factors, STWPF data, LTWPF data and WGRPP forecast data for at least 7 years. | Rejected | Bill Blevins | The RPP process needs to be changed to WPF (See S. No 41). Secondly, see S.No. 16 for the reason for rejection.
43 | Wind Coalition (W. Reid) | 17 | 4.1 | RPP-SR1 |  | Description: At-least one valid, as defined in Data Validation requirements, WGRPP forecast for each Operating Day shall be available to ERCOT from the wind power production forecasting service, by 0600 of the Day-Ahead, 99.8% of the time, yearly | Rejected | Bill Blevins | Written so that the Short Term Wind Power Forecast (STWPF) must provide the WGRPP Wind Generation Resource Production Potential as part of the STWPF for the day ahead so that ERCOT may post the WGRPP as required by protocols 4.2.2 (2) and 4.2.2(3) .
44 | Brazos Electric (T.Kroskey) | 16 | 4.2 | RPP-SR3 |  | Description: The RPPWPF Pprocess shall calculate … | Accepted | Bill Blevins | See S. No 2 reason
45 | Wind Coalition (W. Reid) | 17 | 4.2 | RPP-SR3 |  | Description: The RPP Process shall calculate statistics comparing the forecasts to the actual total ERCOT wind-power output and the output of wind farms. These statistics shall include mean forecast, mean actual, mean error (bias), absolute mean error, RMS error, and a measure of dispersion (probably standard deviation) for total ERCOT wind-power production and each WGR for each hour-of-day by month for a set of specific forecast “lead times” (probably the 1600 forecast with a 8 hour lead time examinining the following day). | Accepted | Bill Blevins | Add clarification
46 | Wind Coalition (W. Reid) | 17 | 4.3 | RPP-SR4 |  | Description: The STWPF shall meet the following accuracy criteria: The expected value of the total ERCOT wind-power production forecast used as the basis for the STWPF has an absolute mean error for the Day-Ahead forecast (the latest forecast prior to 0600 for all the hours in the next calendar day), over a calendar month, that is less than 4% | Pending | Bill Blevins | As written the WGR is statistically bound to meet performance criteria to meet aggregate and local (Farm) ERCOT needs. This recommendation adds a performance metric on the day ahead forecast for TPTF consideration this is listed as pending. Also the vendor believes the term absolute mean error may be too wide an error band. Their feeling is that an absolute error of 4% would be better than the 4% absolute mean error. If this were to be adopted.
47 | Brazos Electric (T.Kroskey) | 16 | 4.3 | RPP-SR4 |  | … less than 18% of its maximum capability. | Accepted | Bill Blevins | Correction of Typo.
48 | Wind Coalition (W. Reid) | 18 | 4.3 | RPP-SR5 |  | Description: The WGRPP shall meet the following accuracy criteria: The actual total ERCOT wind-power output of each WGR is less than the expected value of the total ERCOT wind-power production forecast used as the basis for the WGRPP produced in Day-Ahead, between 15% and 25% of the hours, over a calendar six month period | Rejected | Bill Blevins | The suggested changes restrict the services focus and would not be in ERCOT's benefit. As written the service is more flexible while meeting protocol requirements.
49 | Brazos Electric (T.Kroskey) | 17 | 4.3 | RPP-SR5 |  | … over a calendar six month period. | Accepted | Bill Blevins | Correction of Typo.
50 | Wind Coalition (W. Reid) | 18 | 4.3 | RPP-SR6 |  | … wind speed forecast from an ERCOT designated vendor … | Accepted | Bill Blevins | Correction of Typo.
51 | Brazos Electric (T.Kroskey) | 17 | 4.3 | RPP-SR6 |  | … supply the generated wind speed forecasts to ERCOT . | Accepted | Bill Blevins | Correction of Typo.
52 | Wind Coalition (W. Reid) | 18 | 4.4 | RPP-SR7 |  | Description: ● The vendors wind power production forecasting service shall support a total ERCOT probabilistic production STWPF self-training mode to train or re-train the Wind Power Model for each WGR based on the historical wind generation and meteorological data used for the forecastfor each WGR site. ● The vendors wind power production forecasting service shall support a self-training mode for each WGR’s distribution factor to train or re-train the Wind Power Model based on the historical wind generation and meteorological data used for the forecast. | Rejected | Bill Blevins | The suggested changes restrict the services focus and would not be in ERCOT's benefit. A training mode will be supported and the extent of the method of training the service is to deliver will be determined in the detail design. As written the service is more flexible while meeting protocol requirements.
53 | Wind Coalition (W. Reid) | 19 | 4.5 | RPP-SR8 |  | Description: The output of WGRPP RPP shall be validated to ensure that the forecasted MWh values are valid: that is they are non-negative and with in the maximum capability of each WGR. | Accepted | Bill Blevins | See S. No 2 reason (this means ERCOT will accept the change but use the term agreed upon in response to Comment S. No 2)
54 | Brazos Electric (T.Kroskey) | 17 | 4.5 | RPP-SR8 |  | Description: The output of WGRPP shall be validated to ensure that the forecasted MW values are valid:, that is they are non-negative and with in the maximum capability of each WGR. If the data is invalid, last valid forecast shall be provided, indicating the condition with a flag and potentially reason. | Accepted | Bill Blevins | accept typo correction. Also recommend striking the word "potential".
55 | Brazos Electric (T.Kroskey) | 18 | 4.6 | RPP-SR10 |  | Description: ERCOT Operators shall have the capability to view RPPwind power forecasts … | Accepted | Bill Blevins | See S. No 2 reason

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.