Texas Nodal

<Project Name>

Software Requirements Specification

For Outage Scheduler

Version 0.10

19 January, 2007

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 08/03/2006 | 0.01 | New document based on template version 1.2 for requirements and use case specification | ABB Outage Scheduler Team |
| 08/25/2006 | 0.02 | R. Matlock (ERCOT) and ABB-generated changes. Template version 1.2 | ABB Outage Scheduler Team |
| 08/30/2006 | 0.03 | R. Matlock updated FRs | Robert Matlock |
| 09/01/2006 | 0.04 | R. Matlock removed use cases | Robert Matlock |
| 10/25/2006 | 0.05 | New document based on template version 1.4 received from ERCOT on 23 October and ERCOT feedback till October 24, 2006 | ABB Outage Scheduler Team |
| 11/02/2006 | 0.06 | Reintroduced FR1-5, FR1-6, FR1-7, FR1-8, FR1-9, FR1-11, and FR3-3. Incorporated changes recommended by ERCOT as of November 02, 2006 | ABB Outage Scheduler Team |
| 11/14/2006 | 0.07 | Incorporated changes recommended by ERCOT as of November 13, 2006 | ABB Outage Scheduler Team |
| 11/21/2006 | 0.08 | Incorporated changes recommended by ERCOT including those from the IDA as of November 21, 2006 | ABB Outage Scheduler Team |
| 01/09/2007 | 0.09 | Incorporated ERCOT and TPTF comments and recommended changes – summarized in e-mail from Venkat Gajjela on January 8, 2007 – including the removal of FR1-7 and FR1-11 (i.e., Disable Continuous Outage and Convert Tentative Outage, respectively) | ABB Outage Scheduler Team |
| 01/19/2007 | 0.10 | Incorporated changes recommended by ERCOT and input provided by ABB and discussed with ERCOT in telephone conversation on January 18, 2007 (Robert Matlock and the ABB team) – This document includes red-lining for all changes since version 0.08 (draft 0.09 and 0.10) | ABB Outage Scheduler Team |

Document Approval

| Date | Approved/ Rejected | Approved/Rejected By | Signature (indicate if electronic approval) |
| --- | --- | --- | --- |
|  |  | <Name> <Role> |  |

Table of Contents

1.	Introduction	6

1.1	Purpose	6

1.2	Objective	6

1.3	Traceability	6

1.4	Definitions and Acronyms	6

2.	System Scope	7

2.1	As Is Sub-Process for the Outage Scheduler System	7

2.2	To Be Sub-Process for the Outage Scheduler System	7

2.3	Differences between the As Is and To Be Sub-Process	8

2.4	Assumptions and Dependencies	8

3.	Functional Requirements	9

3.1	External Client Requirements	10

3.1.1	FR1-1 Submit Outage Request	10

3.1.2	FR1-2 Edit Outage Request	12

3.1.3	FR1-3 Cancel Outage Request	12

3.1.4	FR1-4 Create Outage Extension	12

3.1.5	FR1-5 Create Recurring Outages	13

3.1.6	FR1-6 Copy Existing Outage	13

3.1.7	FR1-7 Create Opportunity Outage	15

3.1.8	FR1-8 Create Outage Group	15

3.1.9	FR1-9 Respond to Warning (External Client)	16

3.2	Internal ERCOT Requirements	16

3.2.1	FR2-1 Study Outage	16

3.2.2	FR2-2 Approve, Accept or Reject Outage	17

3.2.3	FR2-3 Withdraw Outage	17

3.2.4	FR2-4 Respond to Warning	18

3.2.5	FR2-5 Manage Unit Relationship	18

3.2.6	FR2-6 Perform Privileged Operations	19

3.3	Information Exchange Requirements	19

3.3.1	FR3-1 Post Outage Information	19

3.3.2	FR3-2 Expose Outage Information	20

3.3.3	FR3-3 Export Outage Data	21

3.3.4	FR3-4 Import Transmission Element Names	21

3.3.5	FR3-5 Programmatic Interface	22

3.4	Administration Requirements	23

3.4.1	FR4-2 Manage Users and Roles	23

3.4.2	FR4-3 Manage Outage Versions	23

4.	Supplementary Requirements	24

4.1	SR-1 Performance Requirements	24

4.2	SR-2 Legal and Regulatory Requirements	24

4.3	SR-3 System and Communication Requirements	25

4.4	SR-4 System Security Requirements	25

4.5	SR-5 Back Up and Recovery Requirements	25

4.6	SR-6 Availability and Redundancy Requirements	25

4.7	SR-7 Maintainability Requirements	25

4.8	SR-8 Training and Documentation Requirements	25

4.9	SR-9 Usability Requirements	26

4.10	SR-10 Use of Rules Engine	26

5.	Protocol Coverage	27

6.	Sub-Process Coverage	31

A.	Definitions and Acronyms	32

A.1	Definitions	32

A.2	Acronyms	35

B.	Outage Life-Cycle Matrix	37

C.	Outage State Transitions	38

D.	Configurable Rules	41

D.1	User Role Rules	41

D.2	Validation Rules for Submitting Outages	41

D.3	Submittal Time Line Rules	42

D.4	Outage Editing Rules	42

D.5	State/Status Rules	42

D.6	Outage Extension Rules	43

D.7	Outage ID and Version Tracking Rules	43

D.8	User Preferences Rules	43

E.	Outage Submission and Approval Requirements and Guidelines	44

Software Requirements Specification

(This Requirements Document is Subordinate to and Compliant with the Texas Nodal Protocols effective May, 2006.)

# Introduction

The primary authority directing the operational characteristics and behavior of the Outage Scheduler system is the Texas Nodal Protocols.  This requirements document is provided as a supplement to assist in the implementation of this system which includes all processes, tools (hardware and software), and operations and constraints necessary for full compliance to the Texas Nodal Protocols.  The Texas Nodal Protocols with this set of requirements documents completes the System “Design To” definition for implementation, test, and operation of a fully compliant Market Management System.

## Purpose

The requirements for the document Texas Nodal Market Management Systems (MMS) Requirement Specification for Outage Scheduler and its associated processes are described in the Texas Nodal Protocols.  This supplemental specification describes the external behavior of this specific sub-system.  The Texas Nodal Protocols (Protocols) and this document together with all applied vendor provided products’ functional specifications, describe both functional and nonfunctional requirements, design constraints, and other factors, in order to provide a complete and comprehensive description of the operational performance to be delivered.  All statements or requirements specified in this document are subordinate to the Protocols.

## Objective

The objective of this set of documents is to provide a clear, concise and unambiguous set of requirements together with the Texas Nodal Protocols which provides the complete required technical description of this Texas Nodal Sub-System to allow the developer/implementer to deliver a fully operational, compliant and robust Texas Nodal System.

## Traceability

All requirements are traceable to the Nodal Protocols, and/or regulations such as NERC and FERC.

## Definitions and Acronyms

A definition of terms and acronyms used in this document is provided in Appendix A.  This list is exclusive of those defined in the “ERCOT Nodal Protocols Section 2: Definitions and Acronyms, May 2006”.

# System Scope

This section describes the As Is and To Be sub-processes of the Outage Scheduler system. ERCOT has provided the Outage Scheduler team with two sub-process maps, as illustrated in Figure 1 and Figure 2. Figure 1 demonstrates the As Is sub-process, while Figure 2 demonstrates the To Be sub-process.

## As Is Sub-Process for the Outage Scheduler System

The current sub-process for managing Outages is illustrated in the As Is sub-process in Figure 1. Activities within the Outage Scheduler are highlighted with dashed borders.

Outage management activities lead to the creation of an updated Outage Schedule.

The Transmission Network Model, Load Forecast, and Generation Plan together with the Approved Outages are used to evaluate any security or reliability violation linked to the requested Outage(s). If there are no violations, the Outage Request(s) are accepted and the Outage Schedule is updated. Actual Market Operational Data, Estimated Market Data, Registration Data, and Additional Adjustments are input into the Outage Scheduler process.

Figure 1: As Is sub-process for managing Outage activities

## To Be Sub-Process for the Outage Scheduler System

Figure 2 illustrates the To Be sub-process for the Outage Scheduler system. In the process diagram below, each process or information source which is hosted by the Outage Scheduler application is labeled “Outage Scheduler” in parentheses. Activities within the Outage Scheduler are represented in the process P-4 and output of the Outage Scheduler is illustrated by the box labeled I-6. The dashed boxes (I-2, P-4 and I-6) represent the Outage Scheduler. Light yellow color (lighter shade) indicates existing processes and dark yellow color (darker shade) indicates new processes.

The TSP or QSE (i.e., the Outage Requestor) submits Outage Requests using the Outage Scheduler. The ERCOT Outage Coordinator creates a Date Determinate Power Flow Model, which includes Approved, Accepted, and Requested Outages, Generation Plan, and Load Forecast. The ERCOT Outage Coordinator then uses this model to perform Contingency Analysis.

For most Scheduled Outages, if any requested Outage under evaluation causes pre or post contingent limit violations, the ERCOT Outage Coordinator consults with the Outage Requestor and determines if there is an acceptable solution (i.e., remedial action, generation adjustment, etc). If an acceptable solution exists, the Outages will be Approved or Accepted, if not, the Outage will be Rejected or Withdrawn and rescheduled at a better time.

Figure 2: To Be sub-process for managing Outage activities

## Differences between the As Is and To Be Sub-Process

The To Be sub-process includes Power Flow Analysis for evaluation of the requested Outage(s) using Energy and Ancillary Market Data and Current Operating Plan information in place of what is Generation Plan data in the As Is sub-process.

## Assumptions and Dependencies

Outage Scheduler is a critical application that maintains Transmission and Resource Element availability information. Accuracy and availability of this information to such systems as EMS, MMS and CRR (through the NMMS) is essential for ERCOT market operation. The requirements and assumptions regarding availability, security, performance, and information accessibility for the Outage Scheduler are described in the following chapters in this document.

# Functional Requirements

This section contains the Functional Requirements for the Outage Scheduler system.

The Functional Requirements have been grouped according to the view of the user. The first group – External Client Requirements - focuses on the originator of an Outage - the Transmission Service Provider (TSP), the Qualified Scheduling Entity (QSE), and ERCOT acting on behalf of or in coordination with either. The second group – Internal ERCOT Requirements - focuses on the role of ERCOT itself and how Outage Requests are managed by ERCOT. The third group – Information Exchange Requirements - deals with the acceptance and dissemination of Outage data. Finally the fourth group – Administration Requirements - deals with general administrative issues in the system, not directly involved with the submission and management of Outages.

The numbering convention for the Functional Requirements is “FR”, followed by the group number and the intra-group requirement number separated by a dash. For example, FR1-1 addresses the first requirement in the group of External Client Requirements.

To assist in understanding the Requirements Specification document, the following background information is provided.

ERCOT, as an Independent System Operator (ISO) for a large portion of Texas, is required to review and approve, accept or reject Transmission and Resource Outages. The criterion for approval, acceptance, or rejection is adherence with NERC Transmission Security Standards and ERCOT protocols and guidelines. ERCOT has developed and is continuing to develop tools to assist Outage Coordinators in evaluating the transmission security impact of Outages. These tools are described in a companion requirement document “Texas Nodal Energy Management System Requirements Specification for Outage Evaluation”. The Outage Scheduler application described in this document is the operational interface between participants, particularly TSPs and QSEs and Outage Coordination personnel at ERCOT.

## External Client Requirements

### FR1-1 Submit Outage Request

| Requirement ID | FR1-1 |
| --- | --- |
| Protocol Reference | NP Section 3.1.2, 3.1.3.1, 3.1.3.2, 3.1.4.2, 3.1.4.8, 3.1.5.1, 3.1.5.2, 3.1.5.9, 3.1.5.12, 3.1.6, 3.1.6.1, 3.1.6.2, 3.1.6.8, 3.1.7, NERC Standards IRO-002-1, TOP-003-0, TOP-004-0, TOP-005, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Full – NP section 3.1.2 Partial – all others |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: Each TSP and QSE shall have the ability to submit to ERCOT their Outage Elements in a timeframe that is a function of the Outage Category and Type. TSPs shall be permitted to submit Outage Requests within the Transmission Category, while QSEs shall be permitted to submit Outage Requests within the Resource Category (Generation and Load). Refer to Appendix A.1 for Transmission Outage Types. A Forced Extension can only be created from an original Forced Outage that cannot be submitted as a Planned Outage according to ERCOT protocol time lines. Unavoidable Extension can only be created from an original Planned or Maintenance Outage that cannot be submitted as a Planned or Maintenance Outage according to ERCOT protocol time lines. Outage submission time lines according to ERCOT protocols are listed in Appendix E, Table 3. When creating an Outage on a Transmission Element, the TSP shall have the capability of choosing from a list of associated switches and/or breakers for that Transmission Element. The data required to populate these selection lists is provided by the NMMS to the Outage Scheduler. Refer to Appendix A.1 for Resource Outage Types. Planned Outages are handled differently, whether they are submitted eight days or less, or more than eight days. A Forced Extension can only be created from an original Forced Outage that cannot be submitted as a Planned Outage according to ERCOT protocol time lines. Unavoidable Extension can only be created for an original Planned or Maintenance Outage that cannot be submitted as a Planned or Maintenance Outage according to ERCOT protocol time lines. Outage submission time lines according to ERCOT protocols are listed in Appendix E, Table 3. Opportunity Outages are a special category of Planned Outages and are described in FR1-7. The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): - Identification of primary and alternate telephone numbers for the TSP Single Point of Contact, the name of the individual submitting the Outage Request (i.e., Outage Requestor), and location (i.e., TSP) - The identification of the Transmission Facility (i.e., From Station) - Identification of any other Transmission Facility that must be out of service to facilitate the Outage Request, in terms of an existing Outage ID (???or - equipment IDs) - A description of the nature of work to be performed during the proposed Transmission Outage. A drop-down box with a predefined set of work description options shall be provided, as well as a free-text box for further explanation (i.e., Requestor Notes and Supporting Information) - Identification of Equipment and Equipment Type - Normal and Outage States (if the Transmission Element is a CB, DSC, DISC, LS, or MOS) - Planned Start and End Date/Time - Earliest Start and Latest End Date/Time - The time required to: (i) terminate the Outage, and (ii) restore the Transmission Facility to normal operation (i.e., Emergency Restoration Time) - Identification of any remedial actions or special protection systems necessary during this Outage and the contingency that will require the remedial action or relay action - The following information shall be provided in an Outage Request for the Resource Category (varies somewhat based on Outage Category): - Identification of primary and alternate telephone numbers for the QSE Single Point of Contact, the name of the individual submitting the Outage Request (i.e., the Outage Requestor), and location (i.e., QSE) - The identification of the Resource Facility (i.e., Station Name) - A description of the nature of work to be performed during the proposed Resource Outage. A drop-down box with a predefined set of work description options shall be provided, as well as a free-text box for further explanation (i.e., Requestor Notes and Supporting Information) - Identification of Equipment and Equipment Type - Highest Sustainable Limit (HSL) available during the Outage - Lowest Sustainable Limit (LSL) available during the Outage - Planned Start and End Date/Time - Earliest Start and Latest End Date/Time Outage Types and Categories and their life cycle are summarized in the Life-Cycle Matrix in Appendix B. The matrix summarizes the various states for each Outage Category and Type. Allowed state transitions for Outages are depicted in the State Transition Diagram in Appendix C. When ERCOT Outage Coordinator (EOC) enters an Outage Request on behalf of or in coordination with a TSP or QSE, after choosing the TSP or QSE, the OS shall provide the capability and corresponding authorization for entering the Outage. A User Interface for use of external users shall be provided. |  |

### FR1-2 Edit Outage Request

| Requirement ID | FR1-2 |
| --- | --- |
| Protocol Reference | NP Section 3.1.3.1, 3.1.4.2, 3.1.4.8, 3.1.5.2, 3.1.6.1, 3.1.6.4, 3.1.6.8, 3.1.6.9, 3.1.6.10, 3.1.7, 3.1.7 2, NERC standard IRO-002, IRO-005-1, TOP-003-0, TOP-004-0, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: A TSP and a QSE shall be permitted to Edit an Outage submitted on behalf of the same requesting company whenever any information concerning that Outage changes or ERCOT requires modification and/or re-submission. The ability to edit an Outage and the properties that can be edited depend on the Outage Type and the state of the Outage. Any changes to an Outage will require resubmission to ERCOT (and therefore also revalidation). All changes to an Outage, which are submitted to ERCOT are tracked through version control as covered in FR4-3.The Outage states that allow the Edit operation are illustrated in the State Transition Diagram in Appendix C. |  |

### FR1-3 Cancel Outage Request

| Requirement ID | FR1-3 |
| --- | --- |
| Protocol Reference | NP Section 3.1.4.2, 3.1.7, 3.1.4.8, NERC Standard IRO-002, IRO-005-1, TOP-003-0, TOP-004-0, TOP-005,TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The originator – an Outage Requestor – or someone acting on his/her behalf shall be permitted to Cancel an Outage Request, if the need for the request no longer exists. Cancellation must occur before the Outage is Active, hence before Planned Start Date/Time has past. The Cancel operation for any Outage is summarized in the Life-Cycle Matrix in Appendix B. Allowed state transitions from the various Cancel states are depicted in the State Transition Diagram in Appendix C. |  |

### FR1-4 Create Outage Extension

| Requirement ID | FR1-4 |
| --- | --- |
| Protocol Reference | NP Section 3.1.4.6, 3.1.4.8, 3.1.5.2, 3.1.6.1, 3.1.6.8, 3.1.6.9, 3.1.6.10, 3.1.7, NERC Standard IRO-002, TOP-003-0, TOP-004-0, TOP-005, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: A TSP or QSE shall have the capability to extend an Outage if it is not possible to complete the Outage by the Planned End Date/Time. There shall be two types of extensions: - Forced Extension –for extending a Forced Outages - Unavoidable Extension –for extending a Planned or Maintenance Outages and where the extension is requested less than three days before the Planned End Date/Time |  |

### FR1-5 Create Recurring Outages

| Requirement ID | FR1-5 |
| --- | --- |
| Protocol Reference | NP Section 3.1.3.2(1) , NERC Standards IRO-002, IRO-005-1, TOP-003-0, TOP-004-0, TOP-005, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The TSP or QSE shall have the capability to create an Outage Request that recurs on a daily basis from a Planned Outage when it is created. The duration of the original Outage Request shall not exceed 24 hours. The Outage Request shall include: Start Date/Time of the original copy, End Date/Time of the last copy, interval in days between each copy, and a maximum number of recurring Outages. The maximum number of recurring Outages shall be set to default 50. This action creates multiple Outage Requests, one for each contiguous period, and no more than 50 for each Recurring Outage Request. |  |

### FR1-6 Copy Existing Outage

| Requirement ID | FR1-6 |
| --- | --- |
| Protocol Reference | NP Section 3.1.3.2(1) , NERC Standards IRO-002, IRO-005-1, TOP-003-0, TOP-004-0, TOP-005, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: A TSP or QSE shall have the capability to copy an existing Outage. The copy shall be identical to the original but subject to user modification of any of the following fields: For Transmission Outages: - Identification of primary and alternate telephone numbers for the TSP Single Point of Contact, the name of the individual submitting the Outage Request (i.e., the Outage Requestor), and location (i.e., the TSP) - The identification of the Transmission Facility (i.e., the From Station) - Identification of any other Transmission Facility that must be out of service to facilitate the Outage Request, in terms of an existing Outage ID (?? Or equipment IDs??) - A description of the nature of work to be performed during the proposed Transmission Outage. A drop-down box with a predefined set of work description options shall be provided, as well as a free-text box for further explanation (i.e., Requestor Notes and Supporting Information) - Identification of Equipment and Equipment Type - Normal and Outage States (if the Transmission Element is a CB, DSC, DISC, LS, or MOS) - Planned Start and End Date/Time - Earliest Start and Latest End Date/Time - The time required to: (i) terminate the Outage, and (ii) restore the Transmission Facility to normal operation (i.e., Emergency Restoration Time) - Identification of any remedial actions or special protection systems necessary during this Outage and the contingency that will require the remedial action or relay action - For Resource Outages: - Identification of primary and alternate telephone numbers for the QSE Single Point of Contact, the name of the individual submitting the Outage Request (i.e., the Outage Requestor), and location (i.e., the QSE) - The identification of the Resource Facility (i.e., the Station Name) - A description of the nature of work to be performed during the proposed Resource Outage. A drop-down box with a predefined set of work description options shall be provided, as well as a free-text box for further explanation (i.e., Requestor Notes and Supporting Information) - Identification of Equipment and Equipment Type - Highest Sustainable Limit (HSL) available during the Outage - Lowest Sustainable Limit (LSL) available during the Outage - Planned Start and End Date/Time - Earliest Start and Latest End Date/Time |  |

### FR1-7 Create Opportunity Outage

| Requirement ID | FR1-7 |
| --- | --- |
| Protocol Reference | NP Section 3.1.5.5, 3.1.6.8 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: Each TSP and QSE shall have the ability to submit to ERCOT an Opportunity Outage. Every Opportunity Outage shall be associated with a Resource Planned or Resource Maintenance Outage. Two types of Opportunity Outages exist, one for Resource Outages and one for Transmission Outages. A QSE shall be able to submit a Resource Opportunity Outage for an already Approved or Accepted Planned or Maintenance Outage of the same Resource if a Forced Outage on the Resource occurs within eight days of the Planned or Maintenance Outage. A TSP shall be able to submit a Transmission Opportunity Outage tied to an already Approved or Accepted Resource Planned or Maintenance Outage. The TSP shall use the respective Resource Outage ID to designate the Resource Outage to its requested Transmission Opportunity Outage. The Outage Scheduler shall verify that the Transmission Opportunity Outage Planned Start/End Date/Time fall within the Planned Start/End Date/Time of the designated Resource Outage. In case of any request for change to the designated Resource Outage, Outage Scheduler shall issue a warning to that effect to all parties involved (ERCOT Outage Coordinator and the respective TSP and QSE). The resolution of the requested change to the designated Resource Outage and its impact on the respective Transmission Opportunity Outage shall be handled by the ERCOT Outage Coordinator and involved TSP and QSE. |  |

### FR1-8 Create Outage Group

| Requirement ID | FR1-8 |
| --- | --- |
| Protocol Reference | NP Section 3.1.3.1, IRO-002, TOP-003-0, TOP-004-0, TOP-005, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The TSP shall have the capability to create an Outage Group. An Outage Group shall be produced using an original non-‘Equipment Status Change’ Transmission Outage to create multiple copies with different affected Transmission Elements that share a common Start and End Date/Time. The resulting Outages shall be bound together as an Outage Group. When creating an Outage on a Transmission Element the TSP shall have the capability of choosing from a list of associated switches and/or breakers for that Transmission Element. Outages for those switches and/or breakers shall be created automatically and all Outages shall be bound together (i.e., the Original Transmission Outage plus the associated switches and breaker Outages) as an Outage Group. |  |

### FR1-9 Respond to Warning (External Client)

| Requirement ID | FR1-9 |
| --- | --- |
| Protocol Reference | NP Section 3.1.3.1 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The following events shall cause warning conditions to be brought to the attention of a TSP or QSE: - Planned Start Date/Time has passed and no Actual Start Date/Time has been entered - Thirty minutes before a Planned End Date/Time and no Actual End Date/Time has been entered - Actual End Date/Time has been entered for a Forced Outage, but no supporting text information has been entered - The combination of Resource and Transmission Opportunity Outages The TSP or QSE shall respond to a warning by entering the required missing information and acknowledging the warning. The TSP or QSE shall have a means of viewing unacknowledged warnings. |  |

## Internal ERCOT Requirements

### FR2-1 Study Outage

| Requirement ID | FR2-1 |
| --- | --- |
| Protocol Reference | NP Section 3.1.5.2, 3.1.5.11, 3.1.6.1, 3.1.7 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The ERCOT Outage Coordinator shall be provided the ability to change the status of an Outage with the status of Received at ERCOT to a status of Study. Once an Outage has a status of Study, the TSP or QSE shall not be able to edit the Outage. The set-to-Study operation for any Outage is summarized in the Life-Cycle Matrix in Appendix B. Allowed state transitions from the Study state are depicted in the State Transition Diagram in Appendix C. |  |

### FR2-2 Approve, Accept or Reject Outage

| Requirement ID | FR2-2 |
| --- | --- |
| Protocol Reference | NP Section 3.1.1, 3.1.4.3, 3.1.4.4, 3.1.4.5, 3.1.4.7, 3.1.5.1, 3.1.5.3, 3.1.5.4, 3.1.5.5, 3.1.5.6, 3.1.5.7, 3.1.5.8, 3.1.5.10, 3.1.5.11, 3.1.6, 3.1.6.3, 3.1.6.5, 3.1.6.6, 3.1.6.7, 3.1.7, 3.1.7.1, , IRO-005-1, TOP-003-0, TOP-004-0, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The capability for the ERCOT Outage Coordinator to Accept, Approve or Reject an Outage (in either Received at ERCOT or Study state) shall be provided. The capability for the ERCOT System Operator to Accept, Approve or Reject Maintenance Level 1 Outage Requests shall be provided. The Accept, Approve or Reject operations for any Outage are summarized in the Life-Cycle Matrix in Appendix B. Allowed state transitions from the Approve, Accept, or Reject states are depicted in the State Transition Diagram in Appendix C. The Accept, Approve or Reject operation shall be handled through an ERCOT approved interface. |  |

### FR2-3 Withdraw Outage

| Requirement ID | FR2-3 |
| --- | --- |
| Protocol Reference | NP Section 3.1.5.7, IRO-005-1, TOP-003-0, TOP-004-0, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The ERCOT Outage Coordinator and System Operator shall be provided a means to withdraw Outages. The withdrawal operation for any Outage is summarized in the Life-Cycle Matrix in Appendix B. Allowed state transitions from the Withdrawn state are depicted in the State Transition Diagram in Appendix C. |  |

### FR2-4 Respond to Warning

| Requirement ID | FR2-4 |
| --- | --- |
| Protocol Reference | NP Section 3.1.4.2, 3.1.4.5 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The Outage Scheduler will produce warnings brought to the attention of ERCOT Outage Coordinators and System Operators for the following events: - Entry of Actual Start Date/Time for Forced, Forced Extension, Unavoidable Extension, Maintenance Level 1-3, Equipment Status Change (ESC), or Outages being monitored (i.e., Monitored Outages) - Entry of Actual End Date/Time for Forced, Forced Extension, Unavoidable Extension, Maintenance Level 1-3, ESC, or Outages being monitored - Cancellation of an Outage being monitored - Submission of Maintenance Level 1-3 Transmission and Resource Outages The ERCOT Outage Coordinator and System Operator shall have the ability to respond to warnings through a process called Acknowledgement. The ERCOT Outage Coordinator and System Operator shall have a means of viewing unacknowledged warnings at any time during operation of the Outage Scheduler. A Monitored Outage is an Outage that has a monitor flag activated as part of its Outage properties. Real-time monitoring of Outages causes warnings to be generated in the Outage Scheduler. An Outage that is being monitored will generate warnings if the Outage is Canceled or if the Actual Start or End Date/Time of the Outage is entered. |  |

### FR2-5 Manage Unit Relationship

| Requirement ID | FR2-5 |
| --- | --- |
| Protocol Reference | NP Section 3.1.1(2d) , 3.1.4.3 IRO-005-1, TOP-003-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The ERCOT Outage Coordinator shall be provided the ability to designate Resources as RMR or Black Start Reliability Resources and specify an affective and termination date. Reliability Resources shall follow the business rules for Reliability Resource, instead of Non-Reliability Resources. These business rules are described in the ERCOT Nodal Protocols sections 3.1.4.3; 3.1.6; 3.1.7; 3.1.14. |  |

### FR2-6 Perform Privileged Operations

| Requirement ID | FR2-6 |
| --- | --- |
| Protocol Reference | NP Section 3.1.1, 3.1.4.3, 3.1.4.5, IRO-005-1, TOP-003-0, TOP-004-0, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: There shall be a privileged role called the OS Admin Role (OAR) that enables a user granted that role to perform all operations of the ERCOT Outage Coordinator and operations not allowed by any other role. These privileged operations shall be: - Change or delete the Actual Start Date/Time, except for Forced Outages. If Actual Start Date/Time is deleted and Actual End Date/Time was also entered, the Actual End Date/Time is deleted too - Change or delete the Actual End Date/Time after a Two-Hour Editing Window has passed. If an Actual End Date/Time is deleted, the system shall check for a conflicting Outage that may have been created within 24 hours after the Actual End Date/Time was entered for this Outage. If it finds a second Outage has been submitted for this Transmission Element, the OAR shall not be permitted to delete the Actual End Date/Time - Cancel an Outage due to error or Date/time expiration after Actual Start Date/Time has been entered, and before Actual End Date/Time has been entered (e.g., while the Outage is Active) - Change status from Withdrawn to Accepted or Approved (e.g., an “undo” operation) - Change status from Rejected to Received at ERCOT (e.g., an “undo” operation) - Change status from Canceled to Received at ERCOT, Accepted or Approved (e.g., an “undo” operation) The OS Admin Role privilege of changing Outage states or “undo” operations are summarized graphically in Appendix C. The state diagram completely illustrates an Outage’s allowed states and transitions, including the Cancel states. Appendix B illustrates the Life-Cycle Matrix and highlights which Outages the OS Admin Role can edit with privileges. |  |

## Information Exchange Requirements

### FR3-1 Post Outage Information

| Requirement ID | FR3-1 |
| --- | --- |
| Protocol Reference | NP Section 3.1.1, 3.1.3.1, 3.1.5.7, 3.1.5.13, 3.2.1, 3.2.2, 3.2.3 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The Outage Scheduler shall provide a means of posting Outage information to the Market Information System (MIS) Secure Area. This information shall include all information provided by the Outage Requestor and the following: - Monthly and annual statistics on how TSP Planned Outages compare with actual TSP Outages - Monthly statistics on how Resource Planned Outages compare with actual Resource Outages - Notice of Outage approval withdrawals within one hour of withdrawal - Proposed Transmission Facilities Outages neither Approved nor Rejected within one hour of receipt - Approved, Accepted or Rejected Transmission Outage within one hour of approval, acceptance or rejection - Proposed and Approved schedules for Planned Outages and Maintenance Outages of Transmission Facilities - Notice of withdraws of approval of Planned Outages and Maintenance Outages of Transmission Facilities within one hour of the change - Daily posting by 06:00 of aggregated Resource Outage schedules showing the MW of Outages and the MW capabilities for each hour for the next 14 days - Daily postings by 06:00 of aggregated Resource Outage schedules showing the MW of Outages and the MW capabilities available on peak for the next 12 months |  |

### FR3-2 Expose Outage Information

| Requirement ID | FR3-2 |
| --- | --- |
| Protocol Reference | NP Section 5.5.1, 5.5.1, 5.5.2, 7.5, 7.5.5.4, IRO-005-1, TOP-003-0, TOP-004-0, TPL-002-0, TPL-003-0, TPL-004-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The Outage Scheduler shall provide Outage information to other subsystems as specified by those subsystems. These subsystems shall include: - Energy Management System (EMS) - Network Market Management System (NMMS) - Congestion Revenue Right (CRR) System - Planning Applications - Any other component requiring knowledge of Outages |  |

### FR3-3 Export Outage Data

| Requirement ID | FR3-3 |
| --- | --- |
| Protocol Reference | NP Section 3.1.3.2 (1) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: ERCOT Outage Coordinators and System Operators shall have the ability to filter for a subset of Outages using any fields in FR1-1 as filter criteria. This subset of Outages shall be able to be exported by the user in an XML or CSV format. |  |

### FR3-4 Import Transmission Element Names

| Requirement ID | FR3-4 |
| --- | --- |
| Protocol Reference | NP Section 3.10, 3.10.1 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: The Outage Scheduler shall have the ability to import names and effective dates of any Transmission Element that can be subject to Outage. The ability to import all pertinent Transmission Elements in their entirety shall be supported, both periodically and at the request of an ERCOT Outage Coordinator. For each Transmission Element, the following information shall be imported: - Transmission Element name - Unique identifier for the Transmission Element - Transmission Element Type - Normal status of switching devices - Station in which the Transmission Element resides - Acronym for the Station Name - Owner of the Transmission Element - Operator of the Transmission Element - Resource HSL - Resource LSL - Resource Type - Voltage of the Transmission Element - ID/Names of all circuit breakers or switches required to Outage the Transmission Element - Transmission Element in/out-service Date/Time In order to support validation of entry or modification of the Single Point of Contact for a QSE or TSP, access to the Master File information is required. It is assumed that this information and the breakers/switches-Transmission Element relationship data are imported from the NMMS. The ability shall also be provided to import all Transmission Element changes since the last full import, both periodically (e.g., after midnight daily) and at the request of an ERCOT Outage Coordinator. If the name by which a Transmission Element is known can change over the Transmission Elements lifetime, then accompanying the name and effective dates shall be some unique nameplate identifier that never changes over the Transmission Elements lifetime. In the latter case, import of a Transmission Element whose name changes shall cause an update in all known Outages pertaining to that Transmission Element of the Transmission Element name. |  |

### FR3-5 Programmatic Interface

| Requirement ID | FR3-5 |
| --- | --- |
| Protocol Reference | NP Section 3.1.4.2 |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: Two sets of programmatic interfaces shall be provided: - A programmatic interface shall be provided to TSPs and QSEs to import and export Outage data in XML format at their request. The data that they provide in the upload to the Outage Scheduler shall conform to the requirements for Outage submission (i.e., FR1-1). The OS shall perform all of the validity checking that would be performed through the OS User Interface. The results of the upload, in terms of which Outages were accepted and which failed validation and were not accepted (along with the reasons for failure) shall be made available to the Outage Requestor in XML format. - A programmatic interface shall be provided for the EMS to transfer the results of Outage study evaluation into the Outage Scheduler (list of proposed Outages that passed the evaluation and those that failed). |  |

## Administration Requirements

### FR4-2 Manage Users and Roles

| Requirement ID | FR4-2 |
| --- | --- |
| Protocol Reference | NP Section 3.10.8.4(a), 3.1.4.1, NERC Standard CIP-003-1 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: A secure mechanism (Digital Certificates) of logging into the Outage Scheduler shall be provided. For audit trail and authentication purposes, each user of the system shall login with a Digital Certificate and a password. Each user (TSP, QSE, ERCOT, etc.) must acquire or be granted their appropriate roles. The role assigned to the user then determines what actions that user is entitled to perform (e.g., OS Admin Role). |  |

### FR4-3 Manage Outage Versions

| Requirement ID | FR4-3 |
| --- | --- |
| Protocol Reference | NP Section 3.1.3.1 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | P4 |
| Sub-Process Element Coverage | Partial |
| Description: Each Outage shall be recognized by an identifier that contains a unique Outage ID and a version number. A new version of an Outage shall be automatically created on initial submission and any subsequent action that changes any Outage attribute (e.g., Edit, Withdraw, etc.). Any operation to an Outage shall be saved to a new state of the Outage. At any time, all versions of an Outage shall be viewable. |  |

# Supplementary Requirements

The Supplementary Requirements capture the system requirements that are not fully captured in the Functional Requirements. Such requirements include:

  - Legal and regulatory requirements, including application standards

  - Quality attributes of the system to be built, including usability, reliability, performance, and supportability requirements

  - Other requirements such as operating systems and environments, compatibility requirements, and design constraints

In the following, the Supplementary Requirements are given an ID (SR-1 through SR-9) for ease of cross referencing.

## SR-1 Performance Requirements

Outage data shall be made available to other systems within the secured ERCOT enterprise.  To date no mechanism has been fully defined as to how this will be implemented.  Until that occurs, the language used in this document to define such requirements is “X” will be made available to system “Y”.  For example, Outage transactions within a time window need to be made available to the MMS system. We assume at this point that the Outage data will be available incrementally (periodic or on demand) or fully (daily or on demand).

The Outage Detection application in the EMS shall have up-to-date information on Forced Outages within ten seconds of when changes to the ERCOT System have occurred. Changes received in the Outage Scheduler shall be made available to the Outage Detector within a ten second window.

It is assumed that there are ~ 3100 authorized Outage Requestors (TSPs, QSEs, etc.) and at most 75 of them are active at any given time.

## SR-2 Legal and Regulatory Requirements

The Outage Scheduler must conform to the “ERCOT Nodal Protocols – Section 3: Management Activities for the ERCOT System, May 2006”.

The following NERC standards shall be followed through operating procedures:

  - “Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled Outages of system voltage regulating equipment such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors etc. among affected Balancing Authorities and Transmission Operators as required.”

  - “Each Transmission Operator, Balancing Authority and Generator Operator shall plan and coordinate scheduled Outages of Telemetering and Control Equipment and associated communication channels between the affected areas.”

## SR-3 System and Communication Requirements

The current average number of Outages per day is about 120 with maximum of 40,000 Outages per year. Based on input from ERCOT, there are some Outages that may have up to 20 versions or more. However, 5 to 8 may be a more common number of versions of an Outage. This specification assumes there are 8 versions for each Outage on the average. The system shall keep the information available on the Outage Scheduler for two years after the Planned End Date/Time.

The networks and links must use the TCP/IP protocol to transfer data.

## SR-4 System Security Requirements

The system shall provide Public Key Infrastructure (PKI) based security using digital certificate for authentication. The system shall provide a centralized mechanism for maintaining user accounts and authorization information based on the LDAP. The system must provide built-in Cyber Security.  HTTPS shall be used for secure communication between the web server and the web clients.  Hard-coded IP addresses and host files must not be used.  The application must be able to move from one server to another without a required code change and must be portable.  There shall not be any hard-coding of accounts or passwords.

## SR-5 Back Up and Recovery Requirements

The Outage Scheduler system shall include solutions for disaster recovery and business continuity.

## SR-6 Availability and Redundancy Requirements

The Outage Scheduler system is a critical business system spanning data collection in the planning time frame through to power system data presentation for real-time operation. The Outage Scheduler system shall be available for real time power system operation on a continual basis. The system shall use proven and reliable IT architecture. The system must achieve an operational availability of a least 99.95% (i.e., at most ~4.38 hours unavailability per year).

## SR-7 Maintainability Requirements

Since regulatory and business requirements may change, the Outage Scheduler shall be modifiable by making system parameters available for update by GUI.  In addition, the Outage Scheduler must lend itself to additions and modifications to the User Interface, as operational requirements are also subject to change.

## SR-8 Training and Documentation Requirements

The Outage Scheduler system shall include comprehensive documentation including:

  - Software Requirements Specification

  - Conceptual System Design

  - Detailed System Design

  - Data Model Definition

  - User’s Guide

  - Documentation for the underlying Market Infrastructure software

Since the staff of both Outage Requestors and ERCOT Outage Coordinators and System Operators evolves over time, ERCOT needs to be self sufficient in their ability to implement an ongoing User Training Program. User-level training shall be provided to ERCOT with the goal of empowering ERCOT trainers to implement their user-level training program.

Internal training shall be provided to ERCOT to enable ERCOT to eventually take over the maintenance of the Outage Scheduler.

## SR-9 Usability Requirements

The Outage Scheduler shall be designed and built to meet the requirements of the Texas Nodal Protocols and other requirements that are in this document. In addition, the Outage Scheduler user interface shall follow ERCOT guidelines on screen layout, menu structures, and other screen design factors.

Data entry actions that require significant processing time prior to display update shall indicate to the user that processing is in progress. The user experience shall not be impaired by the solution responsiveness. Users shall know whether the system is processing normally, waiting for input (from the current user or any other roles that must interact with the user’s task) or otherwise in a locked up or frozen situation. The solution shall allow for multiple users to simultaneously view the same information.

## SR-10 Use of Rules Engine

The Outage Scheduler shall have a rule-based engine and ERCOT shall be able to modify certain types of rules as needed.  Appendix D provides a description of the types of rules that can be implemented in the rules engine, where not restricted or limited by higher priority design requirements.

# Protocol Coverage

Table 1 lists the extent of coverage (Full/Partial) of all relevant Nodal Protocols that are mentioned in this Requirements Specification document. In summary, this specification fully covers the Nodal Protocols.

Table 1: Nodal Protocol Coverage

| Protocol Sub-Section # (To the lowest level of granularity as possible) | Description | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
| 3.1 | Outage Coordination | N/A |
| 3.1.1 | Role of ERCOT | Full: FR2-2, FR2-5, FR2-6, FR3-1 |
| 3.1.2 | Planned Outage or Maintenance Outage Data Reporting | Full: FR1-1, FR4-2 |
| 3.1.3.1 | Transmission Facilities | Full: FR1-1, FR1-2, FR3-1, FR4-3 |
| 3.1.3.2 | Resources | Full: FR1-1, FR1-5, FR1-6, FR1-7, FR1-8, FR1-9, FR1-11, FR3-3 |
| 3.1.4.1 | Single Point of Contact | Partial: FR4-1, Full: FR4-2 |
| 3.1.4.2 | Method of Communication | Full: FR1-1, FR1-2, FR2-4, FR1-3, FR3-5 |
| 3.1.4.3 | Reporting for Planned Outages and Maintenance Outages of Resources and Transmission Facilities | Full: FR2-2, FR2-5, FR2-6 |
| 3.1.4.4 | Communicating Rejection of Proposed Resource Outages | Full: FR2-2 |
| 3.1.4.5 | Management of Resource or Transmission Forced Outages or Maintenance Outages | Full: FR2-2, FR2-4, FR2-6 |
| 3.1.4.6 | Notice of Forced Outage or Unavoidable Extension of Planned or Maintenance Outage Due to Unforeseen Events | Full: FR1-4, FR2-1 |
| 3.1.4.7 | Outage Coordination of Forecasted Emergency Conditions | Full: FR2-2 |
| 3.1.4.8 | Deratings | Full: FR1-1, FR1-2, FR1-3, FR1-4 |
| 3.1.5.1 | ERCOT Evaluation of Planned Outage and Maintenance Outage of Transmission Facilities | Full: FR1-1, FR2-2 |
| 3.1.5.2 | Receipt of TSP Requests by ERCOT | Full: FR2-1 |
| 3.1.5.3 | Timelines for Response by ERCOT for TSP Requests | Full: FR2-2 |
| 3.1.5.4 | Delay | Full: FR2-2 |
| 3.1.5.5 | Opportunity Outage of Transmission Facilities | Full: FR2-2 |
| 3.1.5.6 | Rejection Notice | Full: FR2-2 |
| 3.1.5.7 | Withdrawal of Approval and Rescheduling of Approved Planned Outages and Maintenance Outages of Transmission Facilities | Full: FR2-2, FR2-3, FR3-1 |
| 3.1.5.8 | Priority of Approved Planned Outages | Full: FR2-2 |
| 3.1.5.9 | Information for Inclusion in Transmission Facility Outage Requests | Full: FR1-1 |
| 3.1.5.10 | Additional Information Requests | Full: FR2-2 |
| 3.1.5.11 | Evaluation of Transmission Facility Planned Outage or Maintenance Outage Requests | Full: FR2-1, FR2-2 |
| 3.1.5.12 | Submittal Timeline for Transmission Facility Outage Requests | Full: FR1-1 |
| 3.1.5.13 | Transmission Report | Full: FR3-1 |
| 3.1.6 | Outages of Resources Other than Reliability Resources | Full: FR1-1, FR2-2 |
| 3.1.6.1 | Receipt of Resource Requests by ERCOT | Full: FR1-1, FR1-2, FR1-4, FR2-1 |
| 3.1.6.2 | Resources Outage Plan | Full: FR1-1 |
| 3.1.6.3 | Additional Information Requests | Full: FR2-2 |
| 3.1.6.4 | Approval of Changes to a Resource Outage Plan | Full: FR1-2 |
| 3.1.6.5 | Evaluation of Proposed Short-Noticed Resource Outage | Full: FR2-2 |
| 3.1.6.6 | Timelines for Response by ERCOT for Resource Outages | Full: FR2-2 |
| 3.1.6.7 | Delay | Full: FR2-2 |
| 3.1.6.8 | Opportunity Outage | Full: FR1-1, FR1-2, FR1-4 |
| 3.1.6.9 | Outage Returning Early | Full: FR1-2, FR1-4 |
| 3.1.6.10 | Resource Coming Online | Full: FR1-2, FR1-4 |
| 3.1.7 | Reliability Resource Outages | Full: FR1-1, FR1-2, FR1-3, FR1-4, FR2-1, FR2-2 |
| 3.1.7.1 | Timelines for Response by ERCOT on Reliability Resource Outages | Full: FR2-2 |
| 3.1.7.2 | Changes to an Approved Reliability Resource Outage Plan | Full: FR1-2 |
| 3.2.1 | Calculation of Aggregate Generating Capacity | Full:FR3-1 |
| 3.2.2 | Long-Term Demand Forecasts | Full: FR3-1 |
| 3.2.3 | System Adequacy Report | Full: FR3-1 |
| 3.10 | Network Operations Modeling and Telemetry | Partial: FR3-4 |
| 3.10.1 | Time Line for Network Operations Model Change Request | Partial: FR3-4 |
| 5.1 | Introduction | Partial: FR3-2 |
| 5.5.1 | Security Sequence | Partial: FR3-2 |
| 5.5.2 | Reliability Unit Commitment (RUC) Process | Partial: FR3-2 |
| 7.5 | CRR Auctions | Partial: FR3-2 |
| 7.5.5.4 | Simultaneous Feasibility Test | Partial: FR3.2 |
| NERC IRO-005-1 | Reliability Coordination — Current Day Operations | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-5, FR2-6, FR3-2 |
| NERC PER-004-0 | Reliability Coordination — Staffing | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-6, FR3-2 |
| NERC TOP-001-0 | Reliability Responsibilities and Authorities | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-6, FR3-2 |
| NERC TOP-003-0 | Planned Outage Coordination | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-5, FR2-6, FR3-2 |
| NERC TOP-004-0 | Transmission Operations | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-6, FR3-2l |
| NERC TPL-002-0 | System Performance Following Loss of a Single Bulk Electric System | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-6, FR3-2 |
| NERC TPL-003-0 | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-6, FR3-2 |
| NERC TPL-004-0 | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | Partial FR1-1, FR1-2, FR1-3, FR1-4, FR1-5, FR1-6, FR1-7, FR1-8, FR2-2, FR2-3, FR2-6, FR3-2 |
| NERC CIP-003-1 | Cyber Security — Security Management Controls | Partial FR4-2 |
| PUCT CH 25.361 (16) | Electric Reliability Council of Texas | Full/All |

# Sub-Process Coverage

Table identifies the extent of coverage (Full/Partial) for all Outage Scheduler sub-processes that are mentioned in this Requirements Specification document.

Table 2: Sub-Process Coverage

| Sub-Process ID | Sub-Process Name | Coverage by Requirements (Full/Partial) |
| --- | --- | --- |
| P4 | Create Up-dated Outage Schedule | Full |

# Definitions and Acronyms

For other definitions and acronyms, see the “ERCOT Nodal Protocols Section 2: Definitions and Acronyms, May 2006”.

## Definitions

| Active Outage | This is one of the states of an Outage. It is NOT an Outage Type. An Active Outage has Planned or Actual Start Date/Time of today or earlier and no Actual End Date/Time value yet. If an Outage has a Planned or Actual End Date/Time of yesterday or earlier, it is not considered Active |
| --- | --- |
| Equipment | A Transmission Element or Resource in the ERCOT System |
| Equipment Status Change | Any real-time switching that will be opened or closed to relieve or prevent an overload condition |
| ERCOT Outage Coordinator | An ERCOT role in the Outage Scheduler. EOC is responsible for daily operation of the OS and has more privileges than ESO, but less than OAR |
| ERCOT System Operator | An ERCOT role in the Outage Scheduler. The ESO prime responsibility lies outside the Outage Scheduler. However, for real-time events such as Forced Outages, the ESO has some OS operational privileges |
| Forced Extension | An extended Outage of either Forced or Maintenance Level 1-3 |
| Monitored Outage | This is one of the attributes of an Outage. It is NOT an Outage Type. A Monitored Outage is an Outage that has the monitor flag activated as part of its Outage properties. Real-time monitoring of Outages causes warnings to be generated in the Outage Scheduler. An Outage that is being monitored will generate warnings if the Outage is Canceled or if the Actual Start or End Date/Time of the Outage is entered |
| Non-Reliability Resource | A type of Resource that does not have a Reliability Must Run (RMR) or Black Start Contract with ERCOT |
| OS Admin Role | An ERCOT role in the Outage Scheduler, usually a Senior Outage Coordinator, with privileges to correct mistakes that are entered into the OS. OAR has all the ERCOT role privileges to OS, exclusive to both EOC and ESO |
| Outage Category | There are two Outage Categories: (1) Transmission and (2) Resources. |
| Outage Group | The binding of two or more Outages together so that the Outages share common Date/Time entries as well as note entries or changes |
| Outage Request | A proposed Outage submitted for scheduling by ERCOT. The proposed Outage needs to be Accepted or Approved (if not Rejected) once Received at ERCOT, except for Forced Outages that are always accepted by ERCOT. |
| Outage Requestor | A TSP, QSE, or ERCOT acting on behalf of either |
| Outage Status | The various states of an Outage in the Outage Scheduler system are listed below. The state of an Outage defines the status of the Outage. The states are depicted graphically and described more comprehensively in the Outage State Transition Diagram in Appendix C: - Entered – Not Yet Submitted - Received at ERCOT - Accepted - Approved - Canceled - Canceled – Will Not Reschedule - Canceled – Reschedule Within One Month - Canceled – Reschedule Next Season - Canceled – Reschedule, Date Unknown - Canceled – Coordinating With ERCOT - Canceled – Error - Rejected - Study - Withdrawn - Opportunity - Active - Extension - Forced Extension - Unavoidable Extension - Pending - Completed – Editable - Completed – Not-Editable |
| Outage Types | For each Outage Category, there are several Outage Types. For Resources the following Outage Types are available: - Forced Outage - Forced Extension - Unavoidable Extension - Maintenance - Maintenance Level 1 - Maintenance Level 2 - Opportunity - Maintenance Level 3 - Opportunity - Planned - Planned Outage Non-Reliability > 8 days - Planned Outage Non-Reliability < 8days - Opportunity - Planned Outage Reliability - Opportunity For Transmission the following Outage Types are available: - Equipment Status Change - Forced Outage - Forced Extension - Unavoidable Extension - Maintenance - Maintenance Level 1 - Maintenance Level 2 - Opportunity - Maintenance Level 3 - Opportunity - Planned Transmission Outage - Opportunity - Simple Transmission Outage |
| Planned End Date/Time | The Date and Time the Outage Requestor intends on ending the Outage |
| Planned Start Date/Time | The Date and Time the Outage Requestor intends on starting the Outage |
| Reliability Resource | A Resource that has ether a RMR contract or a Black Start Contract with ERCOT |
| Resource | A term used to refer to both a Generation Resource and a Load Resource. Resource used by itself does not include a Non-Modeled Generator |
| Resource Category | Resource Outage Types available to the QSE, EOC, OAR, and ESO |
| Scheduled Outage | An Outage Request that has been Accepted or Approved by ERCOT |
| Single Point of Contact | All communications concerning a Outages must be between ERCOT and the designated “Single Point of Contact” for each TSP or QSE. The Single Point of Contact must be either a person or a position available seven days per week and 24 hours per day for each QSE and TSP |
| Transmission Category | Transmission Outage Types available to the TSP, EOC, OAR, and ESO |
| Two-Hour Editing Rule/Window | Actual End Date/Time may be edited within a two-hour window after the Actual End Date/Time has been entered |
| Unavoidable Extension | Unavoidable extensions may only be created for Accepted or Approved, Active Outages. If an Outage is not Accepted or Approved and Active, the option to create an extension is not possible. An Unavoidable Extension occurs when a Planned Outage is not completed within the original timeframe and the Outage Requestor submits the extension less than three days before the Planned End Date/Time. |

## Acronyms

| CCB | Change Control Board |
| --- | --- |
| EOC | ERCOT Outage Coordinator |
| ESC | Equipment Status Change |
| ESO | ERCOT System Operator |
| HTML | HyperText Markup Language |
| HTTP | HyperText Transfer Protocol |
| HTTPS | HTTP Secure |
| IDA | Integration Design Authority |
| ISO | Independent System Operator |
| LDAP | Lightweight Directory Access Protocol |
| NOMCR | Network Operations Model Change Request |
| OAR | OS Admin Role |
| OR | Outage Requestor |
| OS | Outage Scheduler (system) |
| PKI | Public Key Infrastructure |
| XML | eXtensible Markup Language |

# Outage Life-Cycle Matrix

Figure 3: Outage Life-Cycle Matrix

# Outage State Transitions

The various states for an Outage are described in Table 2 and illustrated in Figure 4.

Table 2: Outage State Description

| State | Description |
| --- | --- |
| Entered – Not Yet Submitted | The Outage has been entered into the Outage Scheduler, but has not yet been submitted |
| Received at ERCOT | Outages that are not automatically Accepted are initially Received at ERCOT, before they transition into another state |
| Accepted | An Outage Request that has been scheduled – different from the Approved state - depending on the Outage Type (see the Life-Cycle Matrix in Appendix B) |
| Approved | A Outage Request that has been scheduled - different from the Accepted state - depending on the Outage Type (see the Life-Cycle Matrix in Appendix B) |
| Canceled – Will Not Reschedule | An Outage that has been Canceled by the Outage Requestor and will not be rescheduled |
| Canceled – Reschedule Within One Month | An Outage that has been Canceled by the Outage Requestor and will be rescheduled within a month |
| Canceled – Reschedule Next Season | An Outage that has been Canceled by the Outage Requestor and will be rescheduled next season |
| Canceled – Reschedule, Date Unknown | An Outage that has been Canceled by the Outage Requestor and will be rescheduled, but date is unknown |
| Canceled – Coordinating With ERCOT | An Outage that has been Canceled by the Outage Requestor and will be rescheduled in coordination with ERCOT |
| Canceled – Error | An Outage that has been Canceled by the ERCOT Outage Coordinator due to errors |
| Rejected | An Outage Request that has been Rejected |
| Study | An Outage Request that has been assigned the Study status. Once in the Study state, the Outage is locked for any editing by the Outage Requestor |
| Withdrawn | An Outage can be withdrawn by ERCOT at any time before it has a status of Completed, thus until End Date/Time has been entered |
| Active | An Active Outage has Planned or Actual Start Date/Time of today or earlier and no Actual End Date/Time value yet |
| Opportunity | Designation of a Resource Planned or Maintenance Outage as an Opportunity Outage allows the Planned Start/End Date/Time to be editable. |
| Extension | When an Outage cannot be completed within Planned End Date/Time, its End Date/Time can be “extended.” There are two types of Outage extensions: - Forced Extension for Forced Outages - Unavoidable Extension for Planned and Maintenance Outages |
| Pending | A Forced Outage is “pending” when the Actual End Date/Time is enetered without Supporting Information |
| Completed – Editable | The Two-Hour Editing Window/Rule applies |
| Completed – Not-Editable | The final stage of an Outage. Once in this state editing of the Outage is no long possible |

Figure 4: Outage State Transition Diagram

# Configurable Rules

This section describes the types of rules that shall be configurable in the Outage Scheduler system using a rules engine or other methods of validation. It should be noted that while the actual implementation shall follow the specified requirements as a guideline, there could be cases where some rules are not implemented in the rules engine to conform to generic rules engine capabilities, to avoid complexity of the implementation, and/or to address higher priority design criteria.

## User Role Rules

The notion of users and roles will be reflected within the whole Outage Scheduler system. Typically, role configuration is not done in the rules engine. Users and roles will be set up and configured in the Directory Server using Lightweight Directory Access Protocol (LDAP). Any user and role issues not settled through LDAP will be passed on to the rules engine.

Examples of such rule sets include:

  - ERCOT Outage Coordinator

  - ERCOT System Operator

  - OS Admin Role

  - TSP

  - QSE

  - Operations Support

## Validation Rules for Submitting Outages

Examples of such rule sets include:

  - Required Fields

  - Existing Outage – no Outage overlap exists on a Transmission Element

  - Transmission Element in/out-service Date/Time

For the “Required Fields”, the Outage Scheduler provides three methods for Outage Submission: (1) A User Interface and (2) An XML-file upload interface, and (3) A Web Services Interface. All three methods provide configurable validation of submitted data including Required Fields and their contents. The validation is through an XML-schema validation method where fields are defined as optional or required.

For an “Existing Outage”, the verification that a new Outage does not overlap with existing Outages of the same Transmission Element is an inherent part of Outage Scheduler functionality and is performed by invoking a general purpose utility function for checking overlaps of a given set of transaction periods.

For “Transmission Element in/out-service Date/Time”, when a new Outage has been submitted, the validation should confirm that the Transmission Element is available during the time frame the Outage is requested, by comparing with NMMS imported information. The validation should also include the station/company/nodes verification.

## Submittal Time Line Rules

Examples of such rule sets include:

  - Date/Time Entry Rules

    - Planned Start Date/Time (e.g., a Planned Transmission Outage must be submitted greater than or equal to three days from the current date)

    - Earliest Start Date/Time

    - Planned End Date/Time

    - Latest End Date/Time

    - Actual Start Date/Time  (e.g., a Planned Transmission Outage Actual Start Date/Time must be less than or equal to current time and after the Outage has been Approved)

    - Actual End Date/Time

The above rules are configured using different validation methods as they are of different nature. Some of these rules are integral part of the User Interface (e.g., requirement for entering the Actual Start Date/Time of an Outage before entering its Actual End Date/Time) while other rules are more amenable to implementation in a rules engine. Examples of rules that are easily configurable within a rules engine are:

  - A Planned Transmission Outage must be submitted greater than or equal to 3 days from the current date. The number of days can be configured to any value within an acceptable range for this specific rule (e.g., from 3 to 4 days).

  - A Planned Transmission Outage Actual Start Date/Time must be less than or equal to current time and after the Outage has been Approved. The reference date/time can be any reasonable value.

## Outage Editing Rules

These rules address “who”, “what” and “when” aspects of editing an Outage. Examples of such rule sets include:

  - Who can edit an Outage, what can be edited ,and when can editing be made (e.g., once an Outage has been Approved the Outage Requestor cannot move the Start or End Date/Time to prolong the Outage duration)

“Who can edit an Outage” is part of managing users, their roles, and privileges. This is done using a Directory Server/LDAP as described in section D.1 earlier.

“What can be edited” is part of the rules that govern Outage Submission. This is an integral part of the XML schema definition and validation.

“When an authorized person can edit an Outage” is managed through the category of rules that are defined in the rules engine.

## State/Status Rules

The rules applicable to a defined state transition are usually configured in the rules engine.

Examples of such rule sets include:

  - Rules where status transitions take place (e.g.,  ERCOT changing a status from Study to Accepted or Rejected)

## Outage Extension Rules

Examples of such rule sets include:

  - Forced Extension

  - Unavoidable Extension

The respective rules are configurable. An example of such a rule is Unavoidable Extension can be requested less than 3 days from the Planned End Date/Time. The number of days can be configured to any value within an acceptable range for this specific rule (e.g., from 3 to 4 days).

## Outage ID and Version Tracking Rules

Definitions need to be established in order to better define what the subject “rules” are for this category.

## User Preferences Rules

User preferences are configurable through the User Interface.

# Outage Submission and Approval Requirements and Guidelines

Table 3: Outage Submission and Approval Requirements and Guidelines

| Outage Type | Submission | Approval/Acceptance/Rejection* |
| --- | --- | --- |
| Transmission Planned | 3 days prior to Planned Start Date/Time | Within 6 pm 2 days prior to Planned Start Date/Time |
|  | 3-8 days prior to Planned Start Date/Time | Within 6 pm 3 days prior to Planned Start Date/Time |
|  | 9-45 days prior to Planned Start Date/Time | Within 4 days prior to Planned Start Date/Time |
|  | 46-90 days prior to Planned Start Date/Time | Within 40 days prior to Planned Start Date/Time |
|  | More than 90 days prior to Planned Start Date/Time | Within 75 days prior to Planned Start Date/Time |
| Transmission and Resource Forced | After Actual Start Date/Time, but no later than 2 am the day after the Forced Outage occurred | Immediate – ERCOT must always Accept (i.e., the Outage Scheduler assigns a default Accept status when Received at ERCOT) |
| Transmission Maintenance Level 1 | Within 24 hours prior to Planned Start Date/Time | Within 2 hours after Received at ERCOT – ERCOT must always Accept |
| Transmission Maintenance Level 2 | 2-7 days prior to Planned Start Date/Time | Within 2 days prior to Planned Start Date/Time |
| Transmission Maintenance Level 3 | 8-30 days prior to Planned Start Date/Time | Within 3 days prior to Planned Start Date/Time |
| Transmission Simple | 1-2 days prior to Planned Start Date/Time | Within 8 business hours after Received at ERCOT |
| Non Reliability Resource Maintenance Level 1 | Within 24 hours prior to Planned Start Date/Time | Within 2 hours after Received at ERCOT – ERCOT must Accept |
| Reliability Resource Maintenance Level 1 | Within 24 hours prior to Planned Start Date/Time | Within 2 hours after Received at ERCOT – ERCOT must Accept |
| Non Reliability Resource Maintenance Level 2 | Within 2-7 days prior to Planned Start Date/Time | ERCOT must Accept |
| Reliability Resource Maintenance Level 2 | Within 2-7 days prior to Planned Start Date/Time | Within 2 days prior to Planned Start Date/Time |
| Non Reliability Resource Maintenance Level 3 | Within 8-30 days prior to Planned Start Date/Time | ERCOT must Accept |
| Reliability Resource Maintenance Level 3 | Within 8-30 days prior to Planned Start Date/Time | Within 4 days prior to Planned Start Date/Time |
| Reliability Resource | 3-8 days prior to Planned Start Date/Time | Within 12 am 2 days prior to Planned Start Date/Time |
|  | 9-30 days prior to Planned Start Date/Time | 4 days prior to Planned Start Date/Time |
|  | 30-45 days prior to Planned Start Date/Time | 15 days prior to Planned Start Date/Time |
|  | More than 45 days prior to Planned Start Date/Time | 30 days prior to Planned Start Date/Time |
| Non Reliability Resource | 1-2 days prior to Planned Start Date/Time | Within 8 business hours after Received at ERCOT |
|  | 3-8 days prior to Planned Start Date/Time | Within 6 pm 2 days prior to Planned Start Date/Time |
|  | More than 8 days prior to Planned Start Date/Time | Immediate – ERCOT must always Accept (i.e., the Outage Scheduler assigns a default Accept status when Received at ERCOT) |
| Resource Opportunity | 1-8 days prior to Planned Start Date/Time | ERCOT will Approve as soon as possible after coordinating with all parties involved (i.e., the QSE and potentially TSPs) and evaluating reliability issues |
| Transmission Opportunity | N/A | Same rule as those for Transmission Planned Outage |
| Transmission Equipment Status Change | On the day of the status change | Immediate – ERCOT must always Accept (i.e., the Outage Scheduler assigns a default Accept status when Received at ERCOT) |

*	 Approval/Acceptance/Rejection requirements are not absolute or determinate, they function more like guidelines, unless otherwise specified.