## MMS - Outage Scheduler
| Document Name: |  | Texas Nodal TN.MMS Requirements Specification For Outage Scheduler Version 0.08
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table/Fig. | Pg. Sec., Req. | Description | Response | Reviewer | Reason / Comment | IDA Punch List
1 | Reliant (F.Trefny) | 7 | 2.2 |  | p.7, Sec. 2.2 | The TSP or QSE (i.e., the Outage Requestor) submits Outage Requests using the Outage Scheduler system. The ERCOT Outage Coordinator creates a Date Determinate Power Flow Model including Approved, Accepted, and Requested Outages, Generation Plan, and Load Forecast. Using this model, the ERCOT Outage Coordinator uses Contingency Analysis this term is used in the protocols to mean real time; what is this? | Clarification provided * | Robert Matlock | Propose: "The TSP or QSE (i.e., the Outage Requestor) submits Outage Requests using the Outage Scheduler system. The ERCOT Outage Coordinator creates a Date Determinate Power Flow Model including Approved, Accepted, and Requested Outages, Generation Plan, and Load Forecast. Using this model, the ERCOT Outage Coordinator uses contingency analysis.
2 | Reliant (F.Trefny) | 7 | 2.2 |  | p.7, Sec. 2.2 | For most Planned Outages [ do you need to describe the other outage types here? Planned only means one thing, what about Simple Outages?, if any requested Outage under evaluation causes pre or post contingent limit violations, the ERCOT Outage Coordinator consults with the Outage Requestor and determines if there is an acceptable solution (remedial action, generation adjustment, etc). If an acceptable solution exists, the Outages will be Approved or Accepted, if not, the Outage will be Rejected or Withdrawn and rescheduled at a better time. | Clarification provided * | Robert Matlock | Propose: "For most Scheduled Outages, if any requested Outage under evaluation causes pre or post contingent limit violations, the ERCOT Outage Coordinator consults with the Outage Requestor and determines if there is an acceptable solution (remedial action, generation adjustment, etc). If an acceptable solution exists, the Outages will be Approved or Accepted, if not, the Outage will be Rejected or Withdrawn and rescheduled at a better time."
3 | Reliant (F.Trefny) | 7 | 2.2 |  | p.7, Sec. 2.2 |  | Clarification provided * | Robert Matlock | The dashed boxes indicate what are part of the Outage Scheduler. The light yellow indicates and existing process, the dark yellow indicates a new process. Propose adding to the diagram: "The dashed boxes represent the Outage Scheduler" In the yellow box remove comma(,) after AS,Energy,
4 | Reliant (F.Trefny) | 8 | 3 |  | p.8, Sec. 3 | The Functional Requirements have been grouped according to the view of the user. The first group – External Client Requirements - focuses on the originator of an Outage - the Transmission Service Provider (TSP), the Qualified Scheduling Entity (QSE), and ERCOT acting on behalf of either. ERCOT should never “act on behalf of a TSP or QSE. The second group – Internal ERCOT Requirements - focuses on the role of ERCOT itself and how Outage Requests are managed by ERCOT. The third group – Information Exchange Requirements - deals with the acceptance and dissemination of Outage data. Finally the fourth group – Administration Requirements - deals with general administrative issues in the system, not directly involved with the submission and management of Outages. | Clarification provided * | Robert Matlock | ERCOT will need the ability to enter Forced Outages if for some reason the QSE/TSP is unable to do so. ERCOT will also need to be able to edit Outages if the system is unavailable to the MP and the problem is with the ERCOT system. Strict guidelines will be written as to when ERCOT can do this. We will also need to develop a means to track this. Propose: "The Functional Requirements have been grouped according to the view of the user. The first group – External Client Requirements - focuses on the originator of an Outage - the Transmission Service Provider (TSP), the Qualified Scheduling Entity (QSE), and ERCOT acting on behalf and in coordination with either. The second group – Internal ERCOT Requirements - focuses on the role of ERCOT itself and how Outage Requests are managed by ERCOT. The third group – Information Exchange Requirements - deals with the acceptance and dissemination of Outage data. Finally the fourth group – Administration Requirements - deals with general administrative issues in the system, not directly involved with the submission and management of Outages."
5 | Reliant (F.Trefny) | 8 | 3 |  | p.8, Sec. 3 | ERCOT, as an Independent System Operator (ISO) for a large portion of Texas, is required to review and approve, accept or reject Transmission and Resource Outages. The criterion for approval, acceptance, or rejection is adherence with NERC Transmission Security Standards and ERCOT guidelines and protocols and guidelines. ERCOT has developed and is continuing to develop tools to assist Outage Coordinators in evaluating the transmission security impact of Outages. These tools are described in a companion requirement document “Texas Nodal Energy Management System Requirements Specification for Outage Evaluation”. The Outage Scheduler application described in this document is the operational interface between participants, particularly TSPs and QSEs and Outage Coordination personnel at ERCOT. | Accepted | Robert Matlock
6 | Reliant (F.Trefny) | 9 | 3.1.1 | FR1-1 | p.9, Sec. 3.1.1, FR1-1 | Each TSP and QSE shall have the ability to submit to ERCOT their Outage Elements in a timeframe that is a function of the Outage Category and Type. TSPs shall be permitted to submit Outage Requests within the Transmission Category, while QSEs shall be permitted to submit Outage Requests within the Resource Category (Generation and Load). Outage Types for Transmission shall be Equipment Status Change??, Forced Outage, Maintenance Level 1-3 Outage, New/Relocated Outage??, Planned Transmission Outage, Simple Transmission Outage, and Tentative Outage??. Only outage types in the protocols can be allowed. | Clarification provided * | Robert Matlock | Propose: "Each TSP and QSE shall have the ability to submit to ERCOT their Outage Elements in a timeframe that is a function of the Outage Category and Type. TSPs shall be permitted to submit Outage Requests within the Transmission Category, while QSEs shall be permitted to submit Outage Requests within the Resource Category (Generation and Load). For Transmission outage types refer to Appendix A.1." A white paper on Equipment Status Change is being written.
7 | Reliant (F.Trefny) | 9 | 3.1.1 | FR1-1 | p.9, Sec. 3.1.1, FR1-1 | Forced Extension can only be created from an original Forced or Maintenance Outage. Unavoidable Extension can only be created from an original Planned Outage. Note, TSPs performance in meeting outage schedules are required to be posted. These outage types seem to allow for some discretion in performance that will be built into the system. See protocol section 8.3 “(c)Outage scheduling and coordination; TSP Outage planning and scheduling statistics must have less weight the further out these statistics are from the Planned Outage date “ . What codes will keep up with this performance reporting? | Clarification provided * | Robert Matlock | Extension of an outage will be track to determine if the QSE/TSP are completing their outages within the requested time frame. A metrics will be developed to track this. Propose: "Forced Extension can only be created from an original Forced Outage. Unavoidable Extension can only be created from an original Planned or Maintenance Outage." The performance metrics is part of EDW. Add to the IDA punch list. | Add to IDA Punch list
8 | Reliant (F.Trefny) | 9 | 3.1.1 | FR1-1 | p.9, Sec. 3.1.1, FR1-1 | When creating an Outage on a Transmission Element, the TSP shall have the capability of choosing from a list of associated switches and/or breakers for that Transmission Element. The data required to populate these selection lists is provided by the NMMS to the Outage Scheduler. Is this necessary. Seems like all you need to name is the highest level of equipment and then the system should know what associated equipment is also out. | Clarification provided | Robert Matlock | The TSP is required to enter all switches or breakers that will be out of there normal position for more than 2 minutes in the OS.
9 | Reliant (F.Trefny) | 9 | 3.1.1 | FR1-1 | p.9, Sec. 3.1.1, FR1-1 | Outage Types for Resources shall be Mothballed, Derating, Forced Outage, Maintenance Level 1-3 Outage, and Planned Outage, Opportunity, and Simple Transmission Outage. Planned Outages are handled differently, whether they are submitted eight days or less, or more than eight days. | Clarification provided * | Robert Matlock | Propose: "For Resource outage types refer to Appendix A.1. Planned Outages are handled differently, whether they are submitted eight days or less, or more than eight days." Simple Transmission Outage will not work for the Resources per the TAC approved guidelines. We are looking at how we can implement Opportunity outages and are waiting for a clarification from the TPTF.
10 | Reliant (F.Trefny) | 9 | 3.1.1 | FR1-1 | p.9, Sec. 3.1.1, FR1-1 | A Planned Outage is Forced Extension can only be created from an original Forced or Maintenance Outage if it lasts longer than originally scheduled. Derating Extension can only be created from an original Derating Outage. Unavoidable Extension can only be A Forced Outage is created for an original Planned Outage that extends past its scheduled return. | Clarification provided * | Robert Matlock | A Planned outage can only be created if it meets the Protocol requirements for a Planned outage. If the Protocol time lines and approval process can't be met, then the outage will need to be a forced extension. To show a difference between extending a Forced outage and a Planned or Maintenance outage in the metrics, Planned and Maintenance are called Unavoidable Extension. An extended Forced outage will needs to be classified as a Forced Extension. This will allow for better tracking and metrics. Propose: "A Forced Extention can only be created from an original Forced outag that is not able to be submitted as a Planned outage due to the Protocol time lines. A Unavoidable Extention can only be created from an original Planned or Maintenance Outage that is not able to be submitted as a Planned outage due to the Protocol time lines."
11 | Reliant (F.Trefny) | 9 | 3.1.1 | FR1-1 | p.9, Sec. 3.1.1, FR1-1 | Opportunity Outages (as defined in the Nodal Protocol) shall be handled using an operating procedure the outage scheduler. No these must be in the Outage Scheduler so the market may see the request. | Pending | Robert Matlock | We are currently discussing this and awaiting a clarification from the TPTF on the within 8 day requirements.
12 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): · The identification of the Transmission Facility, including TSP operator and location | Accepted | Robert Matlock
13 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): . . . · The A free text message drafted by the Requestor describing the nature of the work to be performed during the proposed Transmission Outage | Clarification provided * | Robert Matlock | Propose: "A drop box with a list will be provided as well as a free text box for further explanation."
14 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): . . . · The preferred requested Start and End Date/Time for each proposed Planned and Maintenance Transmission Outage | Accepted | Robert Matlock
15 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): . . . · The time required to: (i) Terminate the Planned and Maintenance Transmission Outage, and (ii) Restore the Transmission Facility to normal operation | Accepted | Robert Matlock
16 | CNP (D.Caufield) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): . . . •The amount of scheduling flexibility (i.e., the earliest Start Date/Time and the latest End Date/Time for the Outage) | Rejected | Robert Matlock | Required per 3.1.5.9 (f)
17 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): . . . · Identification of any other Transmission Facility or NOMCR , Project Number that must be out of service to facilitate the TSP Outage Request | Clarification provided * | Robert Matlock | The Project Name/Number will be a separate entry field. Propose: Identification of any other Transmission Facility that must be out of service to facilitate the TSP Outage Request. Project identification name/number.
18 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): . . . · Identification of any remedial actions or special protection systems necessary during this Outage and the contingency that will require the remedial action or relay action Note these special protections systems and RAPs must be available to the market at all times; not just when a TSP wants to use one.(see protocols) | Response | Robert Matlock | The NMMS will post SPS and RAPs to the MIS. Moved to IDA Punch List for tracking purposes. | Add to IDA Punch list
19 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Transmission Category (varies somewhat based on Outage Category): . . . · Any oOther relevant information in a free text narrative form | Accepted | Robert Matlock
20 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Resource Category (varies somewhat based on Outage Category): . . . · Resource Status during the Outage | Rejected | Robert Matlock | Not required per the Protocols. Not needed for the business process.
21 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Resource Category (varies somewhat based on Outage Category): . . . · HSL Net MW capacity available during the Outage (i.e., this is for Derating - on a Planned or Maintenance Outage Request this will default to 0) | Accepted | Robert Matlock
22 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Resource Category (varies somewhat based on Outage Category): . . . · LSL available during the Outage | Accepted | Robert Matlock
23 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Resource Category (varies somewhat based on Outage Category): . . . · Estimated Start and End Date/Time for the Planned and Maintenance Level 1-3 Outages | Clarification provided * | Robert Matlock | Propose: "Estimated Start Date/Time and End Date/Time for the Outage."
24 | CNP (D.Caufield) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Resource Category (varies somewhat based on Outage Category): . . . • Earliest Start and End Date/Time | Clarification provided * | Robert Matlock | Protocol 3.1.6.2 (e) requires the acceptable deviation or earlist start latest finish date. Propose: "Earliest Start Date/Time and Latest End Date/Time"
25 | Reliant (F.Trefny) | 10 | 3.1.1 | FR1-1 | p.10, Sec. 3.1.1, FR1-1 | The following information shall be provided in an Outage Request for the Resource Category (varies somewhat based on Outage Category): . . . · Earliest Start and End Date/Time | Clarification provided * | Robert Matlock | Protocol 3.1.6.2 (e) requires the acceptable deviation or earlist start latest finish date. Propose: "Earliest Start Date/Time and Latest End Date/Time"
26 | Reliant (F.Trefny) | 11 | 3.1.1 | FR1-1 | p.11, Sec. 3.1.1, FR1-1 | Outage Types and Categories and their life cycle are summarized in the Life-Cycle Matrix in Appendix B. The matrix summarizes the various states for each Outage Category and Type. Allowed state transitions for Outages are depicted in the State Transition Diagram in Appendix C. needs to be corrected to those outages allowed in the definition of Outages in the Protocols. | Clarification provided * | Robert Matlock | Will correct the State Diagrams
27 | Reliant (F.Trefny) | 11 | 3.1.1 | FR1-1 | p.11, Sec. 3.1.1, FR1-1 | When ERCOT Outage Coordinator (EOC) enters an Outage Request on behalf of a TSP or QSE, after choosing the TSP or QSE, the OS shall provide the capability and corresponding authorization for entering the Outage. NOT ALLOWED> ERCOT has no authority to do so under protocols. | Clarification provided * | Robert Matlock | see ID 4 Propose: "When ERCOT Outage Coordinator (EOC) enters an Outage Request on behalf and in coordination with a TSP or QSE, after choosing the TSP or QSE, the OS shall provide the capability and corresponding authorization for entering the Outage."
28 | Reliant (F.Trefny) | 11 | 3.1.2 | FR1-2 | p.11, Sec. 3.1.2, FR1-2 | A TSP and a QSE shall be permitted to Edit an Outage submitted on behalf of the same requesting company whenever any information concerning that Outage changes or ERCOT requires modification and/or re-submission. How is this captured in the performance monitor required in section 8 | Pending | Robert Matlock | Any change will be recorded and if dates or times are changed the EDW will look at the original for comparison. Will be added to the IDA punch list so it will not get forgotten. | Add to IDA Punch list
29 | Reliant (F.Trefny) | 11 | 3.1.2 | FR1-2 | p.11, Sec. 3.1.2, FR1-2 | The ability to edit an Outage and the properties that can be edited depend on the Outage Type and the state of the Outage according to the timeline specified in the nodal protocols. The Outage states that allow the Edit operation are illustrated in the State Transition Diagram in Appendix C. | Clarification provided * | Robert Matlock | Propose: "The ability to edit an Outage and the properties that can be edited depend on the Outage Type and the state of the Outage. Any change to an outage will require revalidation. The Outage states that allow the Edit operation are illustrated in the State Transition Diagram in Appendix C"
30 | CNP (D.Caufield) | 11 | 3.1.3 | FR1-3 | p.11, Sec. 3.1.3, FR1-3 | The originator – an Outage Requestor – or someone acting on his/her behalf shall be permitted to Cancel an Outage Request, if the need for the request no longer exists. Cancellation must occur before the Planned Start Date/Time, thus before the Outage is Active. Does the two hour editing window apply here so an outage can be canceled after the start time? If not, it should. | Clarification provided | Robert Matlock | Once the Planned Start time has pasted the outage cannot be canceled.
31 | Reliant (F.Trefny) | 11 | 3.1.3 | FR1-3 | p.11, Sec. 3.1.3, FR1-3 | The originator – an Outage Requestor – or someone acting on his/her behalf shall be permitted to Cancel an Outage Request, if the need for the request no longer exists. Cancellation must occur before the Planned Start Date/Time, thus before the Outage is Active. How is this captured in the performance monitor? | Pending | Robert Matlock | A metrics will be developed to capture this. Will be added to the IDA punch. | Add to IDA Punch list
32 | Reliant (F.Trefny) | 12 | 3.1.4 | FR1-4 | p.12, Sec .3.1.4, FR1-4 | A TSP or QSE shall have the capability to extend an Outage if it is not possible to complete the Outage by the Planned End Date/Time. No. They must enter another outage within the time frame allowed or suffer a forced outage. There shall be three types of extensions: • Forced Extension – used for Forced or Maintenance Level 1-3 Outages • Unavoidable Extension – used for Planned Outages when the extension is requested less than three days before the Planned End Date/Time • Derating Extension – used for extending a Derating of a Resource Outage | Clarification provided * | Robert Matlock | see ID 10 Propose: "A TSP or QSE shall have the capability to extend an Outage if it is not possible to complete the Outage by the Planned End Date/Time and a Planned outage cannot be entered. There shall be two types of extensions: Forced Extension – used for Forced Outages • Unavoidable Extension – used for Planned and Maintenance Outages when the extension is requested less than three days before the Planned End Date/Time."
33 | Reliant (F.Trefny) | 12 | 3.1.5 | FR1-5 | p.12, Sec. 3.1.5, FR1-5 | The TSP or QSE shall have the capability to create an Outage Request that recurs on a daily basis from any Planned or Tentative Outage when it is created. The duration of the original Outage Request shall not exceed 24 hours. The Outage Request shall include: Start Date/Time of the original copy, End Date/Time of the last copy, and interval in days between each copy. This action creates multiple Outage Requests, one for each contiguous period. | Clarification provided * | Robert Matlock | This will need to be limited to Planned only. The other outage types do not fit the timeline. Propose: "The TSP or QSE shall have the capability to create an Outage Request that recurs on a daily basis from any Planned Outage when it is created. The duration of the original Outage Request shall not exceed 24 hours. The Outage Request shall include: Start Date/Time of the original copy, End Date/Time of the last copy, and interval in days between each copy. This action creates multiple Outage Requests, one for each contiguous period."
34 | Reliant (F.Trefny) | 13 | 3.1.6 | FR1-6 | p.13, Sec. 3.1.6, FR1-6 | A TSP or QSE shall have the capability to copy an existing Planned or Tentative Transmission Outage or a Planned Resource Outage, respectively. | Accepted | Robert Matlock
35 | Reliant (F.Trefny) | 13 | 3.1.6 | FR1-6 | p.13, Sec. 3.1.6, FR1-6 | The copy shall be identical to the original but subject to user modification of any of the following fields: This list does not seem to be the same as the one before where you described the data in the original request. Seems to me they should be the same. | Clarification provided * | Robert Matlock | will need to compare and correct. Make FR1-1 match with FR1-6
36 | Reliant (F.Trefny) | 13 | 3.1.6 | FR1-6 | p.13, Sec. 3.1.6, FR1-6 | • Transmission (Planned and Tentative Outages) | Clarification provided * | Robert Matlock | remove the bullet on Transmission and remove: "Planned and Tentative Outages"
37 | CNP (D.Caufield) | 13 | 3.1.6 | FR1-6 | p.13, Sec. 3.1.6, FR1-6 | A TSP or QSE shall have the capability to copy an existing Planned or Tentative Transmission Outage or a Planned Resource Outage, respectively. The copy shall be identical to the original but subject to user modification of any of the following fields: . . . •Earliest Start Date/Time Delete or explain why needed! •Latest End Date/Time Delete or explain why needed! | Rejected | Robert Matlock | 3.1.5.9 (f) and 3.1.6.2 (e) require this information when submitting an outage request. Propose: "A TSP or QSE shall have the capability to copy an existing Outage. The copy shall be identical to the original but subject to user modification of any of the following fields:"
38 | CNP (D.Caufield) | 13 | 3.1.6 | FR1-6 | p.13, Sec. 3.1.6, FR1-6 | Resource (Planned Outages): . . . •Earliest Start Date/Time •Latest End Date/Time | Rejected | Robert Matlock | 3.1.5.9 (f) and 3.1.6.2 (e) require this information when submitting an outage request.
39 | Reliant (F.Trefny) | 14 | 3.1.7 | FR1-7 | p.14, Sec. 3.1.7, FR1-7 | Description: A TSP or QSE shall have the capability to temporarily disable an outage period inside an active continuous Outage (i.e., temporarily return the Transmission Element to service). In such a case, a copy of the original Outage shall be created. A new Planned End Date/Time shall be entered into the original Outage. A new Planned Start Date/Time shall be entered into the copy. The original Planned End Date/Time remains the same on the copy. The Outage Scheduler shall create naming convention for the Outage ID that allows users to determine that the resulting Outages were derived from the original Outage through the process of disablement.Why is this needed. Seems like they should just enter new outages. This makes tracking performance very difficult. Suggest you delete. | Accepted | Robert Matlock
40 | Reliant (F.Trefny) | 14 | 3.1.8 | FR1-8 | p.14, Sec. 3.1.8, FR1-8 | The TSP shall have the capability to create a Common Outage Not an allowed outage type.. A Common Outage shall be produced using an original non-‘Equipment Status change’ Transmission Outage to create multiple copies with different affected Transmission Elements that share a common Start and End Date/Time. The resulting Outages shall be bound together as a Common Outage. When creating an Outage on a Transmission Element the TSP shall have the capability of choosing from a list of associated switches and/or breakers for that Transmission Element. Outages for those switches and/or breakers shall be created automatically and all Outages shall be bound together (initial transmission Outage plus the associated switches and breaker Outages) as a Common Outage | Clarification provided * | Robert Matlock | Propose: "The TSP shall have the capability to group a set of outages together. A group shall be produced using an original non-‘Equipment Status change’ Transmission Outage to create multiple copies with different affected Transmission Elements that share a common Start and End Date/Time. The resulting Outages shall be bound together as a Common Group. When creating an Outage on the inital Transmission Element the TSP shall have the capability of choosing from a list of Transmission Elements associated with the inital Outage. Outages for the chosen Transmission Elements shall be created automatically and all Outages shall be bound together (initial transmission Outage plus the associated Transmission Element Outages) as a Common Group."
41 | Reliant (F.Trefny) | 15 | 3.1.9 | FR1-9 | p.15, Sec. 3.1.9, FR1-9 | The following events shall cause warning conditions to be brought to the attention of a TSP or QSE, but only for Outages entered by or on behalf of that TSP or QSE only TSPs and QSEs may enter outages: | Rejected | Robert Matlock | see ID 4 Propose: "The following events shall cause a warning condition to be brought to the attention of the requesting TSP or QSE."
42 | Reliant (F.Trefny) | 15 | 3.1.9 | FR1-9 | p.15, Sec. 3.1.9, FR1-9 | The TSP or QSE shall respond to a warning by entering the required missing information and acknowledging the warning. The TSP or QSE shall have a means of viewing unacknowledged warnings. How does this get to the performance monitior? | Clarification provided | Robert Matlock | This is an alarm function and has no affect on the performance monitior.
43 | Reliant (F.Trefny) | 15 | 3.1.10 | FR1-11 | p.15, Sec. 3.1.10, FR1-11 | The TSP that originally submitted a Tentative Outage shall be permitted to convert it to a Planned Outage no later than 15 days before the Outage is proposed to begin. If the TSP does not convert the Tentative Outage to a Planned Outage by that timeframe, the Outage shall automatically be given a status of Cancel – Expired should not be allowed.. | Accepted | Robert Matlock
44 | Reliant (F.Trefny) | 17 | 3.2.3 | FR2-3 | p.17, Sec. 3.2.3, FR2-3 | The ERCOT Outage Coordinator and System Operator shall be provided a means to Withdraw Outages that have been Approved or Accepted, with the exception of Forced, Derating, Mothballed, and Planned Resource - Non-Reliability Outages (submitted more than eight days before Planned Start Date/Time) | Accepted | Robert Matlock
45 | Reliant (F.Trefny) | 17 | 3.2.3 | FR2-3 | p.17, Sec. 3.2.3, FR2-3 | The ERCOT Outage Coordinator and System Operator shall be provided a means to Withdraw Outages that have been Approved or Accepted, with the exception of Forced, Derating, Mothballed, and Planned Resource - Non-Reliability Outages (submitted more than eight days before Planned Start Date/Time). How does this get to performance monitor? | Pending | Robert Matlock | The EDW will be providing the metrics to track Withdraw Outages. Will be added to the IDA punch list. | Add to IDA Punch list
46 | Reliant (F.Trefny) | 17 | 3.2.4 | FR2-4 | p.17, Sec. 3.2.4, FR2-4 | The Outage Scheduler will produce warnings brought to the attention of ERCOT Outage Coordinators and System Operators for the following events: • Entry of Actual Start Date/time for Forced, Forced Extension, Unavoidable Extension, Maintenance Level 1-3, Equipment Status Change (ESC), Monitored or Mothballed Outages these types all do not exist and some are missing. | Clarification provided * | Robert Matlock | The need for an outage extension are explaned in ID 10. Propose: " • Entry of Acutal Start Date/time for Forced, Forced Extension, Unavoidable Extension, Maintenance Level 1-3 Outages, Equipment Status Change (ESC), or outage being monitored • Entry of Actual End Date/Time for Forced, Forced Extension, Unavoidable Extension, Maintenance Level 1-3 Outage, ESC, or Outage being monitored"
47 | Reliant (F.Trefny) | 17 | 3.2.4 | FR2-4 | p.17, Sec. 3.2.4, FR2-4 | The Outage Scheduler will produce warnings brought to the attention of ERCOT Outage Coordinators and System Operators for the following events: . . . · Cancellation of Monitored Outages??? | Clarification provided | Robert Matlock | The definition of a monitored is in Appendix A. This is an internal function to track changes to an outage. Propose: " • Cancellation of an outage being monitored"
48 | Reliant (F.Trefny) | 18 | 3.2.5 | FR2-5 | p.18, Sec. 3.2.5, FR2-5 | FR2-5 Manage Unit Relationship: This designation is not needed in Outage Scheduler as it is something that is done through the registration system. We can not have multiple systems doing this. | Pending | Robert Matlock | We are currently looking to see where this information will be stored. Add to IDA punch list | Add to IDA Punch list
49 | CNP (D.Caufield) | 18 | 3.2.6 | FR2-6 | p.18, Sec. 3.2.6, FR2-6 | Description: Why is this privilege necessary, who would have a privileged role and what rules apply to who and when it could be used? | Clarification provided | Robert Matlock | There will be mistakes made from time to time, this role will be one of the Senior Coordinators and will only be used when needed. A means of tracking this will need to be developed.
50 | Reliant (F.Trefny) | 18 | 3.2.6 | FR2-6 | p.18, Sec. 3.2.6, FR2-6 | There shall be a privileged role called the OS Admin Role (OAR) that enables a user granted that role to perform all operations of the ERCOT Outage Coordinator and operations not allowed by any other role. These privileged operations shall be: · Change or delete the Actual Start Date/Time, except for Forced Outages. If Actual Start Date/Time is deleted and Actual End Date/Time was also entered, the Actual End Date/Time is deleted too Can only be done by the TSP or QSE. • Change or delete the Actual End Date/Time after a Two-Hour Editing Window has passed. If an Actual End Date/Time is deleted, the system shall check for a conflicting Outage that may have been created within 24 hours after the Actual End Date/Time was entered for this Outage. If it finds a second Outage has been submitted for this Transmission Element, the OAR shall not be permitted to delete the Actual End Date/Time Can only be done by the TSP or QSE. • Cancel an Outage due to error or Date/time expiration after Actual Start Date/Time has been entered, and before Actual End Date/Time has been entered (e.g., while the Outage is Active) Can only be done by the TSP or QSE. | Clarification provided | Robert Matlock | Deleting the Actual Start and End Date/Time is limited to two hours for the TSP/QSE. Mistakes do happen and this will allow for corrections. This will be limited to one or two Senior Coordinators and will require an explanation in the comments section. A Forced outage is active when it is submitted, if the requestor has entered the wrong element by mistake, it will need to be canceled. This ability is limited to the OAR.
51 | Reliant (F.Trefny) | 19 | 3.3.1 | FR3-1 | p.19, Sec. 3.3.1, FR3-1 | The Outage Scheduler shall provide a means of posting all Outage information to the Market Information System (MIS) Secure Area. This information shall include all information provided by the Outage Requestor and the following: | Clarification provided * | Robert Matlock | Resource outage information is protected, Protocol 1.3.1.1. Propose: "The Outage Scheduler shall provide a means of posting required Outage information to the Market Information System (MIS) Secure Area. This information shall include all information provided by the Outage Requestor and the following:"
52 | Reliant (F.Trefny) | 19 | 3.3.1 | FR3-1 | p.19, Sec. 3.3.1, FR3-1 | · Semi-annualMonthly and Annual statistics on how TSP Planned Outages compare with actual TSP Outages | Accepted | Robert Matlock
53 | CNP (D.Caufield) | 19 | 3.3.1 | FR3-1 | p.19, Sec. 3.3.1, FR3-1 | The Outage Scheduler shall provide a means of posting Outage information to the Market Information System (MIS) Secure Area. This information shall include: . . . • Monthly statistics on ERCOT compliance with Protocol 3.1.5.3 Timelines for Response by ERCOT for TSP Requests. • Monthly statistics on ERCOT compliance with Protocol 3.1.5.6 Rejection Notice. • Monthly statistics on ERCOT compliance with Protocol 3.1.5.7 for the number of outages withdrawn by ERCOT after approval. (A large number will indicate problems with the prior approval process). | Pending | Robert Matlock | The EDW will do this type of reporting. Add to the IDA punch list. | Add to IDA Punch list
54 | CNP (D.Caufield) | 19 | 3.3.1 | FR3-1 | p.19, Sec. 3.3.1, FR3-1 | The Outage Scheduler shall provide a means of posting Outage information to the Market Information System (MIS) Secure Area. This information shall include: . . . • Notice of Outage approval withdrawals within one hour Withdrawn by ERCOT within one hour of approval or one hour prior to scheduled start or what?? | Clarification provided * | Robert Matlock | Protocol 3.1.5.7 (1). Propose: "• Notice of Outage approval withdrawals within one hour or withdrawal"
55 | Reliant (F.Trefny) | 20 | 3.3.1 | FR3-1 | p.20, Sec. 3.3.1, FR3-1 | · Daily postings of aggregated schedules of Planned Outages foravailability of Resources showing the MW of Outages of capability for each hour for the next 14 days | Clarification provided * | Robert Matlock | Propose: " • A schedule of the aggregated Resource Outages showing the MW of Outages and MW capabilities for each hour for the next 14 days posted daily.” This may be moved to the EDW system. Add to the IDA Punch List | Add to IDA Punch list
56 | Reliant (F.Trefny) | 20 | 3.3.1 | FR3-1 | p.20, Sec. 3.3.1, FR3-1 | • Daily postings of weekly aggregated schedules of Planned Outages foravailability of Resources showing the MW of Outagesavailable on peak for each week in for the next 12 months | Clarification provided * | Robert Matlock | Propose: " • A schedule of the aggregated Resource Outages showing the MW of Outages and MW capabilities available on peak for the remainder of the 12 months posted daily” This may be moved to the EDW system. Add to the IDA Punch List | Add to IDA Punch list
57 | CNP (D.Caufield) | 20 | 3.3.2 | FR3-2 | p.20, Sec. 3.3.2, FR3-2 | • Protocol 3.1.5.13 states that Transmission Reports should be posted on the MIS Secure area. No outage information should be posted on the open access ERCOT Website, as it is currently! There is no mention in the Outage Scheduler Requirements Specification nor in Protocol 3 that outage information will be posted anywhere but on the MIS Secure Area. | Clarification provided | Robert Matlock | FR3-2 is for internal to ERCOT systems. FR3-1 posts outage information to the MIS secure area.
58 | Reliant (F.Trefny) | 21 | 3.3.4 | FR3-4 | p.21, Sec. 3.3.4, FR3-4 | For each Transmission Element, the following information shall be imported: . . . • Resource maximum HSL generation • Resource minimum generationLSL • Resource by type provided for in the protocols definition of Resources | Accepted | Robert Matlock
59 | CNP (D.Caufield) | 21 | 3.3.4 | FR3-4 | p.21, Sec. 3.3.4, FR3-4 | For each Transmission Element, the following information shall be imported: . . . • Transmission Operator area to which a Resource is electrically connected. | Pending | Robert Matlock | Still looking onto the ability to do this.
60 | CNP (D.Caufield) | 21 | 3.3.4 | FR3-4 | p.21, Sec. 3.3.4, FR3-4 | If the name by which a Transmission Element is known can change over the Transmission Elements lifetime, then accompanying the name and effective dates shall be some unique nameplate identifier that never changes over the Transmission Elements lifetime. In the latter case, import of a Transmission Element whose name changes shall cause an update in all known Outages pertaining to that Transmission Element of the Transmission Element name. Remove completely – or adequately explain why this statement is needed! All Transmission elements are subject to having their name changed. | Rejected | Robert Matlock | All Transmission elements have a unique ID that will remain with that elements as long as it is in the model.
61 | TXU | 21 | 3.3.5 | FR3-5 | p.21, Sec. 3.3.5, FR3-5 | 1. A programmatic interface shall be provided to TSPs and QSEs to import and export Outage data in XML format at their request. The data that they provide in the upload to the Outage Scheduler shall conform to the requirements for Outage submission (i.e., FR1-1). The OS shall perform all of the validity checking that would be performed through the OS User Interface. The results of the upload, in terms of which Outages were accepted and which failed validation and were not accepted (along with the reasons for failure) shall be made available to the Outage Requestor in XML format. ( TXU: Shouldn’t there also be a Web Services Interface through the MIS Infrastructure as well. Does Daryl Shing have this interface on in his purview?) | Clarification provided | Robert Matlock | There are three types of interface: 1. GUI 2. GUI File Upload and Download 3. WEB Services
62 | Reliant (F.Trefny) | 22 | 3.3.5 | FR3-5 | p.22, Sec. 3.3.5, FR3-5 | Programmatic Interface Are all Outages posted including those that were disallowed by ERCOT?? | Clarification provided | Robert Matlock | All transmission outages will be posted.
63 | Reliant (F.Trefny) | 23 | 3.4.2 | FR4-3 | p.23, Sec. 3.4.2, FR4-3 | Manage Outage Versions Is there a table of this outage IDs for the market and ERCOT to view? | Clarification provided | Robert Matlock | Yes this information is available in the OS tool.
64 | Reliant (F.Trefny) | 23 | 4 |  | p.23, Sec. 4 | How are SCADA outages handled? Seems like we need something to manage that too?? | Pending | Robert Matlock | Add to the IDA punch list. | Add to IDA Punch list
65 | CNP (D.Caufield) | 24 | 4.1 | SR-1 | p.24, Sec. 4.1, SR-1 | 4.1 SR-1 Performance Requirements Outage data shall be made available to other systems within the secured ERCOT enterprise. To date no mechanism has been fully defined as to how this will be implemented. | Accepted | Robert Matlock
66 | Reliant (F.Trefny) | 25 | 4.3 |  | p.25, Sec. 4.3 | The current average number of Outages per day is about 120 with maximum of 40,.000 Outages per year. | Accepted | Robert Matlock
67 | Reliant (F.Trefny) | 26 | 4.8 |  | p.26, Sec. 4.8 | Since the staff of both Outage Requestors and ERCOT Outage Coordinators System Operators evolves over time, ERCOT needs to be self sufficient in their ability to implement an ongoing User Training Program. In response to this need, user-level training for the Outage Scheduler follows a “Train-the-Trainer” philosophy. As such, user-level training shall be provided to ERCOT with the goal of empowering ERCOT trainers to implement their user-level training program. Nodal training requirements specify users will be trained by ERCOT. Internal training shall be provided to ERCOT to enable ERCOT to eventually take over the maintenance of the Outage Scheduler. | Clarification provided * | Robert Matlock | Propose: “Since the staff of both Outage Requestors and ERCOT Outage Coordinators System Operators evolves over time, ERCOT needs to be self sufficient in their ability to implement an ongoing User Training Program. User-level training shall be provided to ERCOT with the goal of empowering ERCOT trainers to implement their user-level training program.”
68 | CNP (D.Caufield) | 26 | 4.10 |  | p.26, Sec. 4.10 | NOTE: there is no mention in this requirements specification of the Actual Start and Actual End fields in the Outage Scheduler on the Portal where TSP (and Resource?) operators enter actual equipment out and in service times, how this data is used, etc. | Clarification provided | Robert Matlock | To create the metrics on how the QSE/TSP Planned outages compare to the actual outages requires this information. 3.1.3.1 (2) and 3.1.3.2 (2).
69 | Reliant (F.Trefny) | 32 | A.1 | Definitions | p.32, Sec. A.1 Definitions | A.1 Definitions These definitions do not correspond to those allowed under the protocols. Please revise. | Clarification provided * | Robert Matlock | Will correct the Definitions.
70 | CNP (D.Caufield) | 33 | A.1 | Definitions | p.33, Sec. A.1 Definitions | Outage Status The various states of an Outage in the Outage Scheduler system are listed below. The state of an Outage defines the status of the Outage. The states are depicted graphically and described more comprehensively in the Outage State Transition Diagram in Appendix C: . . . • Canceled – Reschedule Within One MonthTo be Rescheduled •Canceled – Reschedule Next Season •Canceled – Reschedule, Date Unknown | Rejected | Robert Matlock | The five Cancel types are to allow the requester more flexibility when canceling an outage request. A metrics will be created to show the canceled outages.
71 | CNP (D.Caufield) | 33 | A.1 | Definitions | p.33, Sec. A.1 Definitions | Outage Status The various states of an Outage in the Outage Scheduler system are listed below. The state of an Outage defines the status of the Outage. The states are depicted graphically and described more comprehensively in the Outage State Transition Diagram in Appendix C: . . . • Cancelled by ERCOT . . . • Withdrawn by ERCOT | Rejected | Robert Matlock | ERCOT should not cancel an outage other than when a forced outage is entered by mistake. If this occurs, it will have a status of 'Cancelled mistake' with comments. Withdrawn is only available to ERCOT.
72 | Reliant (F.Trefny) | 33 | A.1 | Definitions | p.33, Sec. A.1 Definitions | Outage Types For each Outage Category, there are several Outage Types. For Resources the following Outage Types are available: These types do not correspond to those allowed under the protocols. Please revise. • Mothballed (Reliability) • Derating • Forced Outage • Maintenance Level 1 • Maintenance Level 2 • Maintenance Level 3 • Planned Outage Non-Reliability > 8 days • Planned Outage Non-Reliability < 8days • Planned Outage Reliability | Clarification provided * | Robert Matlock | Propose: "For each Outage Category, there are several Outage Types. For Resources the following Outage Types are available: • Forced Outage • Maintenance Level 1 • Maintenance Level 2 • Maintenance Level 3 • Planned Outage o Non-Reliability > 8 days o Planned Outage Non-Reliability < 8days o Planned Outage Reliability"
73 | Reliant (F.Trefny) | 34 | A.1 | Definitions | p.34, Sec. A.1 Definitions | Outage Types: . . . For Transmission the following Outage Types are available: These types do not correspond to those allowed under the protocols. Please revise. • Equipment Status Change • Forced Outage • Maintenance Level 1 • Maintenance Level 2 • Maintenance Level 3 • New/Relocated Outage • Planned Transmission Outage • Simple Transmission Outage This outage is not discussed in the above descriptions. Please provide descriptions on how ERCOT or a TSP will determine if an outage is “Simple” • Tentative Outage | Clarification provided * | Robert Matlock | Propose: “For Transmission the following Outage Types are available:. • Equipment Status Change • Forced Outage • Maintenance Level 1 • Maintenance Level 2 • Maintenance Level 3 • Planned Transmission Outage • Simple Transmission Outage “ Determination on a Simple outage is out of scope for the OS project
74 | CNP (D.Caufield) | 35 | A.1 | Definitions | p.35, Sec. A.1 Definitions | Simple Outage Define | Clarification provided | Robert Matlock | Simple Outage is in the Protocol Section 2 Definitions and Acronyms. The TACK approved definition is posted on the ERCOT web site.
75 | Reliant (F.Trefny) | 35 | A.1 | Definitions | p.35, Sec. A.1 Definitions | Tentative Outage: A type of Future Transmission Outage Request for which the Planned Start and End Date/Time is not known, but the general time frame is. This type of Outage Request will be automatically Canceled 15 days prior to the Planned Start Date/Time if not converted to a Planned Outage by the initial Outage Requestor not allowed. | Clarification provided * | Robert Matlock | will remove
76 | CNP (D.Caufield) | 35 | A.1 | Definitions | p.35, Sec. A.1 Definitions | Tentative Outage A type of Future Transmission Outage Request for which the Planned Start and End Date/Time is not known, but the general time frame is. This type of Outage Request will be automatically Canceled 15 days prior to the Planned Start Date/Time if not converted to a Planned Outage by the initial Outage Requestor. Add verbage about whether Tentative Outages are or are not included in studies, auctions, etc… | Clarification provided * | Robert Matlock | will remove
77 | Reliant (F.Trefny) | 37 | B |  | p.37, Sec. B | B. Outage Life-Cycle Matrix These definitions do not correspond to those allowed under the protocols. Please revise. | Clarification provided * | Robert Matlock | will edit
78 | CNP (D.Caufield) | 38 | C | Table 2 | p.38, Sec. C, Table 2 | Canceled – Weather An Outage has been canceled by the Requestor due to weather conditions (rain, hurricane, freezes, etc) | Rejected | Robert Matlock | This outage will be rescheduled at some time so one of the five cancel types with an explanation in the remarks about weather.
79 | CNP (D.Caufield) | 38 | C | Table 2 | p.38, Sec. C, Table 2 | Canceled – Unavoidable System Conditions An Outage has been canceled by the Requestor due to unavoidable conditions such as equipment failure, loading conditions, loss of generation, etc | Rejected | Robert Matlock | Cancel will need to be one of the five with an explanation in the remarks.
80 | CNP (D.Caufield) | 38 | C | Table 2 | p.38, Sec. C, Table 2 | Canceled – Reschedule Within One MonthTo be Rescheduled An Outage that has been Canceled by the Outage Requestor and will be rescheduled within a month | Rejected | Robert Matlock | We tried to give more flexibility with cancel. There will be multiple metrics to track the different reasons for canceling an outage.
81 | CNP (D.Caufield) | 38 | C | Table 2 | p.38, Sec. C, Table 2 | Canceled – Reschedule Next Season An Outage that has been Canceled by the Outage Requestor and will be rescheduled next season | Rejected | Robert Matlock | We tried to give more flexibility with cancel. There will be multiple metrics to track the different reasons for canceling an outage.
82 | CNP (D.Caufield) | 38 | C | Table 2 | p.38, Sec. C, Table 2 | Canceled – Reschedule, Date Unknown An Outage that has been Canceled by the Outage Requestor and will be rescheduled, but date is unknown | Rejected | Robert Matlock | We tried to give more flexibility with cancel. There will be multiple metrics to track the different reasons for canceling an outage.
83 | CNP (D.Caufield) | 38 | C | Table 2 | p.38, Sec. C, Table 2 | Canceled by ERCOT An Outage Request that has been Canceled by ERCOT | Rejected | Robert Matlock | ERCOT should not cancel an outage other than when a forced outage is entered by mistake. This has a 'Canceled - Error' status.
84 | CNP (D.Caufield) | 38 | C | Table 2 | p.38, Sec. C, Table 2 | Withdrawn by ERCOT An Outage can be withdrawn by ERCOT at any time before it has a status of Completed, thus until End Date/Time has been entered | Rejected | Robert Matlock | All Withdrawn outages will be by ERCOT.
85 | TXU | 38 | D |  | p.38, Sec. D | D.2 Validation Rules for Submitting Outages . . . For the “Required Fields”, the Outage Scheduler provides two methods for Outage Submission: (1) A User Interface and (2) An XML-file upload interface (TXU: and (3) An XML-Web Services interface?). Both methods provide configurable validation of submitted data including Required Fields and their contents. The validation is through an XML-schema validation method where fields are defined as optional or required. | Clarification provided | Robert Matlock | There are three types of interface: 1. GUI 2. GUI File Upload and Download 3. WEB Services
86 | Reliant (F.Trefny) | 41 | D.3 |  | p.41, Sec. D.3 | Submittal Time Line Rules Examples of such rule sets include: • Date/Time Entry Rules Need rules for all the other outage “types” | Clarification provided * | Robert Matlock | The timing rules will be added to this document.
87 | Reliant (F.Trefny) | 41 | D.3 |  | p.41, Sec. D.3 | Submittal Time Line Rules . . . There are timing rules for the other types of outages too. | Clarification provided * | Robert Matlock | The timing rules will be added to this document.
88 | Reliant (F.Trefny) | 42 | D.6 |  | p.42, Sec. D.6 | D.6 Outage Extension Rules not allowed. You must enter a new outage to extend an existing one. Examples of such rule sets include: • Forced Extension • Unavoidable Extension • Derate Extension The respective rules are configurable. An example of such a rule is Unavoidable Extension can be requested less than 3 days from the Planned End Date/Time. The number of days can be configured to any value within an acceptable range for this specific rule (e.g., from 3 to 4 days). | Clarification provided * | Robert Matlock | See ID 10