|  |  |  |  | System Planning Division |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Monthly Status Report to Technical Advisory Committee Reliability and Operations Subcommittee for December 2006 |  |  |
|  |  | Report Highlights |  |  |  |  |  |  |
| Item |  |  |  |  |  |  |  |  |
| 1. | Analysis of Transmission Alternatives for Competitive Renewable Energy Zones (CREZ) in Texas – This analysis details the potential for wind generation development in Texas and the transmission improvements necessary to integrate new wind-generation capacity in ERCOT. The study was conducted to support the Public Utility Commission of Texas in meeting its requirements under the Public Utility Regulatory Act of 2005, Section 39.904 (g), to designate CREZs in Texas. The report can be found at: http://www.ercot.com/news/presentations/2006/ATTCH_A_CREZ_Analysis_Report.pdf |  |  |  |  |  |  |  |
| 2. | Constraints & Needs Assessment for the ERCOT Region – This report identifies and analyzes existing and potential constraints in the transmission system that could, over the next five years, either pose reliability concerns or increase costs to the electric power market. The projects identified in this report to serve the electric system through 2011 are estimated to cost approximately $3.1 billion over the next five years and are expected to improve or add 3,295 circuit miles of transmission lines and 17,900 megavolt-amperes (MVA) of autotransformer capacity to the ERCOT system. The report can be found at: http://www.ercot.com/news/presentations/2006/Attch_A_-_ERCOT_2006_Report_Transmission_System_Constraints_.pdf |  |  |  |  |  |  |  |
| 3. | Long-Term System Assessment for the ERCOT Region – This assessment represents a long-term view of the generation and transmission needs within the ERCOT region through 2016. The assessment found that significant new generation and transmission infrastructure is essential to maintain system reliability and to accommodate load growth in the ERCOT region and to offset the probable retirement of older units. The report can be found at: http://www.ercot.com/news/presentations/2006/Attch_A_-_Long_Term_System_Assessment_ERCOT_Region_December_.pdf |  |  |  |  |  |  |  |
| 4. | ERCOT Requirements to Integrate Entergy Gulf States – Texas into ERCOT: Phase II Study Report –This study builds on the screening-level analysis (Phase I) performed by ERCOT staff and Entergy Gulf States Inc. (EGSI) in early 2006 and was performed under the Commission’s instructions in Project 32217. The report identifies the minimum set of transmission projects required to reliably integrate EGSI Texas into ERCOT as well as additional economic projects that could relieve remaining transmission constraints. This report can be found at the Regional Planning Group Operations and Planning page (Combined Interest folder) of the ERCOT website http://oldercot.ercot.com/tmaps/login.cfm. |  |  |  |  |  |  |  |

1.0	Status of Active Generation Interconnection Requests

Additional information regarding detailed generation interconnection and impact studies is contained in the “Generation Project Interconnection Information” data folder posted in the “Operations and System Planning” data area on the ERCOT website.

  - New Generation Beginning Commercial Operations.

No new units started commercial operations since the last report.

1.2	Active Generation Interconnection Requests.

| GENERATION INTERCONNECTION REQUESTS CURRENTLY BEING PROCESSED |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Currently tracking 110 active generation interconnection or change requests |  |  |  |  |  |
|  |  | North | South | West | Total |
| Security Screening Study |  | 4 | 4 | 4 | 12 |
| SSS Completed |  | 6 | 11 | 14 | 31 |
| Full Interconnect Study |  | 18 | 18 | 45 | 81 |
| FIS Completed |  | 1 | 0 | 2 | 4 |
| Interconnect Agreement Completed |  | 5 | 4 | 14 | 23 |
| Capacity for Grid, MW |  | 29,522 | 24,886 | 16.873 | 71,281 |
| Wind MW (under development) |  | 620 | 4,577 | 14,142 | 19,339 |

INTERCONNECT REQUESTS CURRENTLY BEING

PROCESSED BY FUEL TYPE

| Fuel | Public | Non-public | Total |
| --- | --- | --- | --- |
| Natural gas | 2.850 | 10,145 | 12,995 |
| Nuclear | 0 | 21,986 | 21,986 |
| Coal | 11,839 | 4,052 | 15,891 |
| Wind | 2,815 | 16,524 | 19,339 |
| Other | 0 | 1,070 | 1,070 |
| Totals | 17,504 | 53,777 | 71,281 |

1.3	Potential Future Generation Interconnections.

The table below summarizes the publicly known potential future generation projects for the ERCOT region.

| FUTURE GENERATION INTERCONNECTIONS (PUBLIC PROJECTS) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| INR # | Site Name | Status | County | Region | Fuel | In Service Date | MW into Grid | Change from Last Report |
| 06INR0016 | Dow 9 | Interconnect Agreement | Brazoria | South | Gas | Dec-06 | 0 |  |
| 05INR0019 | Forest Creek 1 | Interconnect Agreement | Sterling | West | Wind | Dec-06 | 215 |  |
| 06INR0037 | Cirello 1 | Interconnect Agreement | Taylor | West | Wind | Mar-07 | 233 |  |
| 03INR0034 | Silver Star 1 | Interconnect Agreement | Erath | West | Wind | Mar-07 | 60 |  |
| 06INR0035 | Colorado Bend 1 | Interconnect Agreement | Wharton | South | Gas | Apr-07 | 275 |  |
| 06INR0036 | Quail Run 1 | Interconnect Agreement | Ector | West | Gas | Apr-07 | 275 |  |
| 06INR0038 | Scurry County 1 | Interconnect Agreement | Scurry | West | Wind | May-08 | 130 |  |
| 03INR0030 | Wild Horse 1 | Interconnect Agreement | Cottle | West | Wind | Jun-07 | 126 |  |
| 07INR0003 | Whirlwind 1 | Interconnect Agreement | Floyd | West | Wind | Sep-07 | 60 |  |
| 06INR0021 | Barton Chapel | Interconnect Agreement | Jack | North | Wind | Oct-07 | 120 |  |
| 04INR0011 | Mesquite Wind 2 | Interconnect Agreement | Shackelford | West | Wind | Dec-07 | 200 |  |
| 04INR0017 | Ocotillo Wind Farm 1 | Interconnect Agreement | Howard | West | Wind | Dec-07 | 59 |  |
| 04INR0020 | Project Snyder | Interconnect Agreement | Scurry | West | Wind | Dec-07 | 63 |  |
| 07INR0045 | Roscoe 1 | Interconnect Agreement | Scurry | West | Wind | Dec-07 | 209 |  |
| 07INR0010 | Stanton Wind 1 | Interconnect Agreement | Martin | West | Wind | Dec-07 | 101 |  |
| 06INR0035 | Colorado Bend 2 | Interconnect Agreement | Wharton | South | Gas | May-08 | 275 | Signed interconnect agreement |
| 06INR0036 | Quail Run 2 | Interconnect Agreement | Ector | West | Gas | May-08 | 275 | Signed interconnect agreement |
| 03INR0030 | Wild Horse 2 | Interconnect Agreement | Cottle | West | Wind | Aug-08 | 39 |  |
| 05INR0015 | Gulf Wind 1 | Public Letter | Kenedy | South | Wind | Sep-08 | 400 |  |
| 09INR0008 | Big Brown 3 | Public Letter | Freestone | North | Coal | Apr-09 | 858 |  |
| 09INR0010 | Martin Lake 4 | Public Letter | Rusk | North | Coal | Apr-09 | 858 |  |
| 09INR0011 | Monticello 4 | Public Letter | Titus | North | Coal | Apr-09 | 858 |  |
| 09INR0006 | Oak Grove 1 | Interconnect Agreement | Robertson | North | Coal | Apr-09 | 855 |  |
| 09INR0013 | Tradinghouse 3 | Public Letter | McLennan | North | Coal | Apr-09 | 858 |  |
| 09INR0014 | Valley 4 | Public Letter | Fannin | North | Coal | Apr-09 | 858 |  |
| 09INR0006 | Greenville | Public Letter | Hunt | North | Gas | May-09 | 1750 |  |
| 08INR0003 | Sandow 5 | Public Letter | Milam | North | Coal | Jul-09 | 585 |  |
| 05INR0015 | Gulf Wind 2 | Public Letter | Kenedy | South | Wind | Sep-09 | 400 |  |
| 09INR0009 | Lake Creek 3 | Public Letter | McLennan | North | Coal | Oct-09 | 858 |  |
| 09INR0012 | Morgan Creek 7 | Public Letter | Mitchell | West | Coal | Oct-09 | 858 |  |
| 09INR0006 | Oak Grove 2 | Interconnect Agreement | Robertson | North | Coal | Oct-09 | 855 |  |
| 09INR0013 | Tradinghouse 4 | Public Letter | McLennan | North | Coal | Apr-10 | 858 |  |
| 09INR0002 | J K Spruce 2 | Commitment | Bexar | South | Coal | Jun-10 | 750 |  |
| 05INR0015 | Gulf Wind 3 | Public Letter | Kenedy | South | Wind | Sep-10 | 400 |  |
| 10INR0002 | Hugo | Public Letter | Choctaw, OK | North | Coal | Feb-11 | 500 | In-service Date Changed |
| 11INR0001 | Twin Oaks 3 | Public Letter | Robertson | North | Coal | Jun-11 | 630 |  |
| 09INR0001 | Sandy Creek | Interconnect Agreement | McLennan | North | Coal | Sep-11 | 800 | Signed Interconnect Agreement |
|  |  |  |  |  |  | Total | 17,504 |  |

2.0	Status of RMR Contracts

The table below summaries generating units currently under RMR Contract as of December, 2006.

| RMR Units | MW | Status | Contract Dates | Planned Exit | Comments |
| --- | --- | --- | --- | --- | --- |
| Laredo 1, 2, & 3 | 172 | Under Contract | 1/1/07-12/31/07 | 3Q 2010 | N/A |
| Total MW Under RMR Contract as of March 31, 2006 | 172 |  |  |  |  |

3.0	Regional Planning Activities

The following summarizes numerous significant activities associated with regional planning issues.

3.1	Long-term System Study (SB20).

  - LTSA Report was completed and filed with PUCT

  - This long-term assessment represents a view of the generation and transmission needs within the ERCOT region through 2016. The assessment found that significant new generation and transmission infrastructure is essential to maintain system reliability and to accommodate load growth in the ERCOT region and to offset the probable retirement of older units.

3.2	CREZ Study (SB20).

  - CREZ Report was completed and filed with PUCT.  This analysis details the potential for wind generation development in Texas and the transmission improvements necessary to deliver new wind-generated capacity to electric customers

  - Analysis found that there is a significant potential for the development of wind generation in Texas. However, studies indicate that the existing transmission network is fully utilized with respect to wind transfers from West Texas to the remainder of ERCOT. New bulk transmission lines will be needed to support significant transfers of additional wind generation from the West Texas area.

  - Five-year Transmission Plan development.

  - Results of Five-Year Study were documented in Annual Report on Constraints and Needs

  - The projects identified in this report to serve the electric system through 2011 are estimated to cost approximately $3.1 billion over the next five years and are expected to improve or add 3,295 circuit miles of transmission lines and 17,900 megavolt-amperes (MVA) of autotransformer capacity to the ERCOT system.

.

3.4    Entergy Study (PUCT Project 32217:  Entergy Gulf Coast Inc.’s Plan for     Identifying Applicable Power Region Pursuant to PURA 39.452(F)).

  - Report on ERCOT study of requirements to integrate the Texas portion of the Entergy system into ERCOT was completed and filed with the PUCT

3.5      Regulatory and Policy

    - Provided presentations and information related to the CREZ analysis and other planning items to support legislative efforts

3.6	Regional Planning Group Project Reviews.

  - TNP/CNP Alvin 345kV Tie Project will be recommended for endorsement by the ERCOT Board in January.  This is a $19.4 million set of projects to provide support for TNP’s system south of Houston.

  - TXUED TNP One – East Bell County 345kV Double Circuit Project has been submitted. This is a $63 million project in north central Texas driven primarily by the proposed addition of new coal generation in the area.  Comments have been received from stakeholders, which TXUED is currently addressing, and the project will undergo ERCOT Independent Review.

  - TXUED Morgan Creek Auto project has completed ERCOT Independent Review and an endorsement letter is in preparation.

  - TXUED Seagoville Auto project has completed ERCOT Independent Review and an endorsement letter is in preparation.

  - TXUED Anna-Collin-NW Carrollton has been submitted and is currently in ERCOT Independent Review.

  - BEC Granbury-Stephenville 69kV Project has completed ERCOT Independent Review and an endorsement letter is in preparation.

  - Other Projects/Studies

    - Morgan Creek 6 and Mountain Creek Unit 2 were determined not to be needed for RMR service

    - Results of new LOLP study will be presented to GATF in January

4.0	Transmission Services Activities

4.1 	Dynamic Analysis and Modeling.

- Study of dynamic limits for power transfer out of West Texas

      - Completed study with additional simulations to test sensitivities to generation dispatch.

    - Compiled necessary data associated with 2006 Wind Flat Start and sent to LCRA’s Tom Bao for inclusion in the 2006 DWG Stability Book.

    - Continuing to support PTI in the development of combined cycle power plant stability models.

      - Provided assistance in resolving discrepancies between EMS test cases and dynamics data from planning.

    - Supporting ongoing DWG efforts to develop a transient voltage recovery criteria and draft requirements for field testing of NERC generator performance standards (PRC-019,PRC-024,MOD-026,MOD-027).

      - Reviewing comments on OGRR 188

    - Supporting System Operations (Shun-Hsien Huang) in the analysis and enforcement of real time voltage stability limits and transient stability limits.

    - Models for Suzlon wind turbines tested for compilation and/or simulation issues – part of ongoing simulation testing of wind models as they become available.

    - High tier underfrequency load shedding study.  Perform simulation runs using PSSe and TSAT to assess the impact of a few loads participating in the new high-frequency tier scheme.

    - Supporting testing and implementation real-time CSC limit calculation function with VSAT in EMS. Providing work around suggestion or fixes to the problems identified during the testing.

    - Review of dynamic studies produced by TO’s associated with generation interconnection projects into ERCOT.

    - Supporting dynamic studies associated with the proposed integration of Entergy into ERCOT.  Review of Phase II draft Final Report from Powertech done.

  - Case Building.

- 2007 Data Set B cases were completed and posted

4.3	Network Model Management System (NMMS) Support.

- Working on how to resolve Operations to Planning model conversion issues

- Attended CIM for planning meeting in Ft. Worth Dec 12-13

- Meet with STEC about NMMS

4.4	Load Forecasting.

ERCOT Staff:

- Continues to update the Load Shape and Energy forecasting models for the preparation of the 2007 long-term peak and energy demand forecast.

- Continues to update the load, temperature and economic/demographic data.

- Calculated a 90th percentile (cold temperature) forecast scenario for the winter using the 2006 long-term forecasting model.

- Continue to improve user friendliness, efficiency and performance of forecasting programs for production purposes.

  - Studies underway or planned within System Planning Division

- Attending Meetings with Market Redesign Web Developers to discuss the new and improved T-Maps website.

4.6     Congestion Management Working Group Support

- Performed February TCR calculations

4.7 	Engineering Graphics Analysis

- Maintained and updated AutoCAD Transmission Network System map.

- Updated AutoCAD Transmission map to match Data Dictionary, new SCSC zones, line and station additions as requested and added scale and county index. Maps now available in three sizes.

- Updating AutoCAD Transmission map to match Power World map and one-line diagram information.

- Created area maps for reports (JPEG, DXF or wmf  format) as requested.

- Plotted Transmission, Zone and area maps for mailing and internal use.

- Upcoming Events/Deadlines

January

- NERC TIS meeting January 10-11

February

- TAC ROS Dynamics Working Group (DWG) meeting; February 7-8

- LaaR data for inclusion in DWG dynamics data file due; February 15

- TPIT updates are due to Jan Grisham no later than February 1st

- Donate blood after February 9

March

- March 1 ALDR data due to ERCOT

- OTHER ISSUES

- Provide support to ERCOT settlements for new station CM Zone identification

7.0	CSC UTILIZATION   Q3 – 2006

  - CONGESTION CHARGES COLLECTED FROM QSE

| $Million | E_N | N_H | S_H | S_N | W_N | N_W | TOTAL |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2006 Yr to date | 7.4 | 7.4 | 13.8 | 1.2 | 0.2 | 3.0 | 33.0 |
| 2005 Yr to date | 0 | 6.4 | 33.6 | 8.5 | ~0 | 3.9 | 52.4 |
| 2005 total | 0 | 25.7 | 39.2 | 8.9 | ~0 | 5.3 | 79.0 |

  - INTERVALS OF BINDING CONSTRAINTS

|  | E_N | N_H | S_H | S_N | W_N | N_W |
| --- | --- | --- | --- | --- | --- | --- |
| 2006 total | 185 | 393 | 738 | 571 | 44 | 361 |
| 2005 total | 0 | 884 | 1516 | 1135 | 11 | 328 |

  - ZONAL CONGESTION OCCURRENCES – INTERVALS

|  | N_H |  | S_H |  | S_N |  | E_N |  | N_W |  | W_N |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Active | Binding | Active | Binding | Active | Binding | Active | Binding | Active | Binding | Active | Binding |
| Jan | 0 | 0 | 10 | 10 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 |
| Feb | 0 | 0 | 18 | 13 | 131 | 89 | 0 | 0 | 13 | 8 | 0 | 0 |
| Mar | 7 | 6 | 8 | 5 | 0 | 0 | 18 | 16 | 0 | 0 | 2 | 2 |
| Apr | 131 | 106 | 236 | 186 | 5 | 0 | 173 | 164 | 14 | 2 | 7 | 2 |
| May | 100 | 68 | 175 | 130 | 42 | 33 | 2 | 2 | 34 | 21 | 0 | 0 |
| Jun | 27 | 17 | 254 | 173 | 85 | 56 | 0 | 0 | 151 | 128 | 12 | 9 |
| Jul | 26 | 16 | 157 | 72 | 325 | 232 | 0 | 0 | 61 | 43 | 9 | 9 |
| Aug | 27 | 18 | 129 | 78 | 213 | 129 | 0 | 0 | 187 | 147 | 11 | 8 |
| Sep | 195 | 162 | 82 | 71 | 33 | 21 | 1 | 1 | 12 | 12 | 18 | 14 |
| Oct |  |  |  |  |  |  |  |  |  |  |  |  |
| Nov |  |  |  |  |  |  |  |  |  |  |  |  |
| Dec |  |  |  |  |  |  |  |  |  |  |  |  |
| 2006 total | 513 | 393 | 1069 | 738 | 850 | 571 | 192 | 185 | 472 | 361 | 59 | 44 |
| 2005 | 1239 | 884 | 2127 | 1516 | 1578 | 1135 | 0 | 0 | 569 | 328 | 22 | 11 |
| total |  |  |  |  |  |  |  |  |  |  |  |  |

For additional information, go to http://www.ercot.com/calendar/2006/12/20061213-WMS.html and look at item #4.