## Slide 1: Compliance Update
February 2007

## Slide 2: Control Performance Highlights
NERC CPS1 Performance
  December performance indicated a sixth straight month of declining scores since scores peaked in June
    June – 154.6
    December – 129.5
  Month-to-date score as of January 24th – 137
PRR 525 Performance
  Initial scores for December indicate 34 QSEs passed / 1 non-wind-only QSEs failed the measure
  Scores posted on the ERCOT Compliance Website

## Slide 3: ERCOT CPS1 Performance Comparison

## Slide 4: ERCOT’s CPS1 Monthly Trend

## Slide 5: ERCOT CPS1 by Interval

## Slide 6: QSE PRR525 10-Minute Interval Scoring

## Slide 7: December 2006 Resource Plan Performance Metrics

## Slide 8: SCE Performance Monitoring
SCE Performance Monitoring scores for all QSEs are published on the Compliance Website
  SCE Performance Scores

## Slide 9: 525 Passing 10-Min Interval Percentage Trends

## Slide 10: October 3, 2006 Event
Initiated at Gibbons Creek Substation in Bryan/College Station Area
  138 kV coupling capacitor voltage transformer (CCVT) failed catastrophically
  Current-sensing components of the backup protective relay failed due to high fault current
1,214 MW of generation lost – NERC Disturbance Control Standard (DCS) Event
  Frequency recovered to pre-disturbance level in approximately 3 minutes – NERC criteria met; no NERC Reliability Standards violation

## Slide 11: October 3, 2006 Event
ERCOT deployed all RRS being provided by LaaRs in accordance with ERCOT DCS Event Operating Procedures
Six of ten QSEs with LaaR RRS awards did not respond with 95% of their award within 10 minutes
  642 MW tripped – 1,150 MW obligation
  Took over 20 minutes to achieve 95% of obligation
Seven Protocol Violation Notices issued
  Six notices related to Section 6.5.4(2) – tripping requirements for LaaR
  One notice related to Section 6.5.1.1(4) – telemetry requirements
339 MW of firm load shed in area
No NERC Interconnected Reliability Operating Limit (IROL) violations

## Slide 12: LaaR Deployment 10/3/2006

## Slide 13: October 3, 2006 Event
Series connection of protective relays is contrary to current ERCOT Operating Guides for new equipment
  Station equipment installed prior to current requirements
  No issues identified with coordination studies or maintenance
Equipment issues addressed
  Failed CCVT replaced – CCVTs on other two phases also replaced
  Failed relay replaced – current transformer (CT) ratio adjusted to reduce current sensed during faults
  Additional CTs purchased to eliminate series current connections shared by primary and backup relaying

## Slide 14: October 3, 2006 Event
Continuing to investigate:
  Events leading up to CCVT failure
  Restoration activities
To meet NERC Planning Criteria, three transmission projects had been previously identified to address known risks – work still in progress. One project complete; completion of remaining projects scheduled by Summer 2008

## Slide 15: LaaR Deployment 12/22/2006