Remedial Switching Action

Statement of the problem

A new outage scheduler category is needed because some switching actions either cannot be entered in the outage scheduler due to violation of the timing rules (must be entered at least 3 days in advance), or do not meet the definition of forced outages.

In the ERCOT system there are switches and breakers that may be opened or closed to prevent pre or post contingency violations in real time. Normally, TSPs and ERCOT identify and document any such switching actions as part of the Network Operations Model definition of Remedial Action Plans (RAPs). However, during evaluation of Planned or Maintenance Outages or unusual operating conditions, a new Remedial Switching Action may be identified by ERCOT or the TSP to mitigate contingency violations brought on by the outage under evaluation or unusual operating conditions.  In such cases, a Remedial Switching Action shall be entered in the Outage Scheduler.   Remedial Switching Actions should be transparent to Market Participants as any other transmission outage.

If these switching actions are not entered in the outage scheduler, the DAM and DRUC process will not recognize the change in network topology, and may misinform the market about projected congestion.

Recommendations

Allow an outage type in the Outage Scheduler describing “Remedial Switching Actions”. Limit the length of the Remedial Switching Action to a maximum of 3 days. Allow proposal of such actions no more than 2 day in advance. If the Remedial Switching Action is required to remain active for longer than 3 days, a  planned outage will be submitted to change the position of effected breakers and switches or a Remedial Action Plan will be created. Breakers and switches in a Remedial Switching Action must be able to be returned to their normal position in 4 hours or less (this allows for drive time for remote switches w/o SCADA). An explanation for need of the Remedial Switching Action is required and is posted with the sequence of breaker and switch status changes defining the plan.

ERCOT must approve all Remedial Switching actions prior to implementation and make the information visible to the market. ERCOT shall produce statistics reporting use of the “Remedial Switching Actions” as a separate category in addition to those described in section 3.1.3.1.