ERCOT Nodal Operating Guides

Section 4:  Emergency Operation

Draft (Month, Day, Year)

(Effective Upon Texas Nodal Market Implementation)

Contents

4	Emergency Operation	3

4.1	Introduction	3

4.2	Emergency Notifications	4

4.2.1	Operating Condition Notice	4

4.2.2	Advisory	4

4.2.3	Alert	4

4.2.4	Emergency Notice	5

4.3	Operation to Maintain Transmission System Security	6

4.3.1	Remedial Action Plans (RAP)	6

4.4	Block Load Transfers between ERCOT and Non-ERCOT System	8

4.5	Emergency Electric Curtailment Plan (EECP)	9

4.5.1	General	9

4.5.2	Operating Procedures	9

4.5.3	Implementation	10

4.5.3.1 	General Procedures Prior to EECP Operations	10

4.5.3.2 	General Procedures During EECP Operations	11

4.5.3.3	EECP Steps	12

4.5.3.4	Load Shed Obligation	12

4.5.3.3	EECP Termination	13

4.6	Black Start Service	15

4.6.1	Principles	15

4.6.2	Strategies	15

4.6.3	Priorities	16

4.6.4	Responsibilities	17

4.6.5	Black Start Emergency Back Up Communication Facilities Criteria	18

# P

# 4	Emergency Operation

4.1	Introduction

(1)	Emergency operation is intended to address operating conditions under which the reliability of the ERCOT System is inadequate and there is no solution readily apparent.  During a declared system emergency, ERCOT can instruct Transmission Operators (TOs) and Qualified Scheduling Entities (QSEs) to take specific operating actions that would otherwise be discretionary.  Upon receiving a Valid Dispatch Instruction (VDI) from ERCOT, and in compliance with the Operating Guides, the QSEs shall direct relevant Resources or groups of Resources to respond to the instruction.  ERCOT shall coordinate with QSEs and TOs to assure that necessary actions are taken to maintain reliability.

(2)	It is essential that good, timely, and accurate communication routinely occur between ERCOT, TOs, and QSEs.  QSE and TO personnel shall report unplanned equipment status changes as outlined in this section.  ERCOT System operators may ask for status updates as required in order to gather information to make decisions on system conditions to determine what type of emergency communication may be appropriate.

(3)	ERCOT may issue communications in the form of notices, Advisories, Alerts and emergency notices.  These communications may relate to but are not limited to, weather, transmission, computer failure, or generation information.  ERCOT shall specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. These communications will be issued by ERCOT to inform all TOs and QSEs of the current operating situation.  TOs will notify their represented Transmission Service Providers (TSPs) and Load Serving Entities (LSEs).  QSEs will in turn notify the appropriate Resources, Retail Electric Providers (REPs) and LSEs.  QSEs and TOs shall establish and maintain internal procedures for contingency preparedness or to expedite the resolution of the conditions communicated by ERCOT that threaten system reliability.

(4)	Before deciding which emergency communication to issue, ERCOT must consider the possible severity of the operating situation before an Emergency Condition occurs.  If practicable, the market shall be allowed to attempt to mitigate or eliminate any possible Emergency Condition. ERCOT has the responsibility to issue the appropriate communications to facilitate a solution by Market Participants.

4.2	Emergency Notifications

4.2.1	Operating Condition Notice

(1)

An Operating Condition Notice (OCN) will be issued by ERCOT in accordance with Protocol Section 6.5.9.3.1, Operating Condition Notice.  OCNs are for communication only, and ERCOT exercises no extra authority with the issuance of this type of notice.

(2)	ERCOT may require information from QSEs and TOs.  Typical information requested may include, but is not limited to:

(a)	Resource fuel capabilities;

(b)	Resource condition details; and

(c)	Actual weather conditions

(3)	ERCOT will provide verbal notice of an OCN to all TOs and QSEs and post the message electronically to the MIS Secure Area.

TOs should notify their represented TSPs as appropriate of OCN’s.

4.2.2	Advisory

(1)	An Advisory will be issued by ERCOT in accordance with Protocol Section 6.5.9.3.2, Advisory, when it recognizes that conditions are developing or have changed such that QSE and/or TO actions  may be prudent in response to impending severe conditions.

(2)	ERCOT may require information from QSEs and TOs.  Typical information requested may include, but is not limited to:

(a)	Resource fuel capabilities;

(b)	Resource condition details; and

(c)	Actual weather conditions.

(3)	ERCOT shall provide verbal notice of an Advisory to all TOs and QSEs and shall post the message electronically to the MIS Secure Area.  When an Advisory is issued, it does not place ERCOT in an emergency operating state.

QSEs shall notify appropriate Resources, REPs and LSEs of Advisories.

TOs should notify their represented TSPs as appropriate of Advisories.

4.2.3	Alert

(1)	An Alert may be issued by ERCOT in accordance with Protocol Section 6.5.9.3.3, Alert, when it recognizes that conditions have developed such that an insecure operating state exists or is imminent.

(2)

ERCOT may require information from QSEs and TOs.  Typical information requested may include, but is not limited to:

(a)	Resource fuel capabilities;

(b)	Resource condition details; and

(c)	Actual weather conditions.

(3)	When a post-contingency overload of a non-critical element can not be rectified by congestion management methods or a mitigation pPan, ERCOT shall issue an Alert. A “non-critical element” is one whose loss will not result in an uncontrolled separation of cascading outages or large scale service disruptions to Load or overload of a critical transmission element.

(4)	ERCOT shall provide verbal notice of the Alert to all TOs and QSEs and shall post the message electronically to the MIS Secure Area.  While operating under an Alert, ERCOT is operating in an emergency operating state.

QSEs shall notify appropriate resources, REPs and LSEs.

shall

4.2.4	Emergency Notice

(1)	An emergency nNtice will be issued by ERCOT in accordance with Protocol Section 6.5.9.3.4, Emergency Notice.   ECOT is considered to be in an insecure state whenever ERCOT Transmission Grid status is such that the most severe Credible sSngle -cntingency event presents the threat of uncontrolled separation of cascading outages and/or large-scale service disruption to Load (other than Load being served from a single-feed transmission service) and/or overload of a critical Ttrnsmission Eelment, and no timely solution is obtainable from the market.

(2)	ERCOT shall provide verbal notice of an emergency nNtice to all TOs and QSEs and shall post the message electronically to the MIS Secure Area.

(3)	When an emergency notice is issued, ERCOT is operating in an emergency operating condition. QSEs shall notify appropriate resources, REPs and LSEs.  TOs shall notify their represented TSPs and LSEs.

emergency operating state.QSEs shall notify appropriate resouc

.

4.3	Operation to Maintain Transmission System Security

(1)	ERCOT operators are responsible for operating the ERCOT System within first contingency transfer limits so that there is no overload of any significant transmission element whose loss could jeopardize the reliability of the ERCOT System. Whenever the ERCOT System is not engaged in emergency operation, it will be operated in such a manner that the occurrence of a credible single contingency will not cause any of the following:

(a)		Uncontrolled breakup of the transmission system;

(b)		Loading of Transmission Facilities above defined emergency ratings which can not be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures;

(c)		Transmission voltage levels outside system design limits which can not be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs; or

(d)		Customer Outages, except for high set interruptible and radially served loads.

(2)	Significant Transmission Overload – ERCOT can:

(a)	Order adjustment to unit generation schedules, switching of Transmission Elements or Load interruption to relieve a severely overloaded Transmission Element;

(b)	Order a Transmission Element whose loss would not have a significant impact on the reliability of transmission system switched out to increase interconnected system transfers.

(3)	Violation of “First Contingency” Criteria – ERCOT can

order changes to unit dispatch or commitment to eliminate a “first contingency” criteria violation.  Normally these changes should be performed via the market control mechanisms of constraint management as described in the Protocols, but ERCOT operators have the authority to issue valid Dispatch Instructions independent of these systems.

(4)	Violation of Voltage/Reactive Criteria – ERCOT can order changes in unit dispatch if coordinated voltage and Reactive Power criteria that are considered critical to interconnection reliability are violated for the existing or first contingency conditions.

(5)		Total or Partial System Blackout – ERCOT shall implement Black Start procedure.

|  | CONTR |
| --- | --- |
|  | - The Co - The C |
|  | The C |
|  | The Co |

(5)	TDSP operators are responsible for operating the sub-transmission system within safe operating limits, for maintaining the transmission system, for performing all switching operations after coordinating with ERCOT, and for notifying ERCOT operators of threats to, or overloads of the transmission system under their supervision.

(1)	Generation facilities or constrained Transmission Elements that would otherwise be subject to restrictions can operate to full rating if appropriate Special Protection Systems (SPS) or Remedial Action Plans (RAPs) are in place.  See Section 7.2.2, Design and Operating Requirements for ERCOT System Facilities, for SPS requirements.  A RAP refers to predetermined operator actions to maintain reliability in a defined adverse operating condition.  Normally, it is desirable that a TSP constructs Transmission Facilities adequate to eliminate the need for any RAP; however, in some circumstances, such construction may be unachievable in the available time frame.

(2)	A RAP may be proposed by any ERCOT Market Participant, but must be approved by ERCOT prior to implementation.  RAPs must meet the following requirements:

(a)	Be

coordinated and approved with the operators of facilities included in the RAP;

(b)	Limit use to the time required to construct replacement Transmission Facilities;  however, the RAP will remain in effect if replacement Transmission Facilities have been determined by ERCOT to be impractical;

(c)	Comply with all applicable ERCOT and NERC requirements;

(d)

Clearly define and document operator actions;

(e)	Include the option for the transmission operator to override the procedures if the RAP will not improve system reliability;

(f)	Operators must be trained in RAP implementation; and

(g)	Be defined in the Network Operations Model and considered in the Security-Constrained Economic Dispatch (SCED) and reliability unit commitment.  RAPs S whichthat cannote ed using ERCOT’s existing infrastructure shall be refused or a plan developed to work around the infrastructure problem which is explicitly approval by the Technical Advisory Committee (TAC).

4.4	Block Load Transfers between ERCOT and Non-ERCOT System

Under Alert, Emergency Electric Curtailment Plan (EECP) conditions, or for local transmission constraints, it may become necessary to  implement Block Load Transfer (BLT) schemes which will transfer loads normally located in ERCOT to a non-ERCOT System.  Similarly, when a non-ERCOT System experiences certain transmission contingency or short supply conditions, ERCOT may be requested to transfer Loads normally located in the non-ERCOT System to ERCOT. All BLTs must comply with Protocol Section 6.5.9.5, Block Load Transfers between ERCOT and Non-ERCOT Control Areas.

4.5	Emergency Electric Curtailment Plan (EECP)

4.5.1	General

(1)	At times it may be necessary to reduce electrical demand because of a temporary shortfall in available electricity supply.  The reduction in supply could be caused by emergency outages of generators, transmission equipment, or other critical facilities; by short-term unavailability of fuel or generation; or by requirements or orders of government agencies.  To provide an orderly, predetermined procedure for curtailing demand during such emergencies, ERCOT has established this Emergency Electric Curtailment PlanEECP in accordance with Protocol Section 6.5.9.4, Emergency Electric Curtailment Plan.

(2)	The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.

4.5.2	Operating Procedures

(1)	The ERCOT System oOperators have the authority to make and carry through decisions that are required to operate the ERCOT System during emergency or adverse conditions. ERCOT will have sufficiently detailed operating procedures for emergency or short supply situations and for restoration of service in the event of a partial or complete system shutdown.  These procedures will be distributed to the personnel responsible for performing specified tasks to handle emergencies, remedy short supply situations, or restore service.  TSPs will develop procedures to be filed with ERCOT describing implementation of ERCOT requests in emergency and short supply situations, including interrupting load, notifying others and restoration of service.

(2)	ERCOT and each TSP will endeavor to maintain transmission ties intact if at all possible.  This will:

(a) Permit rendering the maximum assistance to an area experiencing a deficiency in generation;

(b) Minimize the possibility of cascading loss to other parts of the system; and

(c) Assist in restoring operation to normal.

(3)	ERCOT's operating procedures will meet the following goals while continuing to respect the confidentiality of market sensitive data.  If all goals cannot be respected simultaneously then the priority order listed below shall be respected:

(a)	Maintain station service for nuclear generating facilities;

(b)	Securing startup power for power generating plants;

(c)	Operating generating plants isolated from ERCOT without communication;

(d)	Restoration of service to critical loads such as:

(i)	Military facilities;

(ii)	Facilities necessary to restore the electric utility system;

(iii)	Law enforcement organizations and facilities affecting public health; and

(iv)	Communication facilities

(e)	Maximum utilization of ERCOT System Capability;

(f)	Utilization of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(g)	Utilization of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT System; and

(h)	Restoration of service to all customers following major system disturbances, giving priority to the larger group of customers.

4.5.3	Implementation

(1)	ERCOT shall be responsible for monitoring system conditions, initiating the EECP steps below, notifying all QSEs and TOs, and coordinating the implementation of the EECP Conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants they represent of each declared EECP Step.

(2)	ERCOT has the authority to obtain emergency assistance energy over the Direct Current (DC) tie(s) for use by ERCOT.  ERCOT is also the coordinating authority for requests for emergency type power into or out of ERCOT.

(3) 	ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation.

(4)	There may be insufficient time to implement all steps in sequence.  ERCOT can immediately implement Step 3 of the EECP any time the system frequency is below 59.8 Hz and will immediately implement Step 3 any time the frequency is below 59.5 Hz.

(5)	Percentages for Step 3 Load shedding will be based on the previous year's TSP peak Load, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

(6)	The ERCOT System Operator shall declare the EECP steps to be taken by QSEs and TSPs.  QSEs and TSPs shall implement actions under that Step (and all above if not previously accomplished) and if ordered by the ERCOT Shift Supervisor or his designate, shall report back to the ERCOT System Operator when the requested step has been completed.

4.5.3.1 General Procedures Prior to EECP Operations

Prior to declaring EECP Step 1 detailed in Section 4.5.3.3, EECP Steps, ERCOT shall:

(1)	Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability;

(2)	Issue Dispatch Instructions to QSEs to suspend any ongoing ERCOT required generating unit testing;

(3)	Utilize Non-Spin Reserve Services that can be deployed to increase Responsive Reserves;

(4)	ERCOT shall use the Reserve Discount Factor (RDF) for the purpose of monitoring Physical Responsive Capability.  The Physical Responsive Capability will be used by ERCOT to determine the appropriate Emergency Notification and EECP Steps; and

(5)	In addition, ERCOT may issue an appeal through the public news media for voluntary load reduction if authorized by the ERCOT Chief Executive Office or its designee based on an evaluation of existing and expected system conditions.

4.5.3.2	General Procedures During EECP Operations

ERCOT Control Area Authority will re-emphasize the following operational practices during EECP operations to minimize non-performance issues that may result from the pressures of the emergency situation.

(1)	ERCOT shall suspend Ancillary Service Obligations that it deems to be contrary to reliability needs;

(2)	ERCOT shall notify each QSE and TO via hotline of declared EECP Step;

(3)	QSEs and TOs shall notify each represented Market Participant of declared EECP Step;

(4)	ERCOT, QSEs and TSPs shall continue to respect confidential market sensitive data;

(5)	QSEs shall update Resource Plans to limit or remove capacity when unexpected start-up delays occur or when ramp limitations are encountered;

(6)	QSEs shall report when online or available capacity is at risk due to adverse circumstances;

(7)	QSEs, TSPs, and all other Entities must not suspend efforts toward expeditious compliance with the applicable EECP Steps declared by the ERCOT nor initiate any reversals of required actions without ERCOT authorization;

(8)	ERCOT shall define procedures for determining the proper redistribution of reserves during EECP operations.

4.5.3.3	EECP Steps

Step 1 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal To 2300 Mw

(1)	ERCOT shall:

(a)	Utilize available DC tie capability that is not already being used by the market;

(b)	Notify the Southwest Power Pool Security Coordinator; and

(c)	Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency.

(2)

QSEs shall notify ERCOT of any resources uncommitted but available in the timeframe of the emergency.

Step 2 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW Provided from LaaR Equal To 1750 MW

(1)	In addition to measures associate with STEP 1, ERCOT shall:

(a)	Instruct TSPs to reduce customer loads by using distribution voltage reduction measures, if deemed beneficial by the TSP;

(b)	Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (LaaRs) (controlled by high-set under-frequency relays); and

(c)	With approval of the affected Non-ERCOT control area, may instruct TDSPs to implement Block Load Transfer, which transfer load from the ERCOT control area to Non-ERCOT control areas.  Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation.

Step 3 - Maintain System Frequency at 59.8 Hz Or Greater

(1)	In addition to measures under Steps 1 and 2, ERCOT shall direct all TSPs and their agents to shed firm load, in 100 MW blocks, distributed as agreed and documented in the ERCOT Operating procedures in order to maintain a steady state system frequency of 59.8 Hz;

(2)	In addition to measures under Steps 1 and 2, TSPs shall, keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs shall not manually drop load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan;

4.5.3.4	Load Shed Obligation

Obligation for load shed is by DSP.  Load shedding obligations need to be represented by an entity with 7x24 operations and hotline communications with ERCOT and control over breakers.  [Use Transmission Operators (TOs) as list of entities.]

ERCOT Load Shed Table

| Transmission Operator | 2005 Total Transmission Operator Load (MW) |
| --- | --- |
| American Electric Power | 9.50 |
| Austin Energy | 3.90 |
| Brazos Electric Power Cooperative | 3.89 |
| CenterPoint Energy | 24.56 |
| City of Bryan | 0.53 |
| City of College Station | 0.29 |
| City of Denton | 0.50 |
| City of Garland | 0.99 |
| City Public Service of San Antonio | 7.05 |
| Lower Colorado River Authority | 4.96 |
| Magic Valley Electric Cooperative | 0.53 |
| Public Utility Board of Brownsville | 0.41 |
| Rayburn Country Electric Cooperative | 1.00 |
| South Texas Electric Coop-Medina Electric Coop | 0.60 |
| Texas New Mexico Power | 2.26 |
| Tex-La | 0.15 |
| TXU-Electric Delivery | 38.88 |
| ERCOT Total | 100.00 |

4.5.3.3	EECP Termination

(1)	ERCOT shall:

(a)	Continue EECP until sufficient resources are available to ERCOT to eliminate the shortfall and restore adequate reserves;

(b)

Restore full reserve requirements (normally 2300 MW);

(c)	Terminate the steps in reverse order, where practical;

(d)	Notify each QSE and TO of EECP Step termination; and

(e)	Maintain a stable ERCOT System frequency when restoring Load.

(4)	QSEs and TOs shall:

(a)	Implement actions to terminate previous actions as EECP steps are released in accordance with these guides;

(b)	Notify represented Market Participants of EECP Step changes;

(c)	Report back to the ERCOT System Operator when each Step is accomplished; and

(d)	Loads will be restored when specifically authorized by the ERCOT.

4.6	Black Start Service

(1)	This section provides general guidelines to be followed in the event of a partial or complete collapse of the ERCOT system. Timely implementation of a restoration plan compiled according to these Operating Guides should facilitate coordination between ERCOT, QSEs, Resource Entities, and TOs and ensure restoration of service to the ERCOT System at the earliest possible time.  Those QSEs representing contracted Black Start Uesources will provide ERCOT with the individual plant start-up procedures for coordination of their activities with those of the appropriate TO.

(2)	Pre-established plans and procedures cannot foresee all the possible combinations of system problems that may occur after a major failure.  It is the responsibility of ERCOT to restore the system to normal, applying the principles, strategies, and priorities outlined in the ERCOT Black Start Plan.

4.6.1	Principles

(1)	In order to minimize the time required, ERCOT will develop the Black Start Plan to utilize the principles, strategies, and priorities outlined in this Gguide.   The ERCOT Black Start Plan shall be coordinated with local TO Black Start Plans, to provide a coordinated Black Start Rresource.

(2)	ERCOT shall establish and maintain a system Black Start capability plan that shall be coordinated, as appropriate, with the black start capability plans of neighboring regions. Documentation of system Black Start capability plans shall be provided to NERC on request.

(3)

Each contracted Black Start Uesource and each QSE with contracted Black Start uUsource(s) will have readily accessible and sufficiently detailed current operating procedures to assist in an orderly recovery.

(4)	Mutual assistance and cooperation will be essential during the restoration.  Deliberate, careful action by each QSE, TO, and Resource Entity is necessary to minimize the length of time required for restoration and to avoid the reoccurrence of a partial or complete collapse.

(5)	Throughout the restoration, recovery will depend on ERCOT receiving an accurate assessment of system conditions and status from each QSE, TO, and Resource Entity throughout the restoration.  Adequate and reliable communications must be available within the ERCOT System.  During Black Start recovery, communication restrictions are lifted to enable the sharing of that information that pertains to reliability including status information and recovery activities.

4.6.2	Strategies

In the event of a partial or complete system blackout, immediate steps must be taken to return the interconnected network to normal as quickly as possible.  For detailed Black Start Information, refer to Section 9 of these Operating Guides.

(1)	Each TO shall immediately initiate its portion of the Black Start procedure and attempt to establish contact with ERCOT.  If communications with ERCOT are unavailable the TO shall immediately establish communications with its interconnected Black Start Uesource(s) and the Black Start uUsource’s QSE.

(2)	Each QSE with representing Black Start Uesources should initiate communications with its Black Start uUsources and immediately notify ERCOT and the appropriate TO of their condition and status.

(3)	Available Black Start Resources should immediately start their isolation and startup procedures and attempt to establish communications with the local TO.

(4)	As generating and transmission capabilities become available, systematic restoration of ERCOT Load with respect to priorities should begin in accordance with the local TO Black Start plans, taking care to balance load and generating capability while maintaining an acceptable frequency.

(5)	Appropriate voltage levels and reactive control must be maintained during the restoration.  Consideration should be given to connecting islands at locations having communications, frequency control, voltage control, synchronization facilities, and adequate transmission capacity.  ERCOT will coordinate the return to full Automatic Generation Control (AGC) in the interconnection.

4.6.3	Priorities

Priorities for an ERCOT Ssystem restart are listed below:

(1)	Secure and/or stabilize generating units where necessary.

(2)	Prepare transmission corridors as necessary to support restoration.

(3)	Assess ERCOT System condition, and available communication facilities.

(4)	Restore and maintain communication facilities to the extent possible.

(5)	Bring units with contracted black start capability on-line.

(6)	Provide service to critical facilities:

(a)	Provide station service for nuclear generating facilities.

(b)	Provide critical power to as many power plants as possible to prevent equipment damage.

(c)	Secure or provide startup power for generating plants that do not have black Start capability.

(d)	Supply station service to critical substations where necessary.

(7)	Connect islands at designated synchronization points taking care to avoid recurrence of a partial or complete system collapse.

(8)	Restore service to critical loads such as:

(a)	Military facilities;

(b)	Facilities necessary to restore the electric utility system, including fuel sources;

(c)	Law enforcement organizations and facilities affecting public health; and

(d)	Public communication facilities.

(9)	Restore service to the remaining customers.  Attention should be given to restoring feeders with under-frequency relay protection.

### 4.6.4	Responsibilities

(1)	ERCOT’s responsibilities are as follows:

(a)	Shall maintain a Black Start plan in accordance with NERC Peliability Standards.

(b)	Coordinate and approve Planned Outage schedule for contracted Black Start units.

(c)	Train QSE, TO, Resource Entity, and Market Participant personnel in the implementation and use of the Black Start plan.

(d) 	Will review the plans and procedures for consistency and conformance with this guide and ensure that they are updated at least annually.

(e) 	Will make annual reports during the first quarter to the Reliability and Operations Subcommittee of plan review and any testing activities of Black Start Generation Resources.

(f) 	Shall verify that the number, size, and location of system Black Start Generation Resources are sufficient to meet system restoration plan expectations.

(g)	In the event of an ERCOT System collapse, ERCOT will:

(i)	Maintain continuous surveillance of the status of the ERCOT System

(ii)	Act as a central information collection and dissemination point for the region

(iii)	Coordinate reconnection of transmission

(iv)	Direct assistance for QSEs, TOs, Resource Entities, and Market Participants.

(v)	Direct the distribution of reserve.

(vi)	Coordinate the return of the ERCOT System to Automatic Generation Control.

(2)	Transmission Operators responsibilities are as follows:

(a)	Shall maintain a local Black Start plan which coordinates with the ERCOT Black Start pPan

(b)	In event of an ERCOT or wide are blackout:

(i)	Shall communicate with local Black Start uUnits and the Black Start uUnit’s QSE.

(ii)	Coordinate switching to next start units nd local Load.

(iii)	Shall implement its local Black Start plan.

(iv)	Shall follow the direction of ERCOT on behalf of represented TDSPs.

(v)	Shall act as the regional ERCOT representative in coordinating interconnection of units

(vi)	Shall follow the direction of ERCOT for reconnection of islands

(3)	QSEs, Resource Entities, and Market Participants responsibilities are as follows:

(a)	Shall use the ERCOT and local TO Black Start plan

(b)	Verify that associated personnel are proficient in its implementation and use.

(c)	In the event of an ERCOT System collapse, the QSEs, Resource Entities, and Market Participants will:

(i)	Take immediate steps to initiate the local Black Start pPlan.

(ii)	Supply ERCOT and/or the local TO with information on th status of generation, fuel, transmission, and communication facilities.

(iii)	Follow the direction of the local TO or ERCOT in picking up local Load and starting next units.

(iv)	Provide available assistance as directed by ERCOT or the local TO.

(4)	Attachment 9A, Detailed Black Start Information, provides a detailed and specific Black Start information guide.  Interested parties should use this information for technical reference material, Black Start testing, development of Black Start plans, and training of personnel.

4.6.5	Black Start Emergency Back Up Communication Facilities Criteria

(1)

All Black Start emergency back up communications should have voice recording capabilities.  To prepare for a blackout event, any back-up communications system shall meet the following minimum requirements:

(a)	Be operational for 72 hours immediately following the start of a blackout without external power from the ERCOT system;

(b)	Provide direct voice communications between Black Start Resource and TO, TO and appropriate TO, and TO and ERCOT;

(c)	Maintain written procedures that address operator training and the testing of the communication system; and

(d)	Comply with ERCOT communications standards in these Operating Guides.

(2)	In addition, public communications services used for back-up must be limited to systems that are not oversubscribed.  Public communication services and dedicated lease lines must be available for 72 hours immediately following the start of a blackout without external power from the ERCOT system.

The TO operators should:

The Black Start facilities should:

Attempt to communicate with their TO.

Start black start facility and request load interconnection from TO.

thintween islands to insure

F

, that the unit can perform its intended

s.

, QSE, and TO o

shall provide the main obje

S

should address

should address

d.	Transmission paths