EECP Events of 12/23/06

On Dec 23rd at 15:52:00 800 MW of capacity was lost due to a forced unit outage.

At 17:00 total ERCOT load was 30,841 MW, which was approximately 1000 MW above the load forecast. The load was increasing 1600 MW/hr until it reached a peak of 34,150 MW at 18:51:18.

At 17:10 an advisory was issued for adjusted responsive was less than 3,000 MW (Adj. RRS 2,944 MW).

At 17:45 an alert was issued due to adjusted responsive was below 2,500 MW (Adj. RRS 2,478 MW). ERCOT total load was at 33,507 MW.

- RMR units raised due to Alert issued for adjusted responsive reserve.

At 18:15 EECP Step #1 was implemented for adjusted responsive was below 2,300 MW (Adj. RRS 2,232.5) with a total ERCOT load of 33,933 MW for about 20 min. The frequency was at 59.94 Hz.

- SPP notified ERCOT declared EECP Step 1.

At 18:45 ERCOT ordered 8 units online with 1,361 MW of capacity.

At 18:51 adjusted responsive was at 2,325 MW with a total ERCOT load of 34,150 MW.

At 19:45 ERCOT started releasing the generation that was bought online for EECP.

- Released units that came online for emergency after 20:00:00

At 20:40 responsive reserve was at 2,642 MW with ERCOT load of 33,756 MW.

At 20:45 EECP Step 1 was cancelled.

Summary: Forced unit outages combined with higher than expected evening load pick-up resulted in ERCOT declaring EECP. Using a 4% error would have given an Adj. RRS 2,304 MW.