EECP Events of 1/20/2007

On Jan 20 at 08:19:00 ERCOT issued an Advisory for Adjusted Responsive Reserve below 3,000 mw.  Total ERCOT load was 39,588 mw, the adjusted Responsive Reserve was 2,734 mw.  The load was increasing 1280 mw/hr until it peaked at 10:35:46.

At 10:32 the frequency dropped to its lowest point of 59.921 Hz with a total ERCOT load of 41, 591 mw.

At 10:33 an Alert was issued for Adjusted Responsive below 2500 mw.    The total ERCOT Load was 41,608 mw with an adjusted Responsive Reserve of 2,381mw.

    - RMR Units maximized.

    - All maintenance suspended.

    - No Non-Spin available.

At 10:35:46 the load peaks to 41,712 mw with an adjusted responsive reserve of 2,355 mw.

At 11:01 the adjusted Responsive Reserve drops to 2,266 mw and ERCOT declares EECP Step 1.   The total Load was 41,563 mw and the Frequency was 59.979 Hz.

    - 1,011 mw Balancing Energy Available

    - 400 mw Regulation Available

3.   SPP notified of EECP

    - Emergency Power started across the North and East DC Ties.  Total combined import was 738 mw.

    - Ordered on 6 GT’s for a total of 486 mw.

At 11:02 the adjusted Responsive Reserve drops to its lowest point of 2,246 mw.

At 12:00 the adjusted Responsive Reserve increases to 3,059 mw and ERCOT Cancelled EECP Step 1.  The total ERCOT load at the time was 41,057 mw.

- GT’s released to come off line.

- SPP was notified to end Emergency power across the Tie.

At 12:30 the frequency dips to 59.926 with a total ERCOT load of 40,726 mw and an Adjusted Responsive Reserve of 3,179 mw.

At 13:50 the adjusted Responsive reserve was 3,400 mw, the Alert and Advisory ended.

- RMR’s released.

- Maintenance resumed

Summary

At 11:00 units were going offline as scheduled which as a result dropped the Adjusted Responsive Reserve to below 2300 mw.  If using a 4% Adj. RR value, EECP would have been avoided, the Adj. RR number would have been 2339 MW.