## Slide 1: Emergency Interruptible Load Service
Paul Wattles
ROS Subgroup
Feb. 7, 2006

## Slide 2: Abbreviated History
May 2005 TAC/WMS ask Demand Side WG to work on the issue of an emergency load program to address 1-in-10-year LOLE
July 2005 TAC rejects new ancillary service for alternative fuels; cites ‘demand-side services for emergency curtailments’ as alternative
Oct. 2005 DSWG presents emergency load proposal to WMS; WMS defers decision in light of PUC rulemaking
July 2006 Emergency Load Response dropped from proposed rule; deferred to Demand Response project (32853)
Q4 2006 ERCOT presents EILS proposal to PUC Demand Response workshop & ERCOT stakeholders; subgroups develop proposals; Commissioners propose parallel rulemaking
Q1 2007 WMS resolution expresses lack of confidence that EILS is necessary; PRS tables PRRs pending new information; PUC rulemaking initiated

## Slide 3: PUC Rulemaking
Project #33457
Regular rulemaking with expedited timeline (not an emergency rule)
Proposal for publication approved by Commission Feb. 2
Comment period now open
  Comments due March 2
Projected effective date: April 11
Based on PRR 705
Rule will sunset Oct. 1, 2007, provided that:
  Alternative PRR acceptable to PUC and ERCOT is approved
  Solution continuously in place with no interruption of protection offered by EILS
    EILS may be extended if a solution is not implemented by Oct. 1

## Slide 4: ERCOT Emergency Operations
A new tool for the ERCOT toolbox
Event/Action | Trigger
ADVISORY | Physical responsive below 3000 MW
ALERT: Start RMR units, suspend unit testing, deploy RPRS & NSRS | Physical responsive below 2500 MW
Emergency Electric Curtailment Plan | 
Step 1: Dispatch all generation, DC Ties | Physical responsive below 2300 MW
Step 2: Deploy LaaRs, issue public media appeal | Physical responsive below 1750 MW
Step 3: Instruct transmission owners to shed firm load | Frequency below 59.8 hz
New Step: Deploy EILS Resources

## Slide 5: EILS: Operational Issues
500 MW floor
  Will not operate program if <500 MW subscribed
1,000 MW ceiling
Loads deployed thru VDI hotline call to QSEs
Loads deployed as single block after all market-based resources have been deployed
QSEs responsible for:
  Knowing EILS Resources committed at all times
  Issuing dispatch instructions to the loads
Loads have 10 minutes to shed full commitment of MW
Loads must stay at committed level throughout deployment
Loads recalled after LaaRs & have 10 hours to return to service
ERCOT operators may go directly to Step 4 of EECP if frequency is decaying
EILS deployment will allow faster recovery of the system

## Slide 6: Questions?