# ERCOT Operations Report for ROS & OWG

# January 2007

## Frequency Control Disturbance (Less than 59.9 Hz or higher than 60.1Hz)

| Disturbance Data |  |  |  |  |
| --- | --- | --- | --- | --- |
| Time | Frequency (Hz) | Duration (mm:ss) | Details | Notes |
| 01/10/2007 14:22:36 | 59.891 | 00:06 | Unit trip. 550MW lost |  |
| 01/14/2007 07:52:57 | 59.848 | 01:03 | Unit trip. 730MW lost |  |
| 01/17/2007 14:06:05 | 59.893 | 00:02 | Unit trip. 475MW lost |  |
| 01/27/2007 12:01:26 | 60.108 | 00:36 |  |  |
| 01/31/2007 05:59:34 | 59.898 | 00:04 | Unit trip. 520MW lost |  |

## Deployed Responsive (17) (Reported Above)

| ID | Time of deployed | Duration (h:mm:ss) | Max Deployed (MW) |
| --- | --- | --- | --- |
| 1 | 01/06/2007 09:02:26 | 0:08:00 | 332.82 |
| 2 | 01/08/2007 06:07:04 | 0:24:30 | 358.8 |
| 3 | 01/09/2007 06:02:38 | 0:16:36 | 348.41 |
| 4 | 01/09/2007 08:35:30 | 0:04:28 | 322.4 |
| 5 | 01/10/2007 00:00:34 | 0:08:48 | 322.4 |
| 6 | 01/10/2007 14:22:39 | 0:07:21 | 410.81 |
| 7 | 01/12/2007 20:00:46 | 0:03:18 | 343.21 |
| 8 | 01/13/2007 03:05:56 | 0:04:56 | 338.01 |
| 9 | 01/13/2007 04:33:57 | 0:08:59 | 343.21 |
| 10 | 01/14/2007 00:04:22 | 0:24:04 | 317.2 |
| 11 | 01/14/2007 07:52:58 | 0:08:23 | 696.81 |
| 12 | 01/16/2007 20:01:00 | 0:15:44 | 1150 |
| 13 | 01/17/2007 14:06:07 | 0:05:46 | 400.4 |
| 14 | 01/21/2007 05:49:14 | 0:03:52 | 353.6 |
| 15 | 01/24/2007 12:27:30 | 0:10:04 | 332.82 |
| 16 | 01/31/2007 05:59:36 | 0:04:38 | 299.53 |
| 17 | 01/31/2007 10:46:00 | 0:06:44 | 295.37 |

## Day-Ahead RMR and OOMC Capacity Purchases

| Historical RMR & OOMC Totals | Jan-06 | Dec-06 | Jan-07 |
| --- | --- | --- | --- |
| Austin | 0 | 11 | 48 |
| Bryan Area | 1 | 0 | 0 |
| Corpus | 9 | 0 | 0 |
| DFW | 8 | 27 | 51 |
| E RIO | 48 | 5 | 5 |
| Houston | 0 | 1 | 21 |
| Laredo | 40 | 90 | 91 |
| North | 6 | 0 | 10 |
| Northeast | 0 | 0 | 3 |
| San Antonio | 34 | 1 | 3 |
| South | 0 | 0 | 4 |
| W RIO | 24 | 62 | 60 |
| Western | 0 | 0 | 16 |
| Total | 170 | 197 | 312 |

| Data in detail | RMR | OOMC | RPRS | Total |
| --- | --- | --- | --- | --- |
| Austin | 0 | 48 | 35 | 83 |
| Bryan Area | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 6 | 6 |
| DFW | 0 | 51 | 3 | 54 |
| E RIO | 0 | 5 | 34 | 39 |
| Houston | 0 | 21 | 0 | 21 |
| Laredo | 91 | 0 | 0 | 91 |
| North | 0 | 10 | 3 | 13 |
| Northeast | 0 | 3 | 9 | 12 |
| San Antonio | 0 | 3 | 21 | 24 |
| South | 0 | 4 | 26 | 30 |
| W RIO | 0 | 60 | 21 | 81 |
| Western | 0 | 16 | 4 | 20 |
| Total | 91 | 221 | 162 | 474 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

## OOME / Congestion Management Activity:

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days of Occurrences |
| --- | --- | --- |
| Zorn - McCarty Lane 138 kV | Comal - Henne 138 kV | 18 |
| Clear Spring & Marion/Zorn 345 kV | Seguin - Zorn 138 kV | 8 |
| Temple Pecan Creek - Tradinghouse & Lake Creek - Temple Switch 345kV | Lake Creek - Temple Pecan Creek 138 kV | 7 |
| STP - Skyline & Whitepoint 345 kV | Blessing - Lolita 138 kV | 5 |
| Clear Spring & Marion/Zorn 345 kV | Comal - Henne 138 kV | 4 |
| Hill Top - McCarty Lane 138 kV | Comal - Henne 138 kV | 4 |
| Morgan switch - Odessa EHV 345 kV | Big spring Switch - Big Spring West 138 kV | 3 |
| Temple Pecan Creek - Tradinghouse & Lake Creek - Temple Switch 345kV | Evant - Goldthwaite 138 kV | 2 |
| STP - Skyline & Whitepoint 345 kV | Blessing - Lane City 138 kV | 2 |
| STP - Whitepoint 345 kV | Blessing - Lane City 138 kV | 2 |
| STP - Whitepoint 345 kV | Blessing - Lolita 138 kV | 2 |
| Zorn - McCarty Lane 138 kV | McCarty Lane - Henne 138 kV | 2 |
| Fisher Road - Bowman/Oklaunion 345 kV | Grossbeck - Vernon 138 kV | 2 |
| Tradinghouse - Venus 345 kV | Evant - Adamsville 138 kV | 2 |
| North Edinburg - Rio Hondo 345 kV | South McAllen - Las Milpas 138 kV | 2 |
| Austrop Auto T2 345/138 kV | Austrop Auto T1 345/138 kV | 2 |
| Gibbons Creek - Twin Oaks Switch 345 kV | Watson Chapel - Robertson 138 kV | 1 |
| Gibbons Creek - Twin Oaks Switch 345 kV | Watson Chapel - Jewett 138 kV | 1 |
| Gibbons Creek - Greens Prairie East 138 kV | Dansby - Tabor | 1 |
| Asherton - Escondido 138 kV | Asphalt Mines - Uvalde 138 kV | 1 |
| Austrop - Lost Pines 345 kV | Winchester - Smithville 138 kV | 1 |
| Dilley Switch - San Miguel 138 kV | Derby - Pearsall 69 kV | 1 |
| Enterprise - Trinidad & Martin Lake - Striker Creek | Nacogdoches SE Auto | 1 |
| Kingsville - Alice 138 kV | Falfurrias Auto 138/69 kV | 1 |
| Marion - Hill Country/Skyline 345 kV | Hill Country - Skyline 345 kV | 1 |
| Menard - Gillespie 138 kV | Menard Auto T1 | 1 |
| La Palma 345/138 kV Auto | South McAllen - Hidalgo 69 kV | 1 |
| Rio Hondo - LaPalma 138 kV | RaymondVille 2- Raymondville 1 | 1 |
| Temple Switch - Tradinghouse & Temple - Lakecreek 138 kV | Lake Creek - Temple Switch 138 kV | 1 |
| Temple Switch - Bell County 138 kV | Seaton - Poag 69 kV | 1 |
| Trinidad - Stryker Creek/ Mt. Ernterprise 345 kV | Troup - Walnut Grove 138 kV | 1 |
| Pawnee - Calaveras 345 kV | Comfort - Cico 138 kV | 1 |
| Kendall - Hays 345 kV | Comal - Henne 138 kV | 1 |
| Lytton Springs - Zorn & Austrop - Zorn 345 kV | Killeen Ft Hood West - Killeen Clear Creek 138 kV | 1 |
| Haysen - Zorn 138 kV | Kendall - Kerrville Stadium 138 kV | 1 |
| Dessau - Austrop 138 kV | Austrop - Decker 138 kV | 1 |
| Gibbons Creek t2 345/138 kV | Gibbons Creek - Greens Prairie 138 kV | 1 |

## Zonal OC1’s

| CSC | Days |
| --- | --- |
| North - West | 1 |
| South - North | 0 |
| North - Houston | 0 |
| West - North | 0 |
| South - Houston | 0 |

## New RAPs

None.

## New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 01/12/2007 | Shift Supervisor Desk V. 3 Rev. 31 | 312 |
| 01/09/2007 | Frequency Control Desk V. 3 Rev. 50 | 311 |
| 01/04/2007 | Transmission & Security Desk - Zonal CSC Congestion Management | 310 |
| 01/02/2007 | Shift Supervisor - Advanced Notice of Diminishing Responsive Reserve | 309 |
| 01/02/2007 | Day Ahead Desk - Methodology for Determining Non-Spin Procurement | 308 |
| 01/02/2007 | Transmission & Security Desk - Relief of Non Spin Obligation | 307 |

## Blackout/Load Shed incidences

None

## EECP

01/20 Implemented EECP

## Major system voltage problems

## None

## Voltage Instructions

None

## Major Computer Problems, Enhancements & Fixes

RTB intervals – 3

1/1/2007, 24:00 Interval Failed due to restart of market applications.

1/09/2007, 10:45 and 11:00 failed during Site Failover

AGC Control lost - 0 minutes

Database Loads

01/04/2007

01/22/2007

01/31/2007

## Communication

None

## ERCOT peak (Unofficial)

01/16/2007 19:00	51444MW

## Yearly Mid-Term Load Forecast Error Comparison

| Month | MAPE for MTLF run at 16:00 Day Ahead (2004) | MAPE for MTLF run at 16:00 Day Ahead (2005) | MAPE for MTLF run at 16:00 Day Ahead (2006) | MAPE for MTLF run at 16:00 Day Ahead (2007) |
| --- | --- | --- | --- | --- |
| January | 4.76 | 5.02 | 4.79 | 4.55 |
| February | 4.81 | 3.47 | 4.81 | N/A |
| March | 2.89 | 3.41 | 4.95 | N/A |
| April | 3.23 | 3.37 | 5.59 | N/A |
| May | 3.93 | 4.21 | 3.59 | N/A |
| June | 4.85 | 3.91 | 2.65 | N/A |
| July | 5.07 | 5.22 | 2.62 | N/A |
| August | 4.10 | 4.86 | 2.09 | N/A |
| September | 3.66 | 6.24 | 4.03 | N/A |
| October | 3.85 | 4.51 | 3.63 | N/A |
| November | 3.60 | 4.53 | 3.28 | N/A |
| December | 4.18 | 5.95 | 3.44 | N/A |
| Average MAPE for Year | 4.08 | 4.56 | 3.79 | N/A |

ERCOT Load Forecast Forum		January 24, 2007

## OCN, Advisory, Alerts, and Emergency Notices:

### Generation:

| Date | Start | End | Details | Subject |
| --- | --- | --- | --- | --- |
| 1/6/2007 | 9:02 | 9:05 | XXXX tripped at 130 MW, ERCOT load 32000MW | Mkt Notice |
| 1/9/2007 | 6:02 | 6:19 | 348MW of RRS deployed due to big morning schedule change, XXXX of 260MW and XXXX. | Mkt Notice |
| 1/9/2007 | 8:35 | 8:40 | XXXX Units Tripped approximately 477 MW. | Mkt Notice |
| 1/10/2007 | 14:22 | 14:30 | XXXX trip of 550MW. System load at time of trip was 30959. | Mkt Notice |
| 1/12/2007 | 20:01 |  | Deployed 343mw RRS when a unit ran back. | Responsive Reserve |
| 1/13/2007 | 3:06 |  | Deployed 338mw RRS due to unit run back. | Responsive Reserve |
| 1/13/2007 | 4:35 |  | Deployed 343mw RRS due to unit run back. | Responsive Reserve |
| 1/17/2007 | 14:06 | 14:09 | XXXX tripped with 475 MW, ERCOT load 46,394 MW | Mkt Notice |
| 1/21/2007 | 5:49 | 5:53 | XXXX tripped with 322MW's. ERCOT load 33381 MW. | Mkt Notice |
| 1/24/2007 | 12:27 | 12:32 | XXXX tripped at 325 MW, ERCOT load 39300 MW | Mkt Notice |
| 1/31/2007 | 10:46 | 10:52 | XXXX tripped 400 MW at Ercot load 40,492 MW. | Mkt Notice |

### Insufficient Capacity:

| Date | Start | End | Details | Subject |
| --- | --- | --- | --- | --- |
| 1/1/2007 | 0:00 | 5:45 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW | Advisory |
| 1/2/2007 | 9:03 | 10:50 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW | Advisory |
| 1/3/2007 | 18:52 | 23:00 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW | Advisory |
| 1/5/2007 | 18:19 | 19:59 | Advisory issued due to Adjusted Responsive Reserve below 3000MW's. | Advisory |
| 1/6/2007 | 10:00 | 14:15 | Advisory issued due to Adjusted Responsive Reserve below 3000MW's. | Advisory |
| 1/6/2007 | 17:43 | 21:00 | Advisory issued due to Adjusted Responsive Reserve below 3000MW's. | Advisory |
| 1/7/2007 | 18:40 | 24:00 | Advisory issued due to Adjusted Responsive Reserve below 3000MW's. | Advisory |
| 1/8/2007 | 0:15 | 10:00 | Advisory issued due to Adjusted Responsive Reserve below 3000MW's. | Advisory |
| 1/9/2007 | 18:20 | 22:30 | Advisory issued due to Adjusted Responsive Reserve below 3000MW's. | Advisory |
| 1/11/2007 | 7:20 | 12:15 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/12/2007 | 12:12 |  | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/13/2007 | 0:00 | 2:28 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/13/2007 | 8:24 | 15:07 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/13/2007 | 9:16 | 15:07 | Alert for Adjusted Responsive Reserve below 2500 MW. | Alert |
| 1/14/2007 | 0:04 |  | Deployed 331MW's of Responsive Reserve due to schedule changes and QSE telemetry issues. | Responsive Reserve |
| 1/15/2007 | 11:18 | 12:28 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/15/2007 | 17:30 | 22:14 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/15/2007 | 17:48 | 22:14 | Alert for Adjusted Responsive Reserve below 2500 MW. | Alert |
| 1/16/2007 | 6:44 | 15:26 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/16/2007 | 18:43 | 19:43 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/17/2007 | 9:35 | 20:51 | Advisory for Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/19/2007 | 18:08 | 20:00 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/20/2007 | 8:19 | 13:50 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/20/2007 | 10:33 | 13:50 | Alert issued due to Adjusted Responsive Reserve below 2500 MW. | Alert |
| 1/20/2007 | 11:01 | 12:00 | EECP Step 1 issued due to Adjusted Responsive Reserve below 2300 MW. | EECP Step 1 |
| 1/23/2007 | 18:02 | 21:15 | Advisory issued due to Adjusted Responsive Reserve below 3000mw. | Advisory |
| 1/28/2007 | 8:10 | 10:20 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/28/2007 | 19:25 | 21:00 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/29/2007 | 8:15 |  | Advisory issued due to Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/30/2007 | 18:05 | 22:00 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW. | Advisory |
| 1/30/2007 | 18:55 | 19:15 | Alert issued due to Adjusted Responsive Reserve below 2500 MW. | Alert |
| 1/31/2007 | 6:20 | 10:40 | Advisory issued due to Adjusted Responsive Reserve below 3000 MW. | Advisory |

### Transmission:

| Date | Start | End | Details | Subject |
| --- | --- | --- | --- | --- |
| 1/3/2007 | 10:00 | 12:00 | Transmission Alert issued for loss of North Edinburg - Lon Hill 345 kV indicates voltage collapse in Valley. | Alert |
| 1/6/2007 | 17:28 | 24:00 | XXXX - limit was revised from 2440 to 3300 due to restoration of a forced outage. | Mkt Notice |
| 1/9/2007 | 4:00 | 11:15 | Transmission Emergency for the Del Rio area for the loss of Asherton - West Conoco 138Kv. | Emergency |
| 1/14/2007 | 21:52 |  | Alert issued for loss of 345kv line Comanche Sw to Comanche Peak overloads Ballinger to South Abiline 69kv line. | Alert |
| 1/15/2007 | 0:00 | 12:20 | Alert issued for loss of 345kv line Comanche Sw to Comanche Peak overloads Ballinger to South Abiline 69kv line. | Alert |
| 1/15/2007 | 12:05 | 13:07 | Alert issued for loss of Gibbons Creek to Greens Praire 138kV causes voltage collapse in the Bryan/Collage Station area. | Alert |
| 1/15/2007 | 16:30 |  | Alert issued due to planned outage Zorn to McCarty Lane 138kV due to multiple post contingent overloads near the Comal area 138 kV past first contingency limits. | Alert |
| 1/15/2007 | 19:00 |  | Alert issued for loss of McQueeny Auto causes voltage collaspe at New Berlin Sub.. | Alert |
| 1/15/2007 | 19:00 | 24:00 | Alert issued for loss of PH Robinson to Southshore 138kv line overloads 138kv line Freeway Park to Alvin. | Alert |
| 1/16/2007 | 0:00 | 23:45 | Alert issued for loss of McQueeny Auto causes voltage collapse at New Berlin Sub.. | Alert |
| 1/16/2007 | 0:00 |  | Alert issued for the loss of Zorn to McCarty Lane 138kV overloads Henne - Comal kV past first contingency limits. | Alert |
| 1/16/2007 | 6:31 |  | Alert issued for loss of PH Robinson to Southshore 138kv line overloads 138kv line Freeway Park to Alvin. | Alert |
| 1/16/2007 | 8:56 |  | Alert issued for loss of South McAllen 138/69kV Auto #1 overloads La Palma - Rangerville 69kV past first contingency limits. | Alert |
| 1/16/2007 | 9:10 | 23:45 | Alert issued for loss of South Texas Project - Skyline & White Point 345kVoverloads Blessing - Lolita 138kV past first contingency limits. | Alert |
| 1/16/2007 | 11:56 |  | Emergency Notice issued due to identified single contingencies that present unsolvable post contingency overloads of transmission elements in Central & South Texas. | Emergency |
| 1/17/2007 | 0:00 |  | Alert issued for the loss of Zorn to McCarty Lane 138kV overloads Henne - Comal kV past first contingency limits. | Alert |
| 1/17/2007 | 0:00 |  | Alert issued for loss of PH Robinson to Southshore 138kv line overloads 138kv line Freeway Park to Alvin. | Alert |
| 1/17/2007 | 0:00 |  | Alert issued for loss of South McAllen 138/69kV Auto #1 overloads La Palma - Rangerville 69kV past first contingency limits. | Alert |
| 1/17/2007 | 0:00 |  | Emergency Notice issued due to identified single contingencies that present unsolvable post contingency overloads of transmission elements in Central & South Texas. | Emergency |
| 1/17/2007 | 4:24 | 6:30 | Alert issued for loss of Rio Hondo - LaPalma 138kV overloads Raymond2 - Raymond1 69kV past first contingency limits. | Alert |
| 1/18/2007 | 0:00 |  | Alert issued for the loss of Zorn to McCarty Lane 138kV overloads Henne - Comal kV past first contingency limits. | Alert |
| 1/18/2007 | 0:00 | 11:50 | Alert issued for loss of PH Robinson to Southshore 138kv line overloads 138kv line Freeway Park to Alvin. | Alert |
| 1/18/2007 | 0:00 |  | Alert issued for loss of South McAllen 138/69kV Auto #1 overloads La Palma - Rangerville 69kV past first contingency limits. | Alert |
| 1/18/2007 | 0:00 |  | Emergency Notice issued due to identified single contingencies that present unsolvable post contingency overloads of transmission elements in Central & South Texas. | Emergency |
| 1/18/2007 | 2:25 |  | Alert issued for the loss of Harlingen Switch 138/69kV autotransformer overloads LaPalma - San Benito 69kV. | Alert |
| 1/18/2007 | 18:30 |  | Alert issued for loss of PH Robinson to Southshore 138kv line overloads 138kv line Freeway Park to Alvin. | Alert |
| 1/19/2007 | 0:00 | 0:30 | Alert issued for the loss of Zorn to McCarty Lane 138kV overloads Henne - Comal kV past first contingency limits. | Alert |
| 1/19/2007 | 0:00 | 0:30 | Alert issued for loss of South McAllen 138/69kV Auto #1 overloads La Palma - Rangerville 69kV past first contingency limits. | Alert |
| 1/19/2007 | 0:00 | 0:30 | Emergency Notice issued due to identified single contingencies that present unsolvable post contingency overloads of transmission elements in Central & South Texas. | Emergency |
| 1/19/2007 | 0:00 | 0:30 | Alert issued for the loss of Harlingen Switch 138/69kV autotransformer overloads LaPalma - San Benito 69kV. | Alert |
| 1/19/2007 | 0:00 | 0:30 | Alert issued for loss of PH Robinson to Southshore 138kv line overloads 138kv line Freeway Park to Alvin. | Alert |
| 1/19/2007 | 9:30 | 23:50 | Alert issued for loss of Harlingen Auto overloads LaPalma to San Benito. | Alert |
| 1/20/2007 | 8:23 | 18:15 | Alert issued for loss of Harlingen Auto overloads LaPalma to San Benito. | Alert |
| 1/23/2007 | 12:15 |  | Transmission Alert- Halinger Switch 138/138 KV tranformer would be above its rating with the loss of La Palma-San Benito 69 KV line with no market solution | Alert |
| 1/24/2007 | 0:15 |  | Transmission Alert- Halinger Switch 138/138 KV tranformer would be above its rating with the loss of La Palma-San Benito 69 KV line with no market solution | Alert |
| 1/25/2007 | 0:15 | 23:45 | Transmission Alert- Halinger Switch 138/138 KV transformer would be above its rating with the loss of La Palma-San Benito 69 KV line with no market solution | Alert |
| 1/31/2007 | 0:30 | 11:10 | Transmission Emergency issued due to loss of Asherton - West Conoco 138 kv indicates voltage collapse in Eagle Pass Area. | Emergency |

### Weather:

| Date | Start | End | Details | Subject |
| --- | --- | --- | --- | --- |
| 1/12/2007 | 7:30 | 24:00 | Advisory issued for arctic winter weather | Advisory |
| 1/13/2007 | 0:15 | 7:30 | Advisory issued for arctic winter weather | Advisory |
| 1/13/2007 | 7:30 |  | Alert issued for arctic winter weather | Alert |
| 1/14/2007 | 0:15 |  | Alert issued for arctic winter weather | Alert |
| 1/15/2007 | 0:15 |  | Alert issued for arctic winter weather | Alert |
| 1/15/2007 | 19:00 |  | ERCOT unofficial new all time winter peak of 50722MW's. | Mkt Notice |
| 1/16/2007 | 0:00 |  | Alert issued for arctic winter weather | Alert |
| 1/16/2007 | 19:00 |  | ERCOT unofficial new all time winter peak of 51444MW's. | Mkt Notice |
| 1/17/2007 | 0:00 |  | Alert issued for arctic winter weather | Alert |
| 1/18/2007 | 0:00 |  | Alert issued for arctic winter weather | Alert |
| 1/19/2007 | 0:00 | 15:15 | Alert issued for arctic winter weather | Alert |

### Miscellaneous:

| Date | Start | End | Details | Subject |
| --- | --- | --- | --- | --- |
| 1/4/2007 | 9:20 | 10:52 | ERCOT data base load completed as planned. | Misc |
| 1/9/2007 | 10:05 | 10:40 | ERCOT performed a site failover of its Energy & Market Management Systems from Taylor to Austin. | Misc |
| 1/9/2007 | 10:08 | 10:30 | Held IE 1030 and 1045 due to site failover. | Misc |
| 1/16/2007 | 7:20 | 12:15 | Operation Condition Notice (OCN) issued due to insufficient UBES bids for intervals 1100 thru 1400. | Mkt Notice |