## Slide 1: RRS Deployment 01/16/2007 20:01:00
ROS Meeting
February 16th, 2007
Carlos González-Pérez
Manager, Operations Support

## Slide 2: Conditions Before RRS Deployment
Frequency: 59.978 Hz
EMS System: Running from Austin Control Center

## Slide 3: EMS Frequency Sources
Direct sources of ERCOT EMS frequency: True Time Devices
  Satellite connection to track Time and compute Time Error
  Input frequency from an electric plug connected to the grid
  4 Devices (2 in TCC and 2 in ACC)
Frequency Source Normal Operation
  1 True Time in primary site, 1 True Time in the back-up site
  Indirect sources of frequency reported by QSEs via DNP 3.0
  Operator can select the source
What happened on 01/16/2007
  Outage in the feeder supplying the primary True Time device

## Slide 4: Cause of the Deployment
Outage at the feeder connected to the primary TrueTime device in the ACC
The outage translates into a 58.13 Hz
EMS frequency below RRS triggering point (59.91 HZ)
Full Deployment of RRS (1150 MW)
Feed power restored (2 seconds)
TrueTime frequency: reading at 59.978 HZ (above recall limit 59.97 Hz)
Total Recall of RRS

## Slide 5: System Recovery

## Slide 6: Conclusions and Next Steps
The system responded appropriately to the incorrect frequency reading
Second occurrence in 3 years
PR-50021 will address consideration of multiple sources of frequency to avoid this occurrence in the future.