## Slide 1: Controllable Loads

## Slide 2: Controllable Load Resource
What is a Controllable Load Resource?
Load Resource capable of providing Regulation Service by controllably reducing or increasing consumption under dispatch control (similar to AGC) and that immediately responds proportionally to frequency changes (similar to generator governor action).

## Slide 3: Controllable Load Resource
In 2002 PRR307, Load providing Regulation services (Controllable Resources), was approved
In June 2007 ERCOT was asked to provide a cost and impact analysis for implementing PRR307
ERCOT estimated the project would cost between $500,000 and $1,000,000 and take up to a year to implement
ERCOT proposed an alternate approach which could be implemented with no system changes, but with limitations
Background:

## Slide 4: Controllable Load Resource
Pilot Limitations:
Meet all requirements for participation as a LaaR
  IDR meter
  Real Time telemetry at the controllable load installed and tested
  Successfully complete qualification test
Able to respond proportionately to frequency changes (similar to generator governor action
Capable of reducing or increasing consumption in response to dispatch instruction (similar to AGC)
Site has to “look”, “act”, and “smell” like a generation resource (eg; power flow at point of the settlement meter shall be a net generation point while providing services as a controllable load)
Need to bid in as a “GEN” type and not “CLD” Resource (for RRS only)
Resource agrees to waive its right to receive any resource-specific premium payments that would result from a unit specific instruction (OOME)

## Slide 5: Controllable Load Resource
Status Summary
Initiated pilot project in October 2006
To limit potential disruption to ERCOT frequency control only one Load Resource was allowed to participate up to 10 MWs
Pilot successfully concluded in early January 2007
January PUCT Open Meeting
  PUCT directed ERCOT to open service up to all participants
ERCOT estimates up to 150 MWs of load could participate as Controllable Load

## Slide 6: Controllable Load Resource
Controllable Load can provide:
Regulation Up, Regulation Down, or both
Responsive Reserve Service
Note:
Any capacity from a Controllable Load providing RRS would not be included in the ERCOT established limit for LaaRs providing RRS.

## Slide 7: Controllable Load Resource
Qualification Test for a Controllable Load
AS Qualification Criteria and Portfolio Test Methods as described in the Protocols is a QSE portfolio level test
The Stakeholders and ERCOT both wanted to test each Controllable Loads ability to provide Regulation and Responsive Reserve Service
Since ERCOT cannot create a resource specific Regulation and Responsive Reserve Service instruction the proposed qualification test procedure is as follows:
Same qualification criteria currently used to qualify QSE portfolio
Require QSE to set all non-CLR on manual control
The control signal sent to the QSE will test the controllable loads ability to achieve the entire amount of Regulation requested for qualification
Only the CLR is expected to control to the signal