GENERATION INTERCONNECTION OR CHANGE

REQUEST PROCEDURE

February 2007

Proposed Implementation March 1, 2007

ERCOT

System Planning, Transmission Services

2705 West Lake Drive

Taylor, Texas 76574-2136

Main Office Phone (512) 248-3000

1.0  INTRODUCTION

1.1  Purpose

The primary purpose of the ERCOT Generation Interconnection or Change Request Procedure is to provide market participants a detailed understanding of the requirements and procedures used to facilitate new or modified generation interconnections with the transmission system of the Electric Reliability Council of Texas (ERCOT).  Through its review of all interconnection or change requests, ERCOT staff expects to:

- Identify any potential electric system security concerns with interconnecting new or modified generation,

- Increase the quality of communications between the generating entity (GE), power generation company (PGC), transmission service providers (TSP), and ERCOT,

- Provide for the best available information on future capacity additions for use in identifying, forecasting, and analyzing both short- and long-range ERCOT capabilities, demands, and reserves, and

- Provide for accurate and appropriate data to aid ERCOT staff and stakeholders in identifying and developing potential transmission improvement projects to alleviate expected transmission constraints in order to maintain the reliability of the ERCOT system.

The requirements and procedures in this document conform to all rules, standards, protocols, and guides of the Public Utility Commission of Texas (PUCT or Commission), the North American Electric Reliability Council (NERC), and ERCOT.

1.2  Applicability

The requirements in this document are applicable, in general, to the following:

- New generating units, plants, or wind farms 10 MW or greater planning to interconnect to transmission in the ERCOT system.

- Existing generating units interconnected in the ERCOT system that are seeking to upgrade their rated capacity 10 MW or greater within a single year, re-power, or change their physical point of interconnection.

Interconnection requirements for on-site distributed generation  are not subject to these procedures but are addressed in PUCT Substantive Rules §25.211 (Interconnection of On-Site Distributed Generation) and §25.212 (Technical Requirements for Interconnection and Parallel Operation of On-Site Distributed Generation).

1.3  Confidentiality

During the security screening study phase of the interconnection process and in accordance with the ERCOT Protocols, data, documents, or other information required by ERCOT from a GE or PGC related to a request for generation interconnection are considered “protected information” to the extent that such information is not otherwise publicly available.  As a result, ERCOT staff shall not publicly release any of the “protected” data, documents, or other information until a request for a full interconnection study (FIS) is received.  Security screening study information will only be publicly released in aggregation amounts.  When a request for a full interconnection study is received, the following information will become public and used in reports:

- Proposed MW Capacity

- Projected month and year of commercial operation

- Fuel and Technology Type

- County location

As the full interconnection study proceeds and executes an interconnection agreement or completes a financial arrangement for transmission construction, data, documents or other information will become public.

1.3.2  Public Projects

When a GE or PGC executes an interconnection agreement or completes a financial arrangement for transmission construction with a TSP, ERCOT and the TSP will reclassify the project as a confirmed or “public project” and the respective studies will be publicly posted when finalized.  The public projects will be added to all ERCOT databases after the steady-state, dynamic, system protection, and facilities portions of the FIS are completed and interconnection requirements are identified.

1.4   Transmission Construction Issues

PUCT Substantive Rule §25.191 (Transmission Service Requirements) requires a TSP to build sufficient transmission or distribution facilities on a nondiscriminatory basis to support the reliable interconnection of generation to its electrical network.  Depending upon the specific findings of the full interconnection study (discussed in more detail in Section 2.3), the TSP may be required, under Texas law, to seek a Certificate of Convenience and Necessity (CCN) from the PUCT before construction can begin.

1.4.1  Certificate of Convenience and Necessity

In order for the PUCT to grant a CCN, Texas law and PUCT rules require the Commission to make a determination that the proposed transmission enhancements are in the public interest.

In many instances, additional transmission improvements (other than those transmission improvements identified in the interconnection agreement) may be required to enable the GE or PGC to reach its desired markets, for ERCOT to minimize any transmission constraints in facilitating the competitive market, and to lower congestion costs.  When this occurs, ERCOT staff will work with the respective Regional Planning Groups in accordance with the ERCOT Power System Planning Charter and Processes.   Should the Regional Planning Process determine that additional transmission will be required to fully integrate the GE or PGC’s generation project, the appropriate TSP(s) responsible for completing the specified improvement project(s) may also have to file a CCN(s) for their respective portion(s) of the work.

While ERCOT’s evaluation of need in the regional planning process is important and given significant weight by the Commission, the PUCT, via the CCN process, has, under Texas law, the final authority to ultimately decide whether a transmission line is in the public interest and should be built.

1.4.2  CCN Approval Timelines

Typically, TSPs require approximately 12 months to prepare a CCN application for filing with the PUCT.  This extended time is generally due to the TSP identifying and evaluating the environmental impacts of potential alternative transmission line routes, as well as the requirement to provide adequate public notice and to hold public meetings in the project area to listen to and address landowner concerns.

After the CCN application is filed by the TSP, the PUCT staff must determine if the application is materially complete.  Any inadequacies or deficiencies in the application must be remedied by the TSP before the Commission will take any action on the application.  Once the PUCT staff has provided notice that the application is materially complete, current rules allow the Commission up to 12 months for hearing and deciding the outcome of the CCN request.  Most CCN applications involving new transmission right of way may become contested cases generally requiring the TSP and any intervening parties the right to discovery, preparing and filing direct and rebuttal testimony, and participating in a hearing on the merits before a State Office of Administrative Hearing (SOAH) administrative law judge (ALJ).  In most contested cases, the ALJ has been delegated the responsibility to determine for the Commission if the project is in the public interest.

Following the hearing on the merits and the issuance of a Proposal for Decision (PFD) by the ALJ, the Commission will either grant or deny the CCN.  Assuming a CCN has been granted, recent experience in ERCOT by TSPs has shown that the acquisition of new or additional transmission right of way and actual construction can take an additional 10 to 18 months.

Therefore, if a GE or PGC desires full transfer capability when its generation is first available for commercial operation on the ERCOT system, ERCOT recommends that a GE or PGC consider making a firm commitment (signed interconnection agreement with the TSP) for the project at least four years prior to the desired commercial in-service date of the generator’s project.  This early commitment is necessary due to the timeline required by the TSP for obtaining all regulatory approvals and rights of way, and for the actual construction of the transmission line project.  Moreover, the GE or PGC should recognize that some projects may require a commitment as long as eight years in advance of desired in-service date depending on the generation project’s impact on the ERCOT transmission system.

1.5  Communications Between ERCOT and GE or PGC

ERCOT’s primary contact for all questions and information related to generation interconnection request applications, fees, and required generation data is ?.

Questions concerning this generation interconnection procedure should be directed to ?.

The GE or PGC shall maintain communications with ERCOT staff at all stages of the generation interconnection process.  Such communication will include any changes in status, capacity, in-service date, signing of interconnection agreement, etc.  All changes of ownership must be communicated to ERCOT and the TSP when the ownership transfer occurs.  At the completion of all studies and the signing of an interconnection agreement, the TSP and GE/PGC will transmit the documents to ERCOT.  The GE/PGC should also provide ERCOT with the status of their air permits and when they receive a permit for their project.

2.0  INTERCONNECTION PROCESS AND PROCEDURES

The ERCOT interconnection process is in accordance with PUCT Substantive Rule §25.198 (Initiating Transmission Service) which delegates to ERCOT the responsibility for implementing the transmission interconnection process.

2.1  Interconnection Request Application

Any generating entity (GE) or power generation company (PGC) seeking an interconnection to the ERCOT transmission system (as applicable in Section 1.2) must submit a generation interconnection request application, required generation information (as detailed in Section 3.1), and the appropriate fee (as detailed in Section 3.2) to ERCOT.

The GE or PGC shall include in the generation interconnection request application all information necessary to allow for timely development, design, and implementation of any electric system improvements or enhancements required by ERCOT and the TSP to reliably meet the interconnection requirements of the proposed generation.  This information shall be of sufficient detail for use in establishing transfer capabilities, operating limits (including stability), and planning margins to provide both reliability and operating efficiency as well as facilitating coordinated planning for future transmission system additions.

Should the generation interconnection request application fail to include all generation interconnection information or applicable fees, ERCOT staff will notify the GE or PGC within 7 days through informal communications in an attempt to remedy the application’s deficiencies.  Once the application has been deemed materially complete, ERCOT staff will date-stamp the application, add the interconnection request to the ERCOT interconnection list, and notify the GE or PGC of receipt of the completed application within 10 days.  The GE or PGC should note that the date stamp is not a reservation of transmission capacity, either planned or unplanned.

After receiving the completed generation entity information sheet, appropriate security screening study fee, and required generation plant data, ERCOT staff will then initiate a steady-state security screening study.

2.1.1  Submitting Request To ERCOT

All generation interconnection request applications, fees, and supporting data must be received in writing by ERCOT.  Facsimile (FAX), Internet email, or other electronic requests for interconnection will not be accepted.  All interconnection correspondence should be sent to the following address:

GENERATION INTERCONNECTION REQUEST

ATTN: LINDA SHIREY (TCC1 1N059)

ERCOT, INC.

2705 WEST LAKE DRIVE

TAYLOR, TEXAS 76574-2136

In order to clearly identify the application and ensure timely processing of the request and due to the large volume of mail received at ERCOT each day, it is important that GENERATION INTERCONNECTION REQUEST is the first line of the address.

2.1.2  Unique Project Identification

Since project names change frequently and in order to facilitate reliable communications between ERCOT, GEs, PGCs, and TSPs, ERCOT staff will assign a unique name to all generation interconnection request applications according to the following convention:

yrINRxxxx

where:  yr  is the calendar year the generation is anticipated to be online (08, 09, 10)

INR indicates interconnection request

xxxx is a sequence number beginning with 0001 (reset for each year)

It is vital that all correspondence relating to a specific generation interconnection request application, security screening study, or full interconnection study reference this unique project number.

2.1.3  Request Application Fee

In order to consider the interconnection or change application, the security screening study fee (as discussed in Section 3.2.1) must be remitted to ERCOT along with the generation interconnection request application.   The check should be made payable to Electric Reliability Council of Texas, Inc.  The security screening study fee and stability modeling fee are non-refundable.

2.2  Security Screening Study

For each proposed generation interconnection or change project, ERCOT staff will conduct a steady-state security screening study (including power flow and transfer studies) based on the expected in-service year to determine the feasibility of interconnection at the site proposed by the GE or PGC.  The security screening study is a quick review of the project and generally includes a number of initial assumptions from both ERCOT and the GE or PGC.  The “ballpark” results of this study will assist ERCOT in determining the level at which the generator can expect to operate simultaneously with other known generation in the area before significant transmission additions or enhancements may be required.  During the course of this study, ERCOT staff may consult with the affected TSP, if needed, to ensure the most efficient means of assuring the feasibility of transmission service is identified and examined.

Upon completion of the security screening study, ERCOT staff will present the GE or PGC a preliminary estimate of future transmission additions or enhancements ERCOT estimates will be required to effect the full transfer of the proposed new or modified generation.  ERCOT will also inform the GE or PGC about any additional transmission system improvements estimated to be required for the continued security and reliability of the ERCOT system.

Following the presentation of the security screening study results, the GE or PGC must determine whether it wants to continue the interconnection process by formally requesting a full interconnection study or to withdraw its application.  Should the GE or PGC decide to go forward at the named site, the GE or PGC will notify ERCOT in writing within 180 days of its desire to pursue a full interconnection study.  Upon receiving this notification, ERCOT staff will then notify the TSPs and will begin initiation and coordination of the full interconnection study.

Unless ERCOT receives notice from the GE or PGC of its decision to go forward with the proposed project, ERCOT will not initiate a full interconnection study.  Such notice must be received in writing by ERCOT within 180 days following completion of the security screening study.

However, should the GE or PGC decline to notify ERCOT of their intent to initiate a full interconnection study within the 180 days, ERCOT will consider the interconnection request cancelled and no longer valid.  Subsequently, should the GE or PGC wish to proceed after the initial 180-day period,  ERCOT will consider the original security screening study invalid and the process must begin again starting with a new request for a security screening study and payment of the appropriate fee.  The GE or PGC will also be required to provide to ERCOT any updates or changes in the project’s generation plant data.

2.3  Full Interconnection Study

A full interconnection study (FIS) may be requested at the same time as a security screening study.  Both fees (security screening study and stability modeling fee) for the security screening study and the full interconnection study will apply.  Requesting both studies at the same time may shorten the overall time to complete the generation interconnection process.

After receiving notice and fee(s) from the GE or PGC to proceed with a full interconnection study, ERCOT will schedule a preliminary interconnection study meeting consisting of ERCOT staff, the GE or PGC, and all TSPs.   At this meeting, ERCOT will present the proposed interconnection or change request and the results of the security screening study and will then lead a general discussion of the preliminary study scope of work, including which study elements may be required to complete the FIS.

2.3.1 Confidentiality

Once a full interconnection study is requested by the GE or PGC, the following information will become public:

1.	Proposed MW Capacity

2.	Projected month and year of commercial operation

3.	Fuel and Technology Type

4.	County location

As the full interconnection study proceeds and executes an interconnection agreement or completes a financial arrangement for transmission construction, data, documents or other information will become public.  Once classified as a public project, ERCOT will post the project description, copies of the generation interconnection studies, and related transmission improvement projects on the ERCOT website.  The full interconnect scope agreement will remain as protected information and will not be released to parties outside ERCOT and the TSP.  Every member of the FIST may review and provide open comment on the scope agreement.  Studies part of the FIS will be public and posted when they are completed (finalized by the study group and accepted).

2.3.2  Proof of Site Control

Before ERCOT will proceed with the initiation of a full interconnection study, the GE or PGC must submit to ERCOT the appropriate fee (as discussed in detail in Section 3.2.2) and proof of site control.

To establish proof of site control, the GE or PGC must demonstrate through an affiliated company, through a trustee, or directly in its name that:

- The GE or PGC is the owner in fee simple of the real property to be utilized by the facilities for which any new generation interconnection is sought, or

- The GE or PGC holds a valid written leasehold interest in the real property to be utilized by the facilities for which new generation interconnection is sought, or

- The GE or PGC holds a valid written option to purchase or obtain a leasehold interest in the real property to be utilized by the facilities for which new generation interconnection is sought, or

- The GE or PGC holds a duly executed written contract to purchase or obtain a leasehold interest in the real property to be utilized by the facilities for which new generation interconnection is sought.

The GE or PGC must maintain site control throughout the duration of the FIS and until execution of an interconnection agreement.  Otherwise, ERCOT will consider the request for interconnection withdrawn as of the date of the loss of site control unless the applicant can show within 30 days that it has re-established site control or has established control of a new site that would not result in any material modification of any interconnection study requested under the current application.

2.3.3  Full Interconnection Study Team

All TSPs shall be members of the full interconnection study team (FIST).  The primary interconnecting TSP will serve as facilitator of the study team.  ERCOT utilizes this approach because the TSPs are most aware of the specific area in which the project is proposed to be located and the actual nature of the transmission system serving it.  In addition, the assistance of more than one TSP may be required in areas where transmission facilities are provided by multiple TSPs.  This knowledge is extremely beneficial in determining the impact of any proposed interconnection request.  ERCOT staff will maintain the lead role in all interconnection studies, will provide input and participate in the analysis.  ERCOT staff may perform additional independent analyses such as steady-state, transient stability, system protection and facilities studies.

2.3.4  Interconnection Study Scope Agreement

The GE or PGC and the TSP(s) comprising the full interconnection study team must reach agreement on the scope of the full interconnection study within 60 days following the preliminary interconnection study meeting.

The full interconnection study scope agreement shall include all assumptions, timetables, study cost estimates and payment schedules, and the determination of all requirements for interconnection.  The GE or PGC and the TSP(s) have flexibility in reaching agreement on the scope of the FIS.  The GE or PGC and the FIST shall consider the ERCOT security screening study and other preliminary studies and documents provided by the GE or PGC when developing the study scope.  These studies and other documents may reduce the work or the time necessary for the full series of interconnection studies.  The FIS can be divided into several distinct study phases such that notice to proceed from the GE or PGC is required before starting each phase.  This approach may limit the GE’s costs if the project is determined early in this process to be not viable at the selected location.

Should the GE or PGC not agree to the interconnection study scope within the 60-day period, ERCOT will consider the GE’s or PGC’s request for interconnection or change to be cancelled and no longer valid.  Later, should the GE or PGC wish to proceed after such cancellation, the GE or PGC must begin the process again starting with a new security screening study and payment of the appropriate fee(s).

2.3.5  Typical Interconnection Study Elements

The full interconnection study is comprised of a series of distinct study elements.  As previously mentioned, some of the elements may or may not be necessary for the study team to undertake and complete depending upon the provisions of the interconnection study scope agreement.  The primary purpose of the FIS is to determine the most effective and efficient manner in which to satisfy the desire of the GE’s or PGC’s interconnection request while continuing to maintain the reliability of the ERCOT system.

Each generation resource that requires a separate physical transmission interconnection will be treated as an individual study to be analyzed separately from all other such requests unless otherwise agreed to by the GE or PGC in the interconnection study scope agreement.

The FIS process includes developing and analyzing various computer model simulations of the existing and proposed ERCOT generation/transmission system.  The results from these model simulations will be utilized by the FIST to determine the impact of the proposed interconnection.

The study team will also examine normal transmission operations as well as potentially adverse, or contingency, conditions in order to identify and analyze the effectiveness of various interconnection design alternatives in alleviating or mitigating any undesirable performance of the interconnection under a variety of operating conditions.  Due to the inherent uncertainty in model information (load forecasts, operating conditions, available resources, etc.), as well as the effect of other potential interconnections in the general study, the study team must perform these simulation studies in an iterative fashion for each interconnection alternative (i.e., grid configuration, equipment design/layout, facility change) under consideration.  The FIST must generally repeat these simulations numerous times to systematically analyze each alternative developed.

In comparing alternatives, the study team will consider such information as interconnection cost and construction schedule, impact to short- and long-range reliability, operational flexibility, and compatibility with future transmission plans for each alternative.  The FIST including ERCOT staff will propose the most effective interconnection alternative to the GE or PGC.

All studies undertaken will be performed in compliance with all applicable PUCT Substantive Rules, ERCOT Protocols and Operating Guides, NERC Reliability Standards, good utility practice, and the guidelines below unless otherwise directed by ERCOT staff.

Steady-State and Transfer (Load Flow, Power Flow, etc.) Analysis.   The steady-state interconnection study base case shall be created from the most recently approved ERCOT Steady State Working Group (SSWG) base case.  ERCOT staff may, at their discretion, remove any future (currently non-existing) transmission facility from the steady-state interconnection study base case that may significantly affect the interconnection study results and is not already determined by ERCOT to be necessary for the reliability of the ERCOT system.  In addition, ERCOT staff may direct that generation resources proposed in other prior generation interconnection requests be included in the steady-state interconnection study base case if deemed appropriate.

Using the steady-state interconnection study base case, the FIST shall perform contingency analyses as required in the ERCOT Planning Criteria (which includes all applicable NERC Reliability Standards) and identify any additional transmission facilities which may be necessary to ensure that expected system performance conforms to these standards.  All facilities necessary to accommodate the proposed generation will be identified and studied with the exception of any transmission facility additions that are determined to be unfeasible due to time constraints or for other reasons.  Any other facility that cannot be constructed or otherwise completed in time to accommodate the initial commercial operations date of the generation will be identified and communicated to the GE or PGC along with any likely limitations of generation output that may result.

Loss-of-generation analyses shall assume that the lost generation will be replaced from all remaining ERCOT units in proportion to their nominal capacity (i.e., inertial response) and respecting generation limits.

Each member of the FIST is responsible for completing an analysis of any contingency events or outages anticipated to result in a violation of the ERCOT Planning Criteria, regardless of which TSP owns the facilities involved.  The results of each member’s analysis will be shared within the FIST, and those TSPs that have facilities involved in planning criteria violations will be responsible for attempting to verify the validity of the anticipated violations.

System Protection (Short-Circuit) Analysis.  The full interconnection study scope agreement will specify at what locations available short-circuit fault duties will be identified, calculated, and documented.  ERCOT staff required associated transmission system improvements will result in any transmission facility(ies) violating the TSP’s short-circuit criteria.  ERCOT staff along with the TSP(s) shall then determine what additional system improvements, if any, are necessary to address such violations and will determine the maximum and minimum available fault currents at the interconnection substation for protective relay setting purposes.

Dynamic and Transient Stability (Unit Stability, Voltage, Subsynchronous Resonance) Analysis.  Transient stability studies will be performed where, at the discretion of the TSP(s) or ERCOT staff, stability concerns exist.  In the performance of such studies, all existing or committed generation in the area of study will normally be represented at full net output.   Any resulting increase in generation will be balanced as addressed in the interconnection study scope agreement.

Stability study base cases shall be formed from the latest available approved ERCOT SSWG base cases consistent with the most recently approved ERCOT Dynamics Working Group (DWG) stability data base. The initial transmission configuration in the area of study included in a stability study base case should be identical to that used in the steady-state studies of the same period.   Any generation resource in a stability study base case for which data is not available in the most recently approved ERCOT stability data base or for which data is not otherwise provided to ERCOT or the ERCOT SSWG shall be removed from the case and a corresponding reduction to the load in the LSE utilizing such resource will be uniformly applied.

Transient stability studies may include critical clearing time analyses. In such analyses, the number of cycles for which a transmission line can sustain a fault without causing loss of synchronism of any of the generators is compared to the response of the protection systems.  They may also include voltage stability or subsynchronous resonance studies.  Analyses shall be identified and defined in the full interconnection study scope agreement.

All stability studies shall be performed in accordance with ERCOT’s Planning Criteria, and the results shall identify any additional transmission facility(ies) or other action(s) necessary to ensure conformance to that standard.

Facilities Study.  The facilities study provides complete details of the facility requirements for the direct interconnection of the proposed generation project specifically to the TSP.  The Facility Study only covers the direct interconnection projects, not any related transmission improvements required elsewhere in the ERCOT system.

Results of the facilities study will provide conceptualdesign descriptions, construction milestones, and detailed cost estimates for all transmission and substation facilities proposed to be installed in accordance with the findings and recommendations of the FIS.

2.3.6   FIS Study Report and Follow-up

Following the completion each of the major study elements of the FIS, the FIST will present a preliminary report of their findings and recommendations to the GE or PGC and ERCOT staff.  Any questions, comments, or proposed revisions or clarifications by any party of each major study element shall be made in writing to the FIST within ten (10) working days, after which a final report of each major study element shall be provided to the GE or PGC, ERCOT, and all TSPs.

Should the GE or PGC wish to proceed with the proposed generation interconnection, the GE or PGC must either 1) execute an interconnection agreement along with a financial arrangement with the respective TSP or 2) agree to a financial arrangement with the respective TSP for any transmission construction required to interconnect within 180 days following the issuance of the final full interconnection study report (includes all major study element reports).

Failure of the GE or PGC to meet either of these two requirements within the 180-day period will result in ERCOT determining the interconnection request cancelled and no longer valid.   Should the GE or PGC reconsider and wish to proceed after the 180-day period, the request for generation must start the interconnection study process anew beginning with a new security screening study and payment of the appropriate fee.

2.4   Interconnection Agreement

2.4.1 Standard Generation Interconnection Agreement

Should the GE or PGC decide, within the 180-day period, to proceed with the construction and completion of the proposed generation project and interconnection, they will execute an interconnection agreement with their respective TSP as a condition for obtaining transmission service.  This is in accordance with PUCT Substantive Rule §25.195 (Terms and Conditions for Transmission Service).  The GE or PGC and the TSP shall use the PUCT’s Standard Generation Interconnection Agreement (SGIA).   A template of the SGIA can be found on the ERCOT website.

While ERCOT is the proper entity for a GE or PGC to request a generation interconnection or change process, the actual negotiation of the interconnection agreement shall be conducted directly between the GE or PGC and the TSP.  ERCOT is not a party to the interconnection agreement and will not participate in these negotiations; nor will ERCOT arrange interconnection agreements.

The signed interconnection agreement will be transmitted to ERCOT by the TSP.  TSP’s are required to submit this signed interconnection agreement to the PUCT which may post it through their filing system as open information, unless showing good cause for portions of the filings as confidential. (PUCT Substantive Rules 25.195(e)) The GE/PGC should also provide ERCOT with the status of their air permits and when they receive a permit for their project.

2.4.2  Provisions for Municipals and Cooperatives

While all other provisions of this interconnection process shall apply, municipal utilities or generation and transmission cooperatives developing generation projects that will interconnect to their own transmission systems are exempt from the requirement for an executed interconnection agreement.  In lieu of the interconnection agreement, a letter from a duly authorized official from the municipal utility or cooperative confirming the entity’s intent to construct and operate the project will be deemed by ERCOT sufficient as a public commitment by the municipal utility or cooperative.

Municipal utility or cooperative generation projects that are proposed to interconnect with a different TSP, other than the municipal utility or cooperative, will be required to execute an interconnection agreement as discussed in Section 2.4.1.

3.0	INTERCONNECTION DATA, FEES, AND TIMETABLES

3.1   Generation Plant Data Requirements

The acquisition of data to simulate the realistic behavior of electrical system components is a fundamental requirement of the system planner in the development of both short- and long-range plans for a reliably interconnected transmission system.  This data is also fundamental to developing plans and schemes for the protection of both generation and transmission equipment.  Accordingly, the GE or PGC is required to submit the most current “actual” facility (both generation and substation) or best available “expected” performance data regarding the physical and electrical characteristics of their proposed facilities with their initial generation interconnection request application.

Failure to supply the required data will result in delays in ERCOT processing the interconnection application as well as initiating and completing the required security screening and full interconnection studies.  Recommendations resulting from these studies that may be based on old, false, or simply bad data may adversely affect the safety and reliability of the ERCOT system and can result in damage to generation or transmission equipment.  Ongoing data updates and reviews are also necessary throughout the service life of the generating plant to ensure the adequacy, reliability, and safety of the ERCOT system are maintained over the long term.

In an effort to produce the best available security screening and full interconnection studies, ERCOT suggests that GEs or PGCs begin collecting all appropriate engineering and equipment data from manufacturers as soon as the GE or PGC selects its major equipment for the proposed project.  In order to perform the required security screening and full interconnection studies, the following data and information shall be provided to ERCOT in accordance with the confidentiality provisions discussed in Section 1.3:

Application and Security Screening Study

•  Generation entity information sheet  (See Appendix A.)

•  Generation summary sheet add link

Full Interconnection Study

•  Updates to above information

•  Detailed generating unit information (by unit for each unit) add link

•  Generator data for transient stability studies (by unit for each unit) add link

•  Electrical network drawing(s) including all transformers, capacitors and electrical equipment

•  Generator step-up or unit main power transformer data add link

•  Scalable site drawings showing the location of the proposed generation facilities

Prior to Start of Construction

•  Any significant design changes in the generator(s) or main power transformer(s) to ensure compatibility with the existing transmission system.

Prior to Commercial Service

•  Updates to above information (“as-built” or “as-tested” data in all cases)

•  Subsynchronous resonance (SSR) data (by unit for each unit)

•  Proof of meeting ERCOT requirements (reactive, low-voltage ride-through standards, stability models, PSS)

During Continuing Operations

The GE or PGC shall provide ERCOT and the TSP with any equipment data changes which result from equipment replacement, repair, or adjustment.  In accordance with ERCOT Protocols , the GE or PGC shall provide such data to ERCOT and the TSP no later than 60 days after the date of the actual change in equipment characteristics.  This requirement shall also apply to all future owners throughout the service life of the project/plant.

In order to perform stability (transient and voltage) analyses, the GE or PGC shall provide unit stability information and data to the FIST.  See the ERCOT Dynamics Workign Group Procedural MANual for more detail and GE or PGC dynamics data requirements.  “Typical” unit data is permissible for the initial studies, including the FIS; however, prior to physical interconnection and commercial operation, valid “actual” data must be provided to ERCOT and the TSP.  To aid the GE or PGC in providing this information, four sets of forms have been developed.

EXCMODEL.PDF – Exciter model forms

GENMODEL.PDF – Generator model forms

GOVMODEL.PDF – Governor model forms

STABMODL.PDF – Stabilizer model and excitation limiter forms

Data submitted for transient stability models shall be compatible with ERCOT standard models (Siemens/PTI PSS/E and Powertech Labs Inc TSAT, VSAT and SSAT).  If there is no compatible model(s), the GE or PGC is required to work with a consultant or software vendor to develop and supply accurate/appropriate models along with other associated data.  These models shall be incorporated into the standard model libraries of both software packages.  It is recommended that generation owners and developers encourage manufacturers and software vendors to work together to develop and maintain these important models.  ERCOT recommends wind generation owners, turbine manufacturers, and developers join the modeling efforts of the Utility Wind Integration Group (UWIG, www.uwig.org).

Appendix B of this document contains a copy of all of the forms required under this section.  Also, these forms are available from the ERCOT internet website.

3.2   Interconnection Study Fees

PUCT Substantive Rule §25.198 (Initiating Transmission Service) states in part that the customer requesting transmission service shall be responsible for all costs associated with the completion of the security screening and full interconnection studies.

3.2.1  Security Screening Study Fee

The ERCOT security screening study fee is a nonrefundable fee ranging from $1,000 to $5,000 depending on the total plant capacity associated with each specific interconnection request.  ERCOT has determined that basing this fee on total plant capacity is reasonable because total plant capacity generally determines the amount of work necessary to complete the study.  The appropriate security screening study fee must be remitted for each generation interconnection request (i.e., each individual interconnection location, in-service date, and total plant capacity at this specific interconnection location) at the time the application is submitted to ERCOT.

| Total Plant Capacity, MW | Screening Study Fee |
| --- | --- |
| 10 to 74 | $1,000 |
| 75 to 149 | $2,000 |
| 150 to 249 | $3,000 |
| 250 to 499 | $4,000 |
| 500 or greater | $5,000 |

3.2.2  Stability Modeling Fee

The ERCOT stability modeling fee is a non-refundable stability modeling fee of $15 per megawatt of total capacity and is paid directly to ERCOT when a full interconnection study is requested.  This fee will reimburse ERCOT for the development of stability software models for each proposed generation unit and allow for continually updating current models as new equipment changes are made.  Payment of the stability modeling fee to ERCOT does not release the GE or PGC from their obligation to provide ERCOT accurate and appropriate stability software models and data (including load) for each of their proposed generation plants.

3.2.3 Full Interconnection Study Fee/Cost

The full interconnection study fee/cost is paid directly to the TSP(s) completing the studies associated with the FIS.  The fee/cost will be agreed on and specified in the study scope agreement. The TSPs will directly invoice the GE or PGC for the reasonable costs associated with undertaking and completing the FIS.

ERCOT recommends that the GE or PGC and the TSP provide for a payment methodology and cancellation provision in the full interconnection study scope agreement.  If the GE or PGC cancels the generating project during the term of the full interconnection study, the GE or PGC is required to immediately notify ERCOT and all TSPs participating in the study team.  The GE or PGC is responsible for all costs associated with any work performed or non-cancelable commitments made prior to notifying ERCOT and the TSP(s) of the termination date of the project.  ERCOT highly recommends the TSP(s) receives the study fee before proceeding with work.

The non-refundable stability modeling fee and proof of site control (as discussed in Section 2.3.2) must be received by ERCOT within 180 days after completion of the security screening study before a full interconnection study will be initiated

3.3  Interconnection Process Timetables

PUCT Substantive Rule §25.198 (Initiating Transmission Service) provides deadlines for ERCOT and TSPs to complete and report on the required interconnection studies provided that the GE or PGC submits all required data and appropriate fee(s).  Therefore, it is vital that the GE or PGC ensure that ERCOT staff and the TSP(s) performing these studies receive all required data in order to establish reasonable study models and assumptions that provide meaningful results and recommendations for interconnecting the proposed generating project.

The ERCOT generation interconnection process can take from 52 to 440 days to complete from initial application to signed interconnection agreement.  ERCOT staff’s experience is that most generation interconnection requests can be completed in 90 to 270 days.  As a result, ERCOT encourages TSPs and the GE or PGC work to optimize this process to reduce the time necessary for the required studies.

Because the full interconnection study is generally the “critical” path item in the generation interconnection process, ERCOT recommends that a timetable for the FIS be developed and included in the study scope agreement.  In addition, major improvements to the transmission system resulting from interconnection requests should be identified as early in the process as possible so project validity can be considered before the parties go forward with extensive interconnection studies.  Once the FIS is underway, the parties may determine that an adjustment to the original estimated completion date is necessary.  Should this schedule adjustment become necessary, the parties are to provide notice to ERCOT and FIST as soon as practicable, indicating the revised expected completion date.

The following timetable complies with PUCT Substantive Rule §25.198 (Initiating Transmission Service).

| TASK | Responsible Entity | Time Required to Complete (Days) |
| --- | --- | --- |
| Initial Review of Generation Interconnection Request Application | ERCOT | 1 to 7 |
| Perform Security Screening Study (after application deemed complete) | ERCOT | 7 to 90 |
| Decision to Pursue Full Interconnection Study (following issuance of Screening Study by ERCOT) | GE/PGC | up to 180 |
| Develop Scope Agreement for Full Interconnection Study (following GE’s or PGC’s notification to ERCOT of desire for Full Interconnection Study and remittance of appropriate fees) | ERCOT, TSP, FIST, GE/PGC | up to 60 |
| Perform Full Interconnection Study (following agreement on scope) | TSP, FIST | 40 to 300 |
| Steady State and Transfer Analysis |  | 10 to 90 |
| System Protection Analysis (following Steady State Analysis) |  | 10 to 30 |
| Dynamic and Transient Stability Analysis (following System Protection Study) |  | 10 to 90 |
| Facilities Study |  | 10 to 90 |
| Study Report Review & Acceptance (following issuance of Full Interconnection Study) | ERCOT, TSP, FIST, GE/PGC | 5 to 15 |
| Negotiate and Execute Interconnection Agreement (following acceptance of Full Interconnection Study) | TSP and+__ GE/PGC | up to 180 |

4.0  GENERAL AND TECHNICAL STANDARDS

This section describes the general and technical standards that must be satisfied by a generation entity (GE) or power generation company (PGC) in order to interconnect generating units greater than 10 MW with the ERCOT transmission system.  Market participants desiring to interconnect small-scale distributed generation should refer to PUCT Substantive Rules §25.211 (Interconnection of On-Site Distributed Generation) and §25.212 (Technical Requirements for Interconnection and Parallel Operation of On-Site Distributed Generation).  These rules detail the technical and other interconnection requirements for on-site distributed generation.

The following general and technical standards were approved by the ERCOT Technical Advisory Committee (TAC) on August 6, 2003, and have been incorporated into various sections of the ERCOT Protocols and Operating Guides.  Low-voltage ride-through requirements were developed by FERC with NERC input.

4.1  Application

All generating units (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected to the same transmission bus that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT transmission grid, and that were not in operation prior to Board approval of this standard shall meet all of the requirements of this standard.

Any such generating units in operation earlier than the ERCOT Board approval date for this standard shall meet the requirements of standards applicable to that generating unit prior to the Board approval date for this standard, and shall meet all of the requirements of this standard except the installed capability requirements.  Previously applicable standards include the interim standards approved by the ERCOT Board, the standards enumerated in ERCOT Protocols Section 6.5.7, and such other standards outlined in the interconnection requirements and ERCOT Operating Guides.

Upon submission by a GE or PGC to ERCOT of a specific proposal for requirements to substitute for those of the applicable standard, ERCOT shall either approve such alternative requirements or provide the submitter an explanation of its objections to the proposal.  Alternative requirements may include supplying additional static or dynamic reactive power capability as necessary to meet the area’s reactive power requirements.  Pending changes to PUCT Rules, an induction generator may elect to contribute to be credited to TCOS  in lieu of meeting the installed capability requirements contained herein.

4.2  Installed Capability Requirements

- Power Factor Requirements

Generating units to which this standard applies shall maintain an overexcited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less.  Both capabilities shall be determined at the generating unit’s maximum net power output to be supplied to the transmission grid and at the transmission system voltage profile established by ERCOT, and both shall be measured at the point of interconnection to the TSP.  (Please note: Not measured at generator unit terminals)

Upon request to and with approval from ERCOT, multiple generating units connected to the same transmission bus may be treated as a single generating unit for the purposes of these power factor requirements only.  For any unit so aggregated, specific power factor requirements based upon the reactive power contribution of that unit to the total reactive power obligation of the aggregation will be assigned to that unit and shall become that unit’s required installed reactive capability at the generating unit’s maximum net active power output.

No generating unit equipment replacement or modification shall reduce the reactive capability of the generating unit below the level required of that generating unit prior to the replacement or modification, unless specifically approved by ERCOT.

- Generating units to which this standard applies shall also maintain the following capabilities:

1.  Over-excitation limiters shall be provided and coordinated with the thermal capability of the        generator field winding and protective relays in order to permit short-term reactive capability that allows at least 80% of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)	  10	  30	  60 	120

Field Voltage %	208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic        AC voltage regulator to reduce field current to the continuous rating.  Return-to-normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

2.  Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection resulting from operator error or equipment misoperation.

4.3  Operating Requirements

All generating units shall maintain the transmission voltage at the point of interconnection to the transmission grid as directed by ERCOT within the operating reactive power capability of the unit(s).

At all times a generating unit is online, the required installed reactive capability must be available for utilization at the generating unit’s continuous rated active power output.  In addition, reactive power up to the unit’s operating capability must also be available for utilization at lower active power output levels.  In no event shall the reactive power available be less than the required installed reactive capability multiplied by the ratio of the lower active power output to the generating unit’s continuous rated active power output.  Also, any reactive power available for utilization must be fully deployed to support system voltage upon request by ERCOT or a transmission operator designated by ERCOT.

GEs or PGCs shall install power system stabilizers (PSS) on each new generating unit to be interconnected unless specifically exempted from this requirement by ERCOT staff.  IF ERCOT or the TSP issues settings for the PSS, the PSSs shall be kept in service and maintained in working order throughout the service life of the plant.  Wind farms are induction in nature and are exempt from the PSS requirement.

Each generating unit shall be operated with any automatic voltage regulator (AVR) set to regulate generator terminal voltage and any power system stabilizers in use, whenever possible, unless specifically permitted to operate otherwise by ERCOT.  If the service status of a PSS is changed, it shall be reported to ERCOT as soon as practicable.

The PSS and excitation system should also be tested periodically, with the longest interval between tests not exceeding five years.  PSS settings should not be changed without performing proper and accurate tuning studies.  Periodically, the TAC Reliability Operations Subcommittee Dynamics Working Group will perform studies to determine if PSS setting changes are necessary.  GEs or PGCs and TSPs shall work jointly to prevent possible adverse conditions by communicating any changes or modifications to the PSS in a timely manner.

Generation resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT ,as conveyed by way of their Qualified Scheduling Entity (QSE), unless equipment damage is imminent.

4.4  Information Supply Requirements

Unit AVR and PSS modeling information required by the ERCOT Planning Criteria shall be determined from actual unit testing as described in the ERCOT Operating Guides.  Within 30 days of ERCOT’s request, the results of the most recent test actually performed shall be supplied to ERCOT, the Transmission Operator (TO) and the appropriate TSP.

Whenever the operating mode of a generating unit’s AVR or PSS is changed or modified while the unit is operating, the QSE shall promptly inform ERCOT.  The QSE shall also supply AVR or PSS status logs to ERCOT upon request.   Within 30 days of ERCOT’s request, GEs or PGCs shall provide ERCOT with the operating characteristics of any generating unit’s equipment protective relay system or controls that may respond to any potential temporary excursions in voltage with actions that could lead to tripping of the generating unit.

Any short-term inability of a generating unit to meet its reactive capability requirements shall be immediately reported to ERCOT, the TO and the appropriate TSP.

ERCOT and the TSP shall be notified of any anticipated equipment changes that affect the reactive capability of an operating generating unit no less than 60 days prior to implementation of the changes, and any such changes that decrease the reactive capability of the generating unit below the required level must be approved by ERCOT prior to implementation.

High reactive loading and reactive oscillations on generation units should be immediately communicated to ERCOT, the TO, the appropriate TSP, and the QSE.

The tripping off line of a generating unit due to voltage or reactive problems should be immediately reported to ERCOT, the TO, the appropriate TSP, and the QSE.

4.5  Compliance Monitoring

GEs or PGCs shall conduct generating unit reactive capability tests as specified in the ERCOT Protocols and Operating Guides.  Test results shall be reported to ERCOT, which shall forward them to the TSPs.  If the generating unit’s reactive output is limited by transmission system conditions during the tests, this shall be noted on the test report.

Upon failure of a generating unit to provide either leading or lagging reactive up to the required capability of the unit upon request from ERCOT or a TSP, ERCOT may, at its discretion, report the performance of the generating unit to the ERCOT Compliance Office, except under force majeure conditions or ERCOT-permitted operation of the generating unit.

While operating at less than the maximum reactive capability of the generating unit, should the GE or PGC fail to maintain the transmission system voltage at the point of interconnection with the TSP within 2% of the scheduled voltage, ERCOT may, at its discretion, report this to the ERCOT Compliance Office, except under force majeure conditions or ERCOT-permitted operation of the generating unit.

The ERCOT Compliance Office will investigate alleged non-compliance conditions using the ERCOT Compliance Procedures.  The ERCOT Compliance Office will advise the generation resource, its QSE, ERCOT, and the appropriate TSP planning and operating staffs of the results of such investigations.

4.6  Harmonic Requirements

Harmonics can cause telecommunication interference, thermal heating in transformers, disruptions to solid-state equipment, and resonant over voltages.  In order to protect equipment from damage, harmonics must be managed and mitigated; therefore, all generating units proposed for interconnection with the ERCOT system shall be in compliance with PUCT Substantive Rule §25.51 (Quality of Service).

4.7  Special Requirements for Wind Generation

4.7.1   Power Factor Design Criteria (Reactive Power)

A wind generating plant shall maintain a power factor within the range of 0.95 leading to 0.95 lagging, measured at the point of interconnection as defined in the SGIA.  The power factor range standard can be met by using, for example, power electronics designed to supply this level of reactive capability (taking into account any limitations due to voltage level, real power output, etc.) or fixed and switched capacitors if agreed to by ERCOT and the TSP.  The GE or PGC shall not disable power factor equipment while the wind plant is in operation.  Wind plants shall also be able to provide sufficient dynamic voltage support in lieu of the power system stabilizer and automatic voltage regulation at the generator excitation system.

4.7.2   Supervisory Control and Data Acquisition (SCADA) Capability

The wind plant shall provide SCADA capability to transmit data and receive instructions from ERCOT or the TSP in order to protect system reliability.   ERCOT, the TSP, and the GE or PGC shall determine what SCADA information is essential for the proposed wind plant, taking into account the size of the plant and its characteristics, location, and importance in maintaining generation resource adequacy and transmission system reliability in its area.

4.7.3   Wind Generation Dynamics Data

In order to perform stability (transient and voltage) analysis of the ERCOT transmission system, the Reliability and Operations Subcommittee Dynamics Work Group (DWG) maintains a database of dynamics models of all ERCOT generation, including wind generation, which is available for all TSPs.  In order to adequately simulate the behavior of the ERCOT system, it is necessary for all wind plants to be modeled, especially with the increasing concentration of wind generation in some areas in ERCOT.  Unlike traditional generation facilities, wind generators do not have generic models.  In addition, each wind technology requires a substantially different model to accurately simulate its dynamic performance.  The facility owner is responsible for providing all models and data for their facility.  Currently there are three sources of wind models: the ERCOT wind models, PTI wind models, and other sources including the equipment manufacturer.  If an ERCOT or PTI wind model is not appropriate for the facility, the GE or PGC shall obtain the most accurate and appropriate model and the associated data for their wind plant from the manufacturer, and supply it to ERCOT and the TSP to which it is connected, with the legal authority to provide to all TSPs.  Models and data will be held confidential under ordinary ERCOT Transmission Provider code-of-conduct rules.  Regardless of the model source, the GE or PGC shall provide the following data:

- Model shall be compatible with the PSS/E version currently used in ERCOT.

- Description of voltage control method.

- How they will meet ERCOT reactive requirements.

- A one-line diagram of the proposed facility.

- Data for all transformers.  The data should include:

  - MVA rating.

  - High and low side rated voltage.

  - Number of taps, and step size.

  - Impedance, including base values if different from rated values listed above.

  - Existing tap settings

- Generator data including:

  - Generator manufacturer and model.

  - Rated voltage.

  - Rated MVA.

  - Reactive capability, leading and lagging.

  - Rated MW output.

  - Net MW output.

  - Transient or subtransient reactance.

  - Transient or subtransient time constant.

  - Total inertia constant, H, of generator, including the shaft and gearbox.

  - Under frequency and under voltage protection.

  - Over frequency and over voltage protection.

- If your machine can be modeled using one of the ERCOT or PTI wind models, state which model applies to your facility.  Include instruction on how to set up and execute analysis.

- If the model is not an ERCOT or PTI model, provide either dynamic model source code for the machine and associated data or dynamic model object code for the machine and associated data.

  - If providing object code, the object code must be updated for PSS/E version changes or as requested by the DWG and/or ERCOT.

  - If your machine can be modeled using one of the ERCOT wind models, state which model applies to your facility.  Include instruction on how to set up and execute analysis.

  - Models for the wind turbine, system protection, reactive resources, etc., can be embedded into a single source code or be provided separately.

  - Models need to account for rotor mass, aerodynamic energy conversion, pitch control,

  - Models should account for multiple wind farm interactions

- If the model is not an ERCOT model, the following requirements apply:

  - Wind models using bus numbers shall be compatible with the ERCOT bus numbering system, and shall allow the user to determine the bus numbers.

  - Wind models shall be capable of adjusting both load flow and dynamic parameters in response to changing network conditions, and the presence of multiple windfarms.

- Number of machines by manufacturer types

- List any reactive sources such as capacitor banks, STATCOMS, etc. Provide the number of devices, location of the devices, step size, speed of switching, location where voltage is sensed and controlled, control strategy, and voltage limits.  For dynamic reactive devices, provide the appropriate PTI PSSE model and data.

- Line data from the point of connection to each wind generator.  Include:

  - Line type (overhead or underground)

  - Line length

  - Line resistance in ohms/1000 ft

  - Line reactance in ohms/1000 ft

  - Line susceptance in mhos/1000 ft

  - Line rating in amperes

4.7.4   Transformer Tap Position

The TSP providing the interconnection will work with the GE or PGC to select the tap position on the main power transformers, and the GE or PGC will confirm the use of this tap position with the TSP and ERCOT.

APPENDIX A

GENERATION ENTITY INFORMATION SHEET

GENERATION ENTITY INFORMATION SHEET - PLEASE PRINT CLEARLY-

FORM MUST BE SIGNED AND SUBMITTED WITH REQUEST

Transmission Customer  (Generating Entity): _____________________________________

Contact Person:_____________________________________________

Title: _________________________________________________

Company: ______________________________________________

Mailing Address: ______________________________________

City: ___________________________ State: _________________ ZIP: ________________

Company Internal Mail Code(s): _____________________________

Telephone Number: (______) ______________________ Facximile (FAX) Number: (______) _____________________

Internet email Address: ____________________________________

Requested Transmission Energization Date (MM/DD/YYYY): ______________________________

Generation In Service (MM/DD/YYYY): Start __________________ through __________________

____________________________________________(generating entity) is, or will be upon commencement of service, an eligible customer.  An eligible customer is any of the following: the transmission provider (for all uses of its transmission system) and any electric utility, federal power marketing agency, exempt wholesale generator, qualifying facility, or power marketer.  An eligible customer may designate an agent to represent it in arranging for interconnection.

Accurate/appropriate information and test data about generator step-up transformers, all generator data including data for stability studies (transient, voltage, etc.) and subsynchronous resonance data will be provided to ERCOT and interconnected TSP before the generation goes into commercial operation.  I understand that all of this data will become public and added to the ERCOT databases (including power flow base cases, stability, system protection, CDR, etc) when a full interconnection study is requested.  This data shall be reviewed and updated when the plant goes into commercial operation.  In addition, any updates to this information will be provided within 60 days to ERCOT and the TSP as changes or upgrades are made during the life of the plant.  This requirement also applies to all future owners of this project/plant.

The generating entity and any future owners of the plant agree to comply with these data requirements along with all applicable ERCOT and NERC requirements, including, without limitation, those contained in the ERCOT Protocols and ERCOT Operating Guides.  It is understood and agreed that such requirements are subject to change from time to time, and such changes shall automatically become applicable based upon the effective date of the approved change.

Authorized Signature:

_____________________________________Date: ______________

__________________________________

(Name printed or typed)

By: ______________________________

As defined in PUCT Substantive Rule  §25.211(c)(10)

ERCOT Protocols Section 1.3.1.1 (10)

Public Utility Regulatory Act (PURA) as amended, Chapter 37, Certificate of Convenience and Necessity, and PUCT Substantive Rule §25.101

PURA 37.056 (c)

The ERCOT Power System Planning Charter and Processes document can be found on the ERCOT website

PUCT Substantive Rule  §25.101 (b)(3)

Substation load forecasts are provided to ERCOT by each TDSP through the Annual Load Data Request (ALDR).

With the concurrence of ERCOT, the GE or PGC may specify any reasonable allocation of the resource output among Load Serving Entities (LSE) in the study cases.  Absent such specification or allocation by the GE or PGC, ERCOT, for study purposes, will assume the proposed generation project’s output will be utilized to proportionately displace unspecified generation resources in ERCOT.  ERCOT will determine how to treat any output remaining after displacement on a case-by-case basis (e.g., ERCOT could proportionally increase all ERCOT loads in an aggregate amount to balance the resource’s output)

As defined in PUCT Substantive Rule §25.211(c)(10)

Transmission Cost of Service

ERCOT Operating Guides Section 2.2.4

ERCOT Protocol Operating Guide Section 2.10