Texas Nodal

Energy Management System

Requirements Specification

For Load Forecasting

Version 0.91

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 12/01/2006 | 0.90 | These requirements were developed through an iterative process and reviewed by various ERCOT teams, including Nodal EMS team, Nodal IDA team, ERCOT Operations and IT Support teams, as well as EMS vendor. | Nodal EMS Team |
| 2/16/2007 | 0.91 | Incorporated comments from TPTF | Nodal EMS Team |

Table of Contents

1.	Introduction	6

1.1	Purpose	6

1.2	Objectives	6

1.3	Scope	7

1.4	Traceability	7

2.	Load Forecasting	8

2.1	Load Forecasting Inputs and Outputs	8

2.2	Load Forecasting Functional Process Diagrams	9

2.2.1	Mid-Term Load Forecast Sub-Process	9

2.2.2	Long-Term Load Forecast Sub-Process	10

2.3	Assumptions and Dependencies	10

3.	Functional Requirements	11

3.1	Weather Data	11

3.2	Forecasts	11

3.3	Forecast Modification and Update Capability	13

3.4	Model Training	13

3.5	Data Posting	13

3.6	Forecast Accuracy Analysis and Archive	14

4.	Supplementary Requirements	16

5.	Protocol Coverage	22

This page is intentionally left blank.

Requirements Specification

This Requirements Document is Subordinate To and Compliant with the Texas Nodal Protocols Effective February 2007.

# Introduction

The requirements for Texas Nodal market implementation are described in the Texas Nodal Protocols.  This document focuses on elaborating the requirements for the Load Forecasting function of the Energy Management System.

This Requirements Specification is a part of the complete set of specification documents for the Texas Nodal market implementation.  For implementation purposes the Texas Nodal market functions are categorized into multiple systems based on clear distinction in functionality.  The Energy Management System is one of these systems.

The EMS requirements are documented in the Texas Nodal EMS Requirements Specification document; supplemented by the following Requirements Specifications:

- Texas Nodal EMS Data Model Requirements Specification

- Texas Nodal EMS SCADA Requirements Specification

- Texas Nodal EMS Dynamic Ratings Requirements Specification

- Texas Nodal EMS Forced Outage Detection Requirements Specification

- Texas Nodal EMS Generation Sub-system Requirements Specification

- Texas Nodal EMS Load Forecasting Requirements Specification

- Texas Nodal EMS Wind Power Forecasting Requirements Specification

- Texas Nodal EMS State Estimator Requirements Specification

- Texas Nodal EMS Network Security and Stability Analysis Requirements Specification

- Texas Nodal EMS Voltage Support Requirements Specification

- Texas Nodal EMS Outage Evaluation Requirements Specification

The definitions and acronyms from Section 2 of the Protocols are used in this document as applicable.  Any additional definitions and acronyms are defined in the Texas Nodal EMS Requirements Specification as needed.

## Purpose

The primary purpose of this requirements specification document is to fully describe the external behavior of the Load Forecasting function.  It also describes nonfunctional requirements, design constraints, and other factors necessary to provide a complete and comprehensive description of the requirements necessary to design and develop the corresponding software systems.

## Objectives

The objective of this requirements specification is to:

- Specify mutually exclusive and collectively exhaustive set of requirements for Load Forecasting

- Ensure that requirements are in compliance with the Nodal Protocols

- Ensure that requirements are traceable to Nodal Protocols, NERC, FERC and any other applicable standards

## Scope

The scope of this document is to elicit requirements for the Load Forecasting function to be in compliance with the Nodal Protocols published in May 2006, NERC, FERC and PUCT guidelines.  However, elaborating requirements that would change the intent of the protocols or proposing a design for the system is outside the scope of this document.  To ensure compliance the designers and developers of the systems are required to read and understand the Nodal Protocols.

Any scope changes to this requirements specification due to alternate design proposals must be driven by Nodal Protocol Revision Request (NPRR) and channeled through Nodal Change Control Board (CCB).  Any scope changes to this requirements specification due to further elaboration, while still being in compliance with Nodal Protocols, must be channeled through Nodal CCB.

## Traceability

All Load Forecasting requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC Standards, FERC guidelines, and PUCT documents.

These requirements are based on the May 2006 version of Nodal Protocols and NERC, FERC, and PUCT requirements approved as of May 2006.

# Load Forecasting

The Load Forecasting function is a sub-system of the Energy Management System (EMS). The primary purpose of the Load Forecasting is to provide forecasted Mid-Term and Long-Term load information to various ERCOT systems and business processes.

The Mid-Term Load Forecast (MTLF) consists of hourly loads for each Weather Zone and the ERCOT system for the remainder of the current day and the next 7 days.  Operations support staff use this information to perform short term analysis of the integrity of the ERCOT grid.  The Reliability Unit Commitment processes also use the MTLF to commit resources to meet anticipated load.

The Long Term Load Forecast (LTLF) consists of the daily minimum and maximum demand for each Weather Zone for the next 365 days. The LTLF is a new forecast that will be produced in the ERCOT Nodal Market and will be used as input along with resource availability data to assist with long term planning and reporting of resource adequacy.

The MTLF and LTLF provide load pattern information to the outage evaluation process  that assesses the various impacts of requested outages to the ERCOT system.

## Load Forecasting Inputs and Outputs

This section provides a summary of inputs and outputs to the Load Forecasting function. Table 1 lists all the required input data to the Load Forecastingsfunction. The “Source” column of the input table identifies the source where the data is provided to the Load Forecasting function.

Table 1: Load Forecasting Inputs

| Source | Data |
| --- | --- |
| Weather Service vendor | - Historical weather data - Most recent weather data – actual hourly weather station data for each Weather Zone - Weather forecasts for each weather station for each Weather Zone |
| SCADA | Most recent Weather Zone load calculations |
| EDW | - Historical load information for each Weather Zone - Load growth rate for each Weather Zone *These data are only required from Enterprise Information Systems (EDW) initially. |

Table 2 lists all the required output data of the Load Forecasting function. The “Destination” column of the output table identifies the receiving system.

Table 2: Load Forecasting Outputs

| Destination | Data |
| --- | --- |
| RUC | MTLF |
| STNET | MTLF |
| VSAT/TSAT | MTLF |
| Outage Evaluation | - MTLF - LTLF |
| MMS | - MTLF - LTLF |
| MIS | - MTLF - LTLF - Weather forecasts - Adverse weather condition indication for each Weather Zone |
| EDW | - Actual and forecasted weather data for each weather station for each Weather Zone - Actual load for each Weather Zone - Mid-Term Load Forecasts - Long Term Load Forecasts |

## Load Forecasting Functional Process Diagrams

### Mid-Term Load Forecast Sub-Process

Brief Description:  ERCOT receives current actual load data from SCADA and weather data from a weather service. Based on the current and historical load and weather data and the hourly weather forecast from weather service, the load forecasting system shall create the MTLF containing forecasted loads for each hour for the remainder of the current day and the next 7 days.  The MTLF is used by RUC, Real-time Operations, Market Participants, operational reliability studies (power flows), and Outage Evaluation.

### Long-Term Load Forecast Sub-Process

Brief Description:  Based on historical actual load data and the load growth rate, the Load Forecasting system shall create the LTLF containing the daily minimum and maximum Load Forecast for the next 365 days.  The LTLF will be used by Outage Evaluation, Market Participants and to assess operational reliability in the future.

## Assumptions and Dependencies

The accuracy of the MTLF depends on consistent good weather load modeling techniques that include specific weather data with a strong correlation to the load of each Weather Zone, and the tuning of these models with weather and Load Forecast errors.  The generation of the MTLF is dependent on weather data forecasts at each weather station from a weather service vendor.

The accuracy of the LTLF depends on consistent good load modeling techniques and load growth rates that truly reflect the load growth of each Weather Zone.  The LTLF is dependent on input each day for the next 12 month period.

All required Load Forecast data shall be available to fulfill the performance monitoring, notification and posting requirements.  It is assumed that performance metrics, notifications and MIS postings are handled by an external system and are therefore outside of the scope of these requirements.

The improvements to the load forecasting applications that are being developed in the Zonal market will be carried over into the Nodal system through change control.

# Functional Requirements

The following tables describe the requirements for Load Forecasting as prescribed by the Nodal Protocols or as deemed necessary to support the Load Forecasting functions indicated.

## Weather Data

| Requirement ID | LF-FR1 |
| --- | --- |
| Requirement Name | Weather Service Inputs |
| Protocol Reference | Section(s) 3.12.1 (2)(a), and 6.3.2 (2)(a)(ii) |
| Coverage of Protocol | Partial, and Full |
| Traceability to Sub-Process | COPS.P05.I-2 and COPS.P05.I-3 |
| Sub-Process Element Coverage | Partial and Partial |
| Description: The Load Forecasting function shall receive automatically the following data at least once every hour, or on request by an ERCOT operator: - Weather data forecasts for the remainder of the current day and the next 7 days - Actual weather data at each weather station within each Weather Zone - An adverse weather condition indicator for each Weather Zone |  |

| Requirement ID | LF-FR2 |
| --- | --- |
| Requirement Name | Weather Parameter Configuration |
| Protocol Reference | Section(s) 3.12.1 (2)(a) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The Load Forecasting function shall support the following: - One or more weather stations per each Weather Zone - Configurable number of Weather Zones (initially set to eight (8) zones) - Weather data at each weather station shall contain the following ten (10) weather parameters: - Temperature - Dewpoint - Relative humidity - Heat index - Wind chill - Wind direction - Wind speed - Temperature wet bulb - Cloud cover - Sunshine minutes |  |

## Forecasts

| Requirement ID | LF-FR3 |
| --- | --- |
| Protocol Reference | Section(s) 3.12 (a); 3.12.1 (1), and 3.12.1 (2)(a) |
| Requirement Name | Mid-Term Load Forecast (MTLF) |
| Coverage of Protocol | Partial, Partial, and Full |
| Traceability to Sub-Process | COPS.P05.P-1 |
| Sub-Process Element Coverage | Partial |
| Description: Each hour the Load Forecasting function shall generate a MTLF that consists of hourly MWh loads for the reminder of the current day and the next 7 days for each of the Weather Zones, and the ERCOT system. Inputs for the calculation of the MTLF shall be: - The hourly updated weather parameters for weather stations within each Weather Zone - The actual hourly MWh load from SCADA by Weather Zone and the ERCOT system - Weather forecast for each weather zone for the next 7 days The Load Forecasting function shall provide the associated time when the forecast was last updated. This information shall be available to all the target applications that use the MTLF. |  |

| Requirement ID | LF-FR4 |
| --- | --- |
| Requirement Name | Long Term Load Forecast (LTLF) |
| Protocol Reference | Section(s) 3.12 (b), and 3.12.2 (1) |
| Coverage of Protocol | Partial and Partial |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: Each day The Load Forecasting function shall produce and update onLTLF consisting of a daily minimum and maximum demand forecast for the next 365 days for each Weather Zone and the ERCOT system. The inputs shall be: - Daily actual minimum and maximum hourly integrated loads by Weather Zone - Model training based on historic daily minimum and maximum hourly integrated loads by Weather Zone - MTLF Max and Min for first 7 days The Load Forecasting function shall provide the associated time when the forecast was last updated. This information shall be available to all the target applications that use the LTLF. |  |

| Requirement ID | LF-FR5 |
| --- | --- |
| Requirement Name | Long Term Demand Forecast |
| Protocol Reference | Section(s) 3.2.2 (1) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The Load Forecasting function shall produce and update once a week a Long Term Demand Forecast consisting of peak demand forecasts for each load zone and the ERCOT system for each week of the next 12 months. The Load Forecasting function shall provide the associated time when the forecast was last updated. This information shall be available to all the target applications that use the LTLF. |  |

## Forecast Modification and Update Capability

| Requirement ID | LF-FR6 |
| --- | --- |
| Requirement Name | Forecast Modification and Update Capability |
| Protocol Reference | Section(s) 3.12 (a), 3.12.1 (3), 3.12.2 (3), 6.3.2 (2) (b) |
| Coverage of Protocol | Partial, Partial, Full, Full |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The Load Forecasting function shall provide the capability for ERCOT Operators to view, modify, and update on demand the MTLF’s and the LTLF’s. Modified information shall be flagged and orginal and modified values shall be retained. Revised data shall be posted to MIS. |  |

## Model Training

| Requirement ID | LF-FR7 |
| --- | --- |
| Requirement Name | Model Training |
| Protocol Reference | Section(s) 3.12.1 (1), 3.12.1(2) (b), 3.12.2 (1) |
| Coverage of Protocol | Partial, Full, Partial |
| Traceability to Sub-Process | COPS.P05.P-1, COPS.P05.I-6 |
| Sub-Process Element Coverage | Partial |
| Description: The Load Forecasting function shall provide a self training mode to train and retrain the MTLF weather-based load model. The Load Forecasting function shall also have the capability to use historic actual daily minimum and maximum hourly integrated loads by Weather Zone to support self-training of the LTLF. |  |

## Data Posting

| Requirement ID | LF-FR8 |
| --- | --- |
| Requirement Name | Data Available for Posting |
| Protocol Reference | Section(s) 3.12(a), 3.12 (b), 3.2.2 (1) and 6.3.2 (2)(a)(ii) |
| Coverage of Protocol | Partial, Partial, Full, and Partial |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The Load Forecast function shall make the following data available to the MIS: - The MTLF hourly Load Forecasts for each Weather Zone and the ERCOT system and adverse weather conditions available each hour (MIS Secured Area) - The LTLF daily minimum and maximum demand forecasts for each Weather Zone on a daily basis (MIS Secure Area) - The Long Term Demand Forecasts on a weekly basis |  |

| Requirement ID | LF-FR9 |
| --- | --- |
| Requirement Name | Operating Day MTLF |
| Protocol Reference | Section(s) 4.2.3(d) |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The load forecasting function shall compare the latest MTLF generated prior to 0600 of the Day Ahead for the following Operating Day with updates and make available to the messaging system indicating any changes to the Operating Day forecasts. |  |

## Forecast Accuracy Analysis and Archive

| Requirement ID | LF-FR10 |
| --- | --- |
| Requirement Name | Operating Day MTLF Accuracy Archive |
| Protocol Reference | Section(s) 8.2 (2)(c)(i) |
| Coverage of Protocol | Full |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The Load Forecasting function shall compare the Operating Day MTLF for ERCOT that is posted at 0600 of the Day-Ahead with the actual ERCOT load for each hour of the Operating Day and make this information available to the EDW. |  |

| Requirement ID | LF-FR11 |
| --- | --- |
| Requirement Name | Mid-Term Load Forecasts Archive |
| Protocol Reference | Section(s) 17.3.5 |
| Coverage of Protocol | Partial, Partial |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | Archive |
| Description: The Load Forecasting function shall make the following information available to the EDW: - The MTLF hourly Load Forecasts and the calculated forecast errors for each Weather Zone and the ERCOT system - The MTLF hourly weather data forecasts and the calculated forecast errors for each weather station - All original data that was modified and the associated modifications |  |

| Requirement ID | LF-FR12 |
| --- | --- |
| Requirement Name | Archive of Actual Information |
| Protocol Reference | Section(s) 17.3.5 |
| Coverage of Protocol | Partial, Partial |
| Traceability to Sub-Process | COPS.P05.I-1, COPS.P05.I-5 |
| Sub-Process Element Coverage | Partial |
| Description: The Load Forecasting function shall make the following information available to the EDW: - Actual hourly load - Actual hourly weather data - Actual daily maximum and minimum demands of Weather Zones and the ERCOT system |  |

# Supplementary Requirements

| Requirement ID | LF-SR1 |
| --- | --- |
| Requirement Name | Forecasting Execution Performance |
| Requirement Type | Performance |
| Description: The execution time of the following load forecasting functions shall be completed in five (5) minutes or less: - The MTLF weather load modeling and the associated Load Forecasting for all Weather Zones and the ERCOT system - The LTLF daily minimum and maximum load modeling and the associated daily Load Forecasting for the ERCOT system and all Weather Zones for 365 days |  |

| Requirement ID | LF-SR2 |
| --- | --- |
| Requirement Name | Recreate LTLF |
| Requirement Type |  |
| Description: The Load Forecasting function shall have the capability to use the archived actual and forecasted weather and load data to recreate the LTLF at any time. |  |

| Requirement ID | LF-SR3 |
| --- | --- |
| Requirement Name | MTLF Accuracy |
| Requirement Type | Forecast Accuracy |
| Description: When back-casting using actual weather data, the hourly MTLF for each Weather Zone shall meet the following Load Forecast error criteria: - Over all hours of each Operating Day the Load Forecast error shall not be greater than 2%. The forecast error calculated shall be defined as the RMS error of the difference between actual values and forecasted values (using actual weather data) divided by the actual value, for the forecasting period. |  |

| Requirement ID | LF-SR5 |
| --- | --- |
| Requirement Name | Day-Ahead MTLF Accuracy |
| Requirement Type | Forecast Accuracy |
| Description: Based upon the MTLF produced at 0600 Day-Ahead, the RMS error of (actual load – forecast load) divided by the actual value shall not be greater than 3% for the next day. Note: A business process will determine the cause of errors of exceedance. |  |

| Requirement ID | LF-SR6 |
| --- | --- |
| Requirement Name | MTLF Weather and Load Forecast Error Analysis |
| Requirement Type | Forecast Accuracy |
| Description: The Load Forecasting function shall calculate on the hour the following: - The MTLF hourly weather data forecast errors at each weather station - The MTLF hourly Load Forecast errors for each Weather Zone and the ERCOT system |  |

| Requirement ID | LF-SR7 |
| --- | --- |
| Requirement Name | LTLF Error Analysis |
| Requirement Type | Forecast Accuracy |
| Description: The Load Forecasting function shall perform the following periodically and/or on demand: - Calculate the LTLF daily minimum and maximum forecast errors for each Weather Zone and the ERCOT system - Issue an alarm message if the forecast errors exceed a pre-set threshold value configurable by an ERCOT Analysts. |  |

| Requirement ID | LF-SR8 |
| --- | --- |
| Requirement Name | Error Threshold Configuration |
| Requirement Type | Forecast Accuracy |
| Description: The Load Forecasting function shall provide the ERCOT Operator the capability to configure percentage threshold values for the following: - The MTLF weather data forecast errors - The MTLF errors - The LTLF daily minimum and maximum forecast errors for each Weather Zone and the ERCOT system |  |

| Requirement ID | LF-SR9 |
| --- | --- |
| Requirement Name | MTLF Error Threshold Analysis |
| Requirement Type | Forecast Accuracy |
| Description: The Load Forecasting function shall compare each hour: - The MTLF weather data forecast errors with the pre-set percentage threshold value(s) and - the MTLF errors with the pre-set percentage threshold value(s) |  |

| Requirement ID | LF-SR10 |
| --- | --- |
| Requirement Name | MTLF Threshold Alarm |
| Requirement Type | Forecast Accuracy |
| Description: The Load Forecasting function shall issue an alarm if: - the MTLF weather data forecast errors exceed a pre-set percentage threshold value and - the MTLF errors for each Weather Zone and ERCOT exceed a pre-set percentage threshold value |  |

| Requirement ID | LF-SR11 |
| --- | --- |
| Requirement Name | LTLF Accuracy |
| Requirement Type | Performance |
| Description: The LTLF daily maximum and minimum Load Forecasts for each Weather Zone shall meet the following Load Forecast error criteria: - For the first 30 days the Load Forecast error shall not be greater than 2% for 95% of the time - For the remainder of the forecasting period, the Load Forecast error shall not be greater than 5% for 95% of the days between 31 and 365. The forecast error calculated shall be defined as the average of the absolute value of the difference between actual values and forecasted values divided by the actual value, for the forecasting period. |  |

| Requirement ID | LF-SR12 |
| --- | --- |
| Requirement Name | Calculate Load Growth Rate |
| Requirement Type | Usability |
| Description: The Load Forecasting function shall support the capability to calculate the load growth rate to be used as input for future Load Forecasting. |  |

| Requirement ID | LF-SR13 |
| --- | --- |
| Requirement Name | Customization to provide multiple models |
| Requirement Type | Forecast Accuracy |
| Description: Customization to suit ERCOT REQUIREMENTS - Provide the ability to load input data from online and offline load forecast models. - Provide the ability to designate one forecast model as Active and all others as Alternates - Provide the ability to store load forecast data from all load forecast models and third party vendor forecast data - Provide a screen which simultaneously displays the forecast from each forecast model. - Provide a screen that displays corresponding weather forecast information for each of the load forecasts. - Provide the ability to select which forecast model will be active for each of the following forecast intervals. - The (7day) forecast period - The current day - Each load zone Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. The market will only receive one load forecast for each item in SR13 No.6 above. |  |

| Requirement ID | LF-SR14 |
| --- | --- |
| Requirement Name | LF Resonability Limits |
| Requirement Type | Data validation |
| Description: The Load Forecasting function shall create and enforce reasonability limits as follows: - Enhance Load Forecast to support automatic setup of reasonability limits during the model study process. - Modification should be made to model processing & validation to scan the processed input data stream and build reasonability (bounds) limits. - Analyst shall have the ability to manually adjust the reasonability limits. - The modeling parameter displays will be modified to accommodate the new values. - Provide a display that allows an operations engineer to view alarms when data is “out of bound”. Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. |  |

| Requirement ID | LF-SR15 |
| --- | --- |
| Requirement Name | LF Rate of Change Detection |
| Requirement Type | alarming |
| Description: The Load Forecasting function shall create and use rate of change limits for alarming as follows. - Add Rate-of Change (ROC) fields in the database. They should be added for weather vairables (WVD) and loads (LD) - The display should have a selection button for auto-scanning for ROC values if needed. There should be appropriate alerts for operator. - Provide a display that allows the Operations engineer to view alarms when “ROC” is violated. Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. |  |

| Requirement ID | LF-SR16 |
| --- | --- |
| Requirement Name | LF Weather verification functionality |
| Requirement Type | Data validation |
| Description: Weather input data shall be verified against reasonability limits. Each check will allow an optional substitution of the tested value. The original raw value will be retained for display. This capability should be supported for all input weather variables. Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. |  |

| Requirement ID | LF-SR17 |
| --- | --- |
| Requirement Name | LF periodic Health Check |
| Requirement Type | Health Check |
| Description: The Load Forecasting function shall perform a health check every N hours (Analyst defined, default = 24). If the health criteria are violated then an audable alarm requesting operator should be issued. Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. |  |

| Requirement ID | LF-SR18 |
| --- | --- |
| Requirement Name | LF Operations Monitoring |
| Requirement Type | archiving |
| Description: The Load Forecasting function shall provide a set of data to the archive which includes all input weather data utilized by the Load forecasting function. Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. |  |

| Requirement ID | LF-SR19 |
| --- | --- |
| Requirement Name | Input Data validation |
| Requirement Type | Data validation |
| Description: The Load Forecasting function shall perform an automated method of excluding abnormally behaved days from the MRLF regression model update to reduce the amount of analysis support LF requires and to make LF more robust. Each time this function is performed it will scan all dates in recent history. An Operations analyst will have the option to override the software decision and force processing for either model update or statistics processing. Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. |  |

| Requirement ID | LF-SR20 |
| --- | --- |
| Requirement Name | LF forecast comparison and selection |
| Requirement Type | Operator selection |
| Description: The Load Forecasting function shall receive a vendor service provided load forecast as well as generating its own. The Load forecasting function shall provide views of both its own forecasts, and the service provided forecasts. The Load Forecasting function shall allow the operator to select which forecast shall be the active forecast. Only this “active” forecast shall be posted to MIS and used by other applications. Note – the above functionality will exist in the zonal EMS system and may be ported to the nodal Load Forecast. |  |

# Protocol Coverage

| Protocol Sub-Section # (To the lowest level of granularity as possible) | Description | Coverage by Requirements (Full/Partial) | Coverage by Requirements |
| --- | --- | --- | --- |
| 3.2.2 (1) | Long Term Demand Forecasts | Partial | LF-FR 5, 8 |
| 3.12 (a) | Load Forecasting | Full | LF-FR 3, 6, 8 |
| 3.12 (b) | Load Forecasting | Full | LF-FR 4, 8 |
| 3.12.1 (1) | Mid-Term Load Forecast | Partial | LF-FR 3, 7 |
| 3.12.1 (2) (a) | Mid-Term Load Forecast | Full | LF-FR 1, 2, 3 |
| 3.12.1 (2) (b) | Mid-Term Load Forecast | Full | LF-FR 7 |
| 3.12.1 (3) | Mid-Term Load Forecast | Full | LF-FR 6 |
| 3.12.2 (1) | Long Term Load Forecast | Partial | LF-FR 4, 7 |
| 3.12.2 (2) | Long Term Load Forecast | Full | LF-FR 6 |
| 4.2.3 (d) | Posting Forecasted ERCOT System Conditions | Full | LF-FR 9 |
| 6.3.2 (3) (b) | Activities for Real-Time Operations | Partial | LF-FR 6 |
| 6.3.2 (2) (a) (ii) | Activities for Real-Time Operations | Partial | LF-FR 1, 8 |
| 8.2 (2) (c) (i) | ERCOT Performance Monitoring and Compliance | Partial | LF-FR 10 |
| 17.3.5 | Data Retention | Partial | LF-FR 10, 12 |