## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For Data Models, Version 0.91
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | Brazos Electric (T.Kroskey) | 8 | 2.1.2 |  |  | The data models and network diagrams are made available by NMMS. The data includes the NOMCRs that are validated, tested, and approved. These data models and network diagrams are received by EMS data model functions, and converted to EMS compatible format. Additionally any EMS software application configuration data is integrated into these data models and kept ready for loading. Upon request from a designated user these data models are uploaded into real-time applications. In general the upload takes place to reflect the changes to ERCOT System in the EMS applications. However, for efficiency purposes these changes are kept to a maximum of one upload per day. (Will ERCOT be able to upload another corrected model in a emergency situation if something went wrong?) The study application user will upload the models to reflect the changes to ERCOT System for the target study time. | Clarification Provided* | J. Dondeti | Requirements will be updated to clarify that ERCOT shall be able to correct the model in an emergency situation. Our discussions with vendors includes this topic, but we agree that the requriemetns need to be clear.
2 | NRG (D.S.Mai) | 8 | 2.1.2 |  |  | The data models and network diagrams are made available by NMMS. The data includes the NOMCRs that are validated, tested, and approved. These data models and network diagrams are received by EMS data model functions, and converted to EMS compatible format. Additionally any EMS software application configuration data is integrated into these data models and kept ready for loading. Upon request from a designated user these data models are uploaded into real-time applications. In general the upload takes place to reflect the changes to ERCOT System in the EMS applications. However, for efficiency purposes these changes are kept to a maximum of one upload per day. The study application user will upload the models to reflect the changes to ERCOT System for the target study time. General comments: 1 Does the “Data Model Upload” replace the database in production, especially for the real-time (non study mode) functions, e.g. LFC, SE etc.? 2. Does the “Data Model Upload” map ICCP/SCADA points automatically to the updated model? 3. Is there any notification issued to the Market Participants after an upload? 4. Is there any process to validate telemetry / model with MPs after an upload? | Clarification Provided* | J. Dondeti | 1. Yes the upload process will replace the database in production for real-time applications, and provide databases representing future for the study applications 2. The ICCP locations/model and mapping to SCADA is managed in NMMS. The SCADA points are mapped to model either in the validation program or in NMMS depending on the nature of the data. 3. We will update the requirments to reflect the need to notify to the market 4. EMS data upload will only consider NOMCRs that are already tested and verified. The process of validating with MPs ought to be done before the data gets into EMS. Provide further clarification. Section 2 is modified to further clarify.
3 | CNP (V.Emesih) | 9 | 2.2 |  |  | The following assumptions are made in writing these requirements: ... B. The Network Operations Models that provide the physical network definition of the future representations of the ERCOT System are available to EMS, from NMMS in CIM format. (I always assumed EMS has the “current”, as-built, operational model that is updated daily. This model is used for both real-time and day-ahead market operation. NMMS manages the complexities of keeping time-based future models used for other “forward looking” applications (CRR, Trx. Planning tools used for outage studies.) | Clarification Provided | J. Dondeti | EMS applications use current as well as future representations of the ERCOT System. Real-time applications use the current Network Operations Model. Outage sutdies use the future representation of the ERCOT System.
4 | CNP (V.Emesih) | 9 | 2.2 |  |  | The following assumptions are made in writing these requirements: ... C. All (??) the supporting data models required by EMS, listed in these requirements, are available from NMMS in CIM format. (This maybe and invalid assumption) | Clarification Provided | J. Dondeti | Currently CIM is being extended for ERCOT purposes to include the data required in EMS. We are considering to include SPS/RAP also in CIM.
5 | CNP (V.Emesih) | 9 | 2.2 |  |  | The following assumptions are made in writing these requirements: … D. All the data models received by EMS are (reasonably tested)already tested and validated. | Rejected | J. Dondeti
6 | Reliant (F.Trefny) | 10 | 3 | DM-FR1 |  | Description: Is data from the Registration system also used in EMS?? | Pending | J. Dondeti | Registration data required in EMS is obtained through NMMS. For example Resource information for LFC. Discuss with Integration, and further clarify. Add to IDA Punch List.
7 | CNP (V.Emesih) | 11 | 3 | DM-FR1 |  | B. EMS shall use the Network Operations Model as follows, to accommodate the NOMCR process: … ii. All study applications in EMS shall use the Network Operations Model that provides the definition of the physical network of the ERCOT System for the target time of study. (What is the allowable target time period 1hr, 1 day, 1 month, 1 year, 5years) This may create undue complexity within operational planning type applications –outage studies etc. | Clarification Provided* | J. Dondeti | Target time of study for network analysis applications could be as small as 1 hr, for example to evaluate outages. The models may change once daily if needed. For studies beyond 30 days we are considering using weekly models instead of daily models. Reference to NOMCRs need to removed. Distinguish between real-time and study models, and test and online system. Exepct to see data model changing 3 or 4 time. All references to NOMCRs are removed. Clarification provided in section 2.
8 | Brazos Electric (T.Kroskey) | 13 | 4 | DM-SR1 |  | A. EMS data model functions shall maintain EMS software application configuration data for the following applications in a format that can be easily updated via GUI by an authorized Applications Data Adminstrator, and can be imported and exported in bulk: ... | Accepted | J. Dondeti | We will update the requirements to clarify. We may come up with common terminology or definition for application data adminstrator and use it across all the documentation. Provide clarification and accept.

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.