## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For Forced Outage Detection, Version 0.91
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  |  | All Forced Outage Detection requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents. In addition all requirements are traceable to the Functional Diagram that describes the Forced Outage Detection. | Accepted | J. Dondeti | The supplimental requrements are not mapped to the Functional Diagram. So, we agree.
2 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | The purpose of Forced Outage Detection (FOD) process is to detect status changes for Resources, transmission lines, transformers, and Loads based on associated breaker and switch status changes, identify forced outages of Transmission Facilities, and produce alarms, in real- time at the same frequency as that of SCADA telemetry processing. In general the SCADA system processes breaker and switch status changes and produces alarms. However, individual breaker or switch alarms do not immediately provide information about the corresponding status change in Transmission Facilities statues. … | Accepted | J. Dondeti | Comment accepted as is.
3 | Brazos Electric (T.Kroskey) | 8 | 2 |  |  | This integration will ensure that therey are no duplicate alarms issued from SCADA and FOD. | Accepted | J. Dondeti | Comment accepted as is.
4 | Brazos Electric (T.Kroskey) | 9 | 3 |  |  | This section describes the functional requirements for the Forced Outage Detection process. | Accepted | J. Dondeti | Comment accepted as is.
5 | Brazos Electric (T.Kroskey) | 9 | 3.1 |  |  | The inputs to FOD are from various Systems and Sub-systems as showndescribed in the functional diagram in Section 2. The proposed system for FOD is expected to use this input data as described in these functional requirements. … | Accepted | J. Dondeti | Comment accepted as is.
6 | Brazos Electric (T.Kroskey) | 9 | 3.1 | FOD-FR1 |  | A. The Forced Outage Detection shall use the following data: i. Breaker and switch statuses data from SCADA | Accepted | J. Dondeti | Comment accepted as is.
7 | Brazos Electric (T.Kroskey) | 9 | 3.2 | FOD-FR2 |  | A. Forced Outage Detection shall translate breaker and switch statuses data in to corresponding status for the following Tranmission Elements statuses: | Accepted | J. Dondeti | Comment accepted as is.
8 | Brazos Electric (T.Kroskey) | 9 | 3.2 | FOD-FR2 |  | … classified in to the following … | Accepted | J. Dondeti | Comment accepted as is.
9 | Brazos Electric (T.Kroskey) | 9 | 3.1 | FOD-FR1 |  | B. FOD shall use the status data only if the SCADA data quality code is good. | Accepted | J. Dondeti | Comment accepted as is.
10 | Brazos Electric (T.Kroskey) | 10 | 3.2 | FOD-FR3 |  | C. FOD shall be able to associate the breaker and switches status changes defined in the Outage Scheduler to Transmission Facilities, in the process of detecting forced outages. | Accepted | J. Dondeti | Comment accepted as is.
11 | NRG (D.S.Mai) | 10 | 3.2 | FOD-FR4 |  | A. After a configurable time (T3; initially set to 30 minutes) into the Operating Hour, FOD shall compare planned resource status from MMS, to the FOD calculated resource status. If the planned resource status is ON, the next hour planned status is also ON, and the Resource status calculated by FOD is OFF, then FOD shall notify the ERCOT operator of an unexpected deviation from the operating plan. Note: the unit may be ramping down to off-line status as planned in the next hour COP. | Accepted | A. Boecker | Comment accepted as is.
12 | Brazos Electric (T.Kroskey) | 11 | 3.2 | FOD-FR5 |  | A. FOD shall detect any deviations between athe telemetered Resource statuses and athe FOD calculated Resource statuses. | Accepted | A. Boecker | Comment accepted as is.
13 | Brazos Electric (T.Kroskey) | 11 | 3.3 |  |  | The primary output to the ERCOT operator from FOD will be through the Alarming sub-system. | Accepted | A. Boecker | Comment accepted as is.
14 | Brazos Electric (T.Kroskey) | 11 | 3.3 | FOD-FR6 |  | A. FOD shall display all Planned Outages and Forced Outages for the ERCOT operator to review … E. The ERCOT operator shall also be able to inhibit an outage on the FOD display after reviewing data and where necessary coordinating with the appropriate TSP or QSE. | Accepted | A. Boecker | Comment accepted as is.
15 | Brazos Electric (T.Kroskey) | 12 | 3.3 | FOD-FR6 |  | F. The inhibited (blocked) outages shall be identified with unique attributes on the display. | Clarification Provided* | A. Boecker | We will clarify what inhibit means in the requirements document. The idea is for the Operator to check off the outage as inhibited, if Operator determines that it was identified as outage due to inaccurate data or telemetry based on analysis or communicatioin with MPs. Describe the business process and choose appropriate word for inhibited.
16 | Brazos Electric (T.Kroskey) | 12 | 3.3 | FOD-FR7 |  | A. FOD shall generate status change alarms for ERCOT operator, via the Alarm sub-system of the EMS, as follows: … iv. Issue an rReturn to normal alarm with color coding | Accepted | A. Boecker | Comment accepted as is.
17 | Brazos Electric (T.Kroskey) | 12 | 3.3 | FOD-FR7 |  | … documented in Texas Nodal EMS Requirements Specification. | Accepted | A. Boecker | Comment accepted as is.
18 | Brazos Electric (T.Kroskey) | 13 | 3.3 | FOD-FR8 |  | … documented in Texas Nodal EMS Requirements Specification. | Accepted | A. Boecker | Comment accepted as is.
19 | Brazos Electric (T.Kroskey) | 13 | 3.3 | FOD-FR9 |  | A. FOD shall generate an alarm for the ERCOT operator, via the Alarm sub-system of the EMS, for each resource status deviation between the telemetered and FOD calculated status. | Accepted | A. Boecker | Comment accepted as is.
20 | Brazos Electric (T.Kroskey) | 13 | 3.3 | FOD-FR9 |  | documented in Texas Nodal EMS Requirements Specification. | Accepted | A. Boecker | Comment accepted as is.
21 | Brazos Electric (T.Kroskey) | 13 | 3.4 | FOD-FR10 |  | B. The daily archived results record shall include the following fields: actual outage start, return to service, planned start time, planned end time, forced outage type, whether the outage was inhibited at any time in the day, and a field to denote if the Outage Scheduler has a matching entry. | Accepted | A. Boecker | Comment accepted as is.
22 | Brazos Electric (T.Kroskey) | 14 | 4 | FOD-SR2 |  | ● If FOD fails to finish the processing of one cycle for a configurable amount of time, it shall be aborted and restarted automatically, and alarm shall be generated to inform the ERCOT operator. | Accepted | A. Boecker | Comment accepted as is.
23 | Brazos Electric (T.Kroskey) | 14 | 4 | FOD-SR4 |  | ERCOT shall have review and approval right for all FOD displays. | Accepted | A. Boecker | Comment accepted as is.

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.