## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For State Estimator, Version 0.91
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | No., Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment | Revised Reason / Comment
1 | Brazos Electric (T.Kroskey) | 7 | 1.4 |  | 1 p. 7 1.4 Brazos Electric (T.Kroskey) | All State Estimator requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, Telemetry Standards approved by TAC on July 6, 2006, State Estimator standards approved by TAC on July 6, 2006, ERCOT Operating Guides, and PUCT documents. In addition all requirements are traceable to the Process Map that describes the State Estimator. | Accepted | Nodal EMS NA Team
2 | Brazos Electric (T.Kroskey) | 8 | 2 |  | 2 p. 8 2 Brazos Electric (T.Kroskey) | (inserted "-" between "real" and "time") The primary purpose of State Estimator is to provide, in real -time, estimates of voltage magnitudes and angles of all energized Topological Buses in the ERCOT network model, … Three separate instances of SE will be supported: ● Real-Time, the version that runs under the real- time sequence. ● Study mode version of State Estimator (protocol section 3.10.7.4(6)), with special tools designed for troubleshooting and tuning purposes, and that can be used independently of any other ERCOT processes that are dependant on the real- time State Estimator. | Accepted | Nodal EMS NA Team
3 | Brazos Electric (T.Kroskey) | 8 | 2 |  | 3 p. 8 2 Brazos Electric (T.Kroskey) | ● Test and simulation facility State Estimator (protocol section 3.10.4), to allow potential model data sets to get tested before the model changes are loaded into the real-time Eenvironment. | Accepted | Nodal EMS NA Team
4 | CNP | 8 | 2 |  | 4 p. 8 2 CNP | The primary purpose of State Estimator is to provide, in real time, estimates of voltage magnitudes and angles of all energized Topological Buses in the ERCOT network model, The estimator also provides estimates of [Change to “computes”]all Electrical Bus loads and branch flows, whether they are operationally metered or not. These state estimates are a starting point for the evaluation and enforcement of ERCOT System security and for the improvement in the economic operation. Specifically, SE provides a starting point for the Network Security Analysis (NSA), Voltage Support Services, Security Constrained Economic Dispatch (SCED), and market applications like HRUC, DRUC, DAM, and Settlements. | Accepted | Nodal EMS NA Team
5 | Reliant (F.Trefny) | 8 | 2 |  | 5 p. 8 2 Reliant (F.Trefny) | The primary purpose of State Estimator is to provide, in real time, estimates of voltage magnitudes and angles of all energized Topological Buses in the ERCOT network model, The estimator also provides estimates of all Electrical Bus loads and branch flows, whether they are operationally metered or not. These state estimates are a starting point for the evaluation and enforcement of ERCOT System security and for the improvement in the economic operation. Specifically, SE provides a starting point for the Network Security Analysis (NSA), Voltage Support Services, Security Constrained Economic Dispatch (SCED), and market applications like HRUC, DRUC, DAM, and Settlements. Does SE also provide alarms for detected limit violations on otherwise telemetered points? Are alarms suppressed if SCADA already alarmed an out of limit condition? | Clarification Provided* | Nodal EMS NA Team | SE does provide alarms for limit violations. These can be either suppressed or assigned a different category than the SCADA alarms. There is no feature to suppress limit alarms if SCADA already alarmed on the same condition. Update requirements to reflect that State Estimator functionality includes alarming. Consult Operation management to clarify if this is okay. | The alarm requirement is reflected in a new text within FR0, Items x & xi x. Issue alarms if flow and/or voltage violations occur. Alarm and event processing for state estimated data shall be the same as for real-time data, in addition to any alarming capability specific to the State Estimator application; however, alarms for state estimated data shall be filtered. That is, the same alarm occurring on sequential executions of the state estimator shall only be alarmed on the first occurrence. Alarms related to state estimated data shall be distinguished on alarm summaries with a different attribute. It shall be possible to inhibit alarming for state estimated data, both globally and on a per-point basis, and it shall be possible to filter out state estimator alarms on a console’s alarm display. xi. A single summary alarm is issued to indicate that violations have been detected by the State Estimator. This alarm should be issued only when new equipment violations have been detected.
6 | CNP | 8 | 2 |  | 6 p. 8 2 CNP | Three separate instances of SE will be supported: ● Real-Time, the version that runs under the real time sequence. ● Study mode version of State Estimator (protocol section 3.10.7.4(6)), with special tools designed for troubleshooting and tuning purposes, and that can be used independently of any other ERCOT processes that are dependant on the real time State Estimator. ● Test and simulation facility State Estimator (protocol section 3.10.4), to allow potential model data sets to get tested before the model changes are loaded into the real-time Environment. [Is this one same as the real-time version but on a test system?] | Clarification Provided | Nodal EMS NA Team | Yes | no change in text
7 | CNP | 9 | 2.1 |  | 7 p. 9 2.1 CNP | Figure 2 [I-7 and P-2 are for test SE and should be listed separately from this digram.]- 1: State Estimator and network security analysis processes | Accepted | Nodal EMS NA Team | The diagram will be updated to distinguish between Real-Time SE and Study mode SE. | Diagram modified as follows: dashed lines used between I-7 & P-2 & P-2 & P-1.
8 | Reliant (F.Trefny) | 9 | 2.1 |  | 8 p. 9 2.1 Reliant (F.Trefny) | The main components of State Estimator are (a) Network Topology Builder Topology Processor, (b) Observability Analysis, (c) Bus Load Forecast Scheduling, (d) State Estimation of State Variables and Computation of Flows, (e) Bad Data Detection., and (f) Load Parameter Adaptation. Please use Nodal Protocol terms when meaning items addressed in the protocols. | Accepted | Nodal EMS NA Team
9 | Brazos Electric (T.Kroskey) | 9 | 2.1 |  | 9 p. 9 2.1 Brazos Electric (T.Kroskey) | The main components of State Estimator are (a) Network Topology Processor, (b) Observability Analysis, (c) Bus Load Scheduling, (d) Estimation of State Variables and Computation of Flows, (e) Bad Data Detection., and (f) Load Parameter Adaptation. | Accepted | Nodal EMS NA Team
10 | CNP | 9 | 2.1 |  | 10 p. 9 2.1 CNP | The main components of State Estimator are (a) Topology Processor, (b) Observability Analysis, (c) Bus Load Scheduling, (d) Estimation of State Variables and Computation of Flows, (e) Bad Data Detection. [ “.” Needs to be deleted.], and (f) Load Parameter Adaptation. | Accepted | Nodal EMS NA Team
11 | Reliant (F.Trefny) | 9 | 2.1.1 |  | 11 p. 9 2.1.1 Reliant (F.Trefny) | 2.1.1 Network Topology Builder Processor The Network Topology ProcessorBuilder is used in both real-time and study mode. Its main functions are as follows: | Accepted | Nodal EMS NA Team
12 | CNP | 9 | 2.1.1 |  | 12 p. 9 2.1.1 CNP | The Network Topology Processor is used in both real-time and study modes. Its main functions are as follows: | Accepted | Nodal EMS NA Team
13 | Brazos Electric (T.Kroskey) | 9 | 2.1.1 |  | 13 p. 9 2.1.1 Brazos Electric (T.Kroskey) | The Network Topology Processor is used in both real-time and study mode. Its main functions are as follows: ● This function eExamines the new status of switching devices, and it groups all CIM connectivity nodes (including bus bars and conducting equipment terminals) connected through closed switching devices into Topological Buses. A distinction should be made between this notion of a topological electrical bus and a related but distinct notion of Electrical Buses. ... ● It cChecks for changes in the connectivity of branches to Topological Buses and based on that it builds a Topological Bus level connectivity information table for internal use by the SE... ● Determines and stores The energized or de-energized status of the Electrical Buses shall be stored ● This function shall also sStore, and on user demand display, a mapping between Topological Buses and Electrical Buses. | Accepted | Nodal EMS NA Team
14 | CNP | 10 | 2.1.2 |  | 14 p. 10 2.1.2 CNP | (deleted ")" after "Analysis") 2.1.2 Observability Analysis) | Accepted | Nodal EMS NA Team
15 | Brazos Electric (T.Kroskey) | 10 | 2.1.2 |  | 15 p. 10 2.1.2 Brazos Electric (T.Kroskey) | 2.1.2 Observability Analysis) | Accepted | Nodal EMS NA Team
16 | Brazos Electric (T.Kroskey) | 10 | 2.1.2 |  | 16 p. 10 2.1.2 Brazos Electric (T.Kroskey) | (deleted spaces before "For") For parts of the system with insufficient measurements, i.e. those determined to be unobservable … | Accepted | Nodal EMS NA Team
17 | Reliant (F.Trefny) | 10 | 2.1.3 |  | 17 p. 10 2.1.3 Reliant (F.Trefny) | State Estimator uses the model of the electrical network as assembled by the Topology nodal terms here too. Processor(Fig. 2-2 P-1), an error model of measurements(Fig. 2-2 P-3), along with bus load forecasts, and measurements of line flows, voltages, voltage angles, generation and loads -- to provide a mathematically consistent estimate of the whole state of the ERCOT system. | Accepted | Nodal EMS NA Team | We will use the Protocol terminology as follows: State Estimator uses the model of the electrical network as assembled by Network Topology Builder
18 | CNP | 10 | 2.1.3 |  | 18 p. 10 2.1.3 CNP | State Estimator uses the model of the electrical network as assembled by the Topology Processor(Fig. 2-2 P-1), an error model of measurements(Fig. 2-2 P-3) [Where is Fig. 2-2?], along with bus load forecasts, and measurements of line flows, voltages, voltage angles, generation and loads -- to provide a mathematically consistent estimate of the whole state of the ERCOT system. | Clarification Provided* | Nodal EMS NA Team | We will correct as follows - Change reference from "Fig 2-2" to "Fig 2-1" | New text: "State Estimator uses the model of the electrical network as assembled by the Network Topology Builder (Fig. 2-1 P-1), an error model of measurements(Fig. 2-1 P-3), along with bus load forecasts, and measurements of line flows, voltages, voltage angles, generation and loads -- to provide a mathematically consistent estimate of the whole state of the ERCOT system."
19 | Brazos Electric (T.Kroskey) | 10 | 2.1.3 |  | 19 p. 10 2.1.3 Brazos Electric (T.Kroskey) | State Estimator uses the model of the electrical network as assembled by the Topology Processor(Fig. 2-2 P-1), an error model of measurements(Fig. 2-2 P-3), along with bus load forecasts, and measurements of line flows, voltages, voltage angles, generation and loads -- to provide a mathematically consistent estimate of the whole state of the ERCOT system. In arriving at the solution, all the measurements, whether acquired from actual meterstelemetry, or pseudo-measurements such as bus load forecasts, are treated simultaneously, with individual contributions to the solution weighted by the confidence in the measurement accuracy. For example, measurements with high accuracy are weighted higher than pseudo-measurements whose accuracy is lower. | Accepted | Nodal EMS NA Team
20 | CNP | 10 | 2.1.3 |  | 20 p. 10 2.1.3 CNP | Based on the estimate of the state and the network topology and parameters, all branch flows and bus injections can be computed. In this way, it is possible to track overloads even on branches without direct measurements, as well as assess bus load injections at all buses whether there are direct measurements there or not. The accuracy of load estimates will be related to the availability of accurate direct measurements, or other flow measurements around the loads: more direct measurements usually means better estimation accuracy. | Accepted | Nodal EMS NA Team
21 | Brazos Electric (T.Kroskey) | 10 | 2.1.4 |  | 21 p. 10 2.1.4 Brazos Electric (T.Kroskey) | (deleted "," after "runs.") The aim at this stage is to identify measurements that have changed beyond an expected band between two successive SE runs., | Accepted | Nodal EMS NA Team
22 | Brazos Electric (T.Kroskey) | 11 | 2.1.5 |  | 22 p. 11 2.1.5 Brazos Electric (T.Kroskey) | (editing of spacing and periods) … Ratings .(SCADA) … measurements include … … and disconnects… … values. . This … | Accepted | Nodal EMS NA Team
23 | Brazos Electric (T.Kroskey) | 11 | 2.1.5 |  | 23 p. 11 2.1.5 Brazos Electric (T.Kroskey) | The Load Models describe how MW system load is split into individual bus MW and MVARr loads, using load distribution factors and power factor lists. | Accepted | Nodal EMS NA Team
24 | Reliant (F.Trefny) | 11 | 2.2.1 | Table 2-1 | 24 p. 11 2.2.1 Table 2-1 Reliant (F.Trefny) |  | Accepted | Nodal EMS NA Team
25 | Reliant (F.Trefny) | 12 | 2.2.1 | Table 2-1 | 25 p. 12 2.2.1 Table 2-1 Reliant (F.Trefny) |  | Accepted | Nodal EMS NA Team
26 | Brazos Electric (T.Kroskey) | 11 | 2.2.1 | Table 2-1 | 26 p. 11 2.2.1 Table 2-1 Brazos Electric (T.Kroskey) | (deleted space before "connectivity") b) Network connectivity | Accepted | Nodal EMS NA Team
27 | Brazos Electric (T.Kroskey) | 11 | 2.2.1 | Table 2-1 | 27 p. 11 2.2.1 Table 2-1 Brazos Electric (T.Kroskey) | 2) Bus load forecasts with load schedules in MW/MVARvar ... c) Transmission Line Flows (MW, MVARvar) d) Generation (MW, MVARvar) e) Loads (MW, MVARvar) f) Transformer Taps (position) g) Condition codes for all telemetered values h) Resource High/Low sustained limit i) Phasor Measurements (future) j) Transformer Flows (MWw, MVARvar) k) DC Ties (MWw, MVARvar) l) Statcom measurements (MVARvar) m) Shunt reactor and Capacitor flows (MVARvar) n) Breaker measurements (MWw, MVARvar) | Accepted | Nodal EMS NA Team
28 | Brazos Electric (T.Kroskey) | 13 | 2.2.2 | Table 2-2 | 28 p. 13 2.2.2 Table 2-2 Brazos Electric (T.Kroskey) | 1) Basecase solution with all breaker/switch statuses, transmission line flows (MW, MVARvar), generation (MW, MVAvar), loads (MW, MVARvar), bus voltages (KV), transformer tap positions. ... Basecase solution with all breaker/switch statuses, transmission line flows (MW, MVAvar), generation (MW, MVARvar), loads (MW, MVARvar), bus voltages (KV), transformer tap positions. | Accepted | Nodal EMS NA Team
29 | Reliant (F.Trefny) | 13 | 2.2.2 | Table 2-2 | 29 p. 13 2.2.2 Table 2-2 Reliant (F.Trefny) |  | Clarification Provided* | Nodal EMS NA Team | We agree that settlements need 15 min average load at each bus. We will put this on IDA Punch list to determine the interface requirements and update accordingly. We will do the same for the SCED interface from SE. | The new text: "Settlements Estimated loads at SE solution cycle."
30 | Reliant (F.Trefny) | 14 | 3.1 | SE-FR0 | 30 p. 14 3.1 SE-FR0 Reliant (F.Trefny) | A. The SE application shall provide the following base SE functionality: ... x. Issue alarms if flow and/or voltage violations occur . Provided SCADA has not already alarmed the violation. | Clarification Provided | Nodal EMS NA Team | Network displays have to log and display all security violations, regardless of whether SCADA issues alarms or not. Based on consulting with Operationg management we will add this requirement if needed. | New text for items x & xi in FR0: "x. Issue alarms if flow and/or voltage violations occur. Alarm and event processing for state estimated data shall be the same as for real-time data, in addition to any alarming capability specific to the State Estimator application; however, alarms for state estimated data shall be filtered. That is, the same alarm condition occurring on sequential executions of the state estimator shall only be alarmed on the first occurrence. Alarms related to state estimated data shall be distinguished on alarm summaries with a different attribute. It shall be possible to inhibit alarming for state estimated data, both globally and on a per-point basis, and it shall be possible to filter out state estimator alarms on a console’s alarm display. xi. A single summary alarm is issued to indicate that violations have been detected by the State Estimator. This alarm should be issued only when new equipment violations have been detected."
31 | Brazos Electric (T.Kroskey) | 15 | 3.1 | SE-FR0 | 31 p. 15 3.1 SE-FR0 Brazos Electric (T.Kroskey) | A. The SE application shall provide the following base SE functionality: ... xii. The capability shall be provided to specify lists of items required for monitoring of measurement-estimated value consistency as defined in ERCOT’s telemetry and State Estimator performance standards shall be provided. | Accepted | Nodal EMS NA Team
32 | Reliant (F.Trefny) | 15 | 3.1 | SE-FR0 | 32 p. 15 3.1 SE-FR0 Reliant (F.Trefny) | B. The state estimator shall be capable of handling the following types of measurements: … ii. Circuit breaker flow measurements (real and reactive power) such as a bus sectionalizer circuit breaker. These are measurements are not required in protocol section 3.10. | Accepted | Nodal EMS NA Team | Delete item ii. | Item ii (circuit flow measurements) deleted.
33 | CNP | 15 | 3.1 | SE-FR0 | 33 p. 15 3.1 SE-FR0 CNP | B. The state estimator shall be capable of handling the following types of measurements: ... iii. Loads (MW, MVArMvar) iv. Generation (MW, MvaVAr) | Accepted | Nodal EMS NA Team
34 | Brazos Electric (T.Kroskey) | 15 | 3.1 | SE-FR0 | 34 p. 15 3.1 SE-FR0 Brazos Electric (T.Kroskey) | B. The state estimator shall be capable of handling the following types of measurements: ... iii. Loads (MW, MVARr) iv. Generation (MW, MVARr) ... viii. Transformer Flows (MWw, MVARvar) ix. Statcom measurements (MVARvar) x. Shunt reactor and Capacitor flows (MVARvar) xi. Breaker measurements (MWw, MVARvar) | Accepted | Nodal EMS NA Team
35 | Brazos Electric (T.Kroskey) | 16 | 3.2 | SE-FR1 | 35 p. 16 3.2 SE-FR1 Brazos Electric (T.Kroskey) | A. Network Operations Model: State Estimator shall use an updated model, when it is made available by the Network Model Management System (NMMS), to ensure that the ERCOT NMMS operations modelTSP’s control center operational model and ERCOT’s Network Operations Model are consistent. | Accepted | Nodal EMS NA Team
36 | Brazos Electric (T.Kroskey) | 16 | 3.2 | SE-FR1 | 36 p. 16 3.2 SE-FR1 Brazos Electric (T.Kroskey) | C. Transmission Elements: For all the transmission elements the associated operating TSP or QSE name shall be available in the State Estimator for reference, for example: to report a telemetry issue that is contributing to State Estimator inaccuracies to the corresponding TSP. D. Resources: For all the resources the associated QSE name shall be available in the State Estimator for reference, for example: to report a telemetry issue that is contributing to State Estimator inaccuracies to the corresponding QSE. ... F. Telemetry: For each telemetered quantity, the name of the associated TSP or QSE providing the telemetry shall be available in the State Estimator. These names shall be the same references used in the ICCP or SCADA modeling. The entities providing telemetry may be different than the operating TSP or QSE. (Isn’t this the same as C and D combined?) | Clarification Provided | Nodal EMS NA Team | Usually this is true, but the distinction is that entities providing telemetry may be different from the operating entities. Correct "TSP or QSE".
37 | CNP | 18 | 3.2 | SE-FR5 | 37 p. 18 3.2 SE-FR5 CNP | Description: The power system shall include model representation of switched shunts and Flexible Alternating Current Transmission Systems (FACTS) devices such as [FACTS devices need to be added here.] …. | Accepted* | Nodal EMS NA Team | will add: "such as Static Synchronous Compensator, Statcoms, Unified Power Flow Controller, Thyristor Controlled Series Compensators"
38 | Reliant (F.Trefny) | 18 | 3.2 | SE-FR6 | 38 p. 18 3.2 SE-FR6 Reliant (F.Trefny) | SE-FR6: Reactive capability curve override: What is this section trying to accomplish? | Clarification Provided* | Nodal EMS NA Team | This requirement is trying to address the situations where telemetry indicates a generator VAR output in excess of what the capability curve says it can be. In this case, the VAR limit is temporarily increased on the side where excess occurred, to make the capability curve consistent with the data; when the telemetry indicates that the VAR output has returned to within the original capability curve, this curve is re-instated. Add business process to verify with State Estimator estimated values, and by communicating with QSEs when overriding the limit. | New text: "Description: The purpose of this function is to facilitate a correction of the generation reactive capability curve when the state estimated output of a generating resource exceeds its reactive capability curve. The system shall alarm whenever the estimated MVAR exceed the value of the reactive capability curve. ERCOT will define a business process that is to be initiated in such a situation for the purpose of verifying with the relevant QSE that the estimated MVAR and the reactive capability curve are accurate. In the case that the reactive capability curve in use by ERCOT is found to be inaccurate, QSE will be responsible for making necessary changes."
39 | Brazos Electric (T.Kroskey) | 18 | 3.2 | SE-FR6 | 39 p. 18 3.2 SE-FR6 Brazos Electric (T.Kroskey) | Description: tThe purpose… … generator’s MVARr or its estimate … … the positive MVARr portion … | Accepted | Nodal EMS NA Team
40 | CNP | 18 | 3.2 | SE-FR6 | 40 p. 18 3.2 SE-FR6 CNP | … generator’s MvaVAr or its estimate … … the positive MVAr Mvar portion … | Accepted | Nodal EMS NA Team
41 | Reliant (F.Trefny) | 19 | 3.2 | SE-FR8 | 41 p. 19 3.2 SE-FR8 Reliant (F.Trefny) | Description: The State Estimator shall receive the condition codes from SCADA to indicate telemetered data quality, e.g. whether the data has been measured within the scan rate requirement, a possible loss of updates, and loss of telemetry link. These conditionquality codes may be identified either in the TSP or QSE system or identified in the ERCOT system as defined by the protocols. State Estimator shall support the conditionquality codes for all the above scenarios, and shall display them along with other SE data, to the operator. Measurements with bad conditionquality codes shall be considered in State Estimator at a lower confidence level. The confidence shall continue to decrease over time at a configurable rate. | Accepted | Nodal EMS NA Team
42 | CNP | 19 | 3.2 | SE-FR8 | 42 p. 19 3.2 SE-FR8 CNP | (deleted space before "data") … display them along with other SE data, to the operator. | Accepted | Nodal EMS NA Team
43 | Reliant (F.Trefny) | 20 | 3.2 | SE-FR10 | 43 p. 20 3.2 SE-FR10 Reliant (F.Trefny) | Description: Split generators shall be available for viewing as two or more independent Generation Resources in the State Estimator solution displays. It shall be possible to identify them as split generators of the corresponding physical generating resource on one line diagrams and tabular outputs. . It shall be possible to receive the total generation facility output as a telemetry input, in addition to receiving all individual split generation resource output telemetry and use this information correctly in the State Estimator solution. Note: ERCOT protocols currently demand that ERCOT models two units where split metering is present. ERCOT staff believes that modeling two units in the State Estimator is a mistake, and will lead to erroneous results. ERCOT is in the process of requesting a protocol change with our participants. This can not be honored. Please find a way to make this work as protocols specify. We have been over this many times before. | Pending | Nodal EMS NA Team | Will add to IDA Punch List. IDA is working on a white paper to model split generators across different software systems.
44 | Brazos Electric (T.Kroskey) | 20 | 3.2 | SE-FR10 | 44 p. 20 3.2 SE-FR10 Brazos Electric (T.Kroskey) | (deleted space and period) … and tabular outputs. . | Accepted | Nodal EMS NA Team
45 | Reliant (F.Trefny) | 21 | 3.4 | SE-FR13 | 45 p. 21 3.4 SE-FR13 Reliant (F.Trefny) | Description: ... 2) When the telemetry of breakers and switches is lost: a) System shall be able to globally do the following according to operator’s choice: i. Use last known state of the device for a configurable amount of time ii. After a configurable amount of time, update the status by taking the default status and replacing it in SCADA with scheduled changes from the Outage Scheduler function and assign appropriate condition code.Should not have any automatic process to change SCADA telemetry. ERCOT should call TSP or QSE and have them Manually Replace and then this is not needed. iii. Accept operator entry b. System shall allow the operator to select an option abovei, ii, or iii. c. System shall keep track of all such instances and revert back to telemetry when telemetry becomes available again. This method could have overrides in the data base forever. Please rethink how this should work. | Clarification Provided* | Nodal EMS NA Team | For item 2, proposing new wording: a) System shall be able to globally do the following : i. Use last known state of the device for a configurable amount of time ii. After a configurable amount of time, the device is added to a display showing the device name, last telemetered status, last valid telemetered update date/time, last manual update date/time, Equipment TSP or QSE, and the ability to change the equipment status. This display can be used by the operator to update the current status. b. If the operator over-rides the suspect status with a manual entry, the operator shall have the option to set a flag that will return the manual entry to the telemetered status if the telemetered status returns to a non-suspect state." Business process shall address identifing if there is a communication issues and correcting the status by manually overriding at the TSP or QSE end. Software capability of over-ride is to aid ERCOT Operator to handle the situations temporarly. | New wording: Description: 1) System shall be able to identify and display probable errors in switch or breaker statuses. ERCOT will develop a business process to resolve or correct such errors via an interaction with the relevant operating entities in a timely manner based on this data. 2) When the telemetry of breakers and switches is lost, the system shall continue to use the last known state of the device until telemetry becomes available again, or manual changes are made by ERCOT operator. ERCOT will develop a business process to review status points that have not been updated in a configurable amount of time, and status points that have been manually entered by ERCOT Operators but not updated for more than a configurable amount of time.
46 | Brazos Electric (T.Kroskey) | 22 | 3.4 | SE-FR16 | 46 p. 22 3.4 SE-FR16 Brazos Electric (T.Kroskey) | (deleted commas after "processor") Description: State Estimator shall make MW and MVAR bus mismatches available as input to the Network Security Analysis processor,, to ensure that its base case power flow (before contingency analysis) will produce the same solution as the SE solution. | Accepted | Nodal EMS NA Team
47 | CNP | 22 | 3.4 | SE-FR16 | 47 p. 22 3.4 SE-FR16 CNP | Description: State Estimator shall make MW and MVAR bus mismatches available as input to the Network Security Analysis processor,, to ensure that its base case power flow (before contingency analysis) will produce the same solution as the SE solution.[ This requirement appears to be propagating a known error in zero-injection bus modeling or SE solution algorithm. Zero injection buses should never have significant mismatches that need to be propagated. If there are issues with modeling zero injection measurements, those should be addressed directly.] | Clarification Provided | Nodal EMS NA Team | Agree with the comment about not wanting to propagate the zero injection errors. However, this requirement refers to a different characteristic of SE, which is that a solved SE, due to errors in measurements can produce results for which a mismatch around a power flow bus becomes non-zero, even in buses that have (physically) non-zero injections. | No changes in text
48 | Reliant (F.Trefny) | 23 | 3.5 | SE-FR18 | 48 p. 23 3.5 SE-FR18 Reliant (F.Trefny) | Description: 1)..State Estimator shall distribute the current system load, based on adapted load schedules, to each load modeled in the system prior to estimating the system state, this is referred to as bBus Lload Fforecast. 2) State Estimator shall use the forecasted load as pseudo load measurements, coupled with the remaining telemetry of bus loads, line flows and voltages, to determine the best estimate of the load on each eElectrical bBus. | Accepted | Nodal EMS NA Team
49 | Brazos Electric (T.Kroskey) | 24 | 3.5 | SE-FR19 | 49 p. 24 3.5 SE-FR19 Brazos Electric (T.Kroskey) | (deleted space before "(" ) … LTLF (Long Term Load Forecast) … … MTLF (Mid Term Load Forecast) … | Accepted | Nodal EMS NA Team
50 | Reliant (F.Trefny) | 24 | 3.5 | SE-FR20 | 50 p. 24 3.5 SE-FR20 Reliant (F.Trefny) | Description: State Estimator shall calculate the following 15-minute average of Loads for other applications and for posting to the MIS: 1) Individual transmission Lload on Electrical Buses 2) Sum of loads on each electrical bus in each Load Zone 3) Sum of all loads Total Load on Electrical Buses in the ERCOT System 4) Loads on theeach Electrical Buses. 5) Individual TSP loads is this the same as 4 above? | Clarification Provided* | Nodal EMS NA Team | We will remove the item 5. Protocol do not require us to post this quantity. | The new wording "Description: State Estimator shall calculate the following 15-minute average of Loads for other applications and for posting to the MIS: 1) Individual Loads 2) Load Zone Loads 3) Total ERCOT System Load 4) Electrical Bus Loads."
51 | Brazos Electric (T.Kroskey) | 24 | 3.5 | SE-FR34 | 51 p. 24 3.5 SE-FR34 Brazos Electric (T.Kroskey) | Description: SE shall have capability of estimating voltage, bus angle and Taps simultaneously. Tap estimation shall be possible for all measurement observable transformers irrespective of their taps are telemetered or not. User shall have capability of enabling or disabling Tap estimation globally. ... | Accepted | Nodal EMS NA Team
52 | Brazos Electric (T.Kroskey) | 24 | 3.5 | SE-FR34 | 52 p. 24 3.5 SE-FR34 Brazos Electric (T.Kroskey) | … minimizing residuals on MWw, MVARvar and Voltage measurements … | Accepted | Nodal EMS NA Team
53 | CNP | 24 | 3.6 | SE-FR21 | 53 p. 24 3.6 SE-FR21 CNP | 3.6 Study Mode Version of the State Estimator This section addresses requirements for the study mode version of the State Estimator. This system is intended for debugging of the production system state-estimator and is NOT the same instance of the system described in protocol section 3. 10.4 paragraph 3. Requirement ID: SE-FR21 Requirement Name: SE – Study and Test Mode SE Execution ... [Study-mode SE and Test SE need to be explained separatedly.] | Accepted* | Nodal EMS NA Team | We propose the following changes: 1. Change the title to: Study and Test mode Versions of State Estimator 2. Group all study mode requirements, then all test mode requirements, followed by common. | Changes made as suggested at left
54 | Brazos Electric (T.Kroskey) | 25 | 3.6 | SE-FR21 | 54 p. 25 3.6 SE-FR21 Brazos Electric (T.Kroskey) | (inserted "-" between "real" and "time"; inserted period at end of three bullets) ... the Real -Time SE, ... ... the real -time State Estimator, ... ... study SE and real -time SE ... ... the real -time State Estimator, ... ... the real -time State Estimator. ... and real -time SE user interface. ... affecting real- time telemetry. ... Stop real -time data updates ... ... using real -time measurements ... | Accepted | Nodal EMS NA Team
55 | Brazos Electric (T.Kroskey) | 29 | 3.8 | SE-FR29 | 55 p. 29 3.8 SE-FR29 Brazos Electric (T.Kroskey) | Description: The adapted bus load distribution factors from State Estimator shall be made available to the following non-EMS applications: ... 2) HRUC; State Estimator estimated load values, and current hour load distribution for the remainingder hours of the current day plus the 24 hours of the next day to perform bus load forecast. | Accepted | Nodal EMS NA Team
56 | Brazos Electric (T.Kroskey) | 31 | 4 | SE-SR1 | 56 p. 31 4 SE-SR1 Brazos Electric (T.Kroskey) | (inserted "-" between "real" and "time") Description: State Estimator in real -time shall complete execution within 10 seconds in tracking mode, and within 1 minute upon cold start. | Accepted | Nodal EMS NA Team

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Accepted* | Comment is accepted with a proposed modification.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.