## TPTF Comments & Responses
Document Name: | [5 empty] | Texas Nodal Energy Management System Requirements Specification For Load Forecasting, Version 0.91
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | No., Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
1 | Power & Gas Consulting (J.Reynolds) |  |  |  | 1 Power & Gas Consulting (J.Reynolds) | 1.. ERCOT currently produces a load forecast by type of Load Profile (Bus High Load Factor, Business Medium Load Factor, Residential Low Winter, etc). -This requirement was not mentioned in these Requirements- is this effort described in some other Requirements Doc? | Clarification Provided | Bill Blevins | The system requirements document is not suggesting a change in capabilities with regard to load forecasting. Load forecasting is generated on a station basis. A station can have a profile applied to it that models the specific load behind the meter. This is done for load forecasting accuracy through tuning and model adaptation. This question is asking if a settlements system process will continue. It is not a part of the EMS functionality.
2 | Brazos Electric (T.Kroskey) | 8 | 2 |  | 2 p. 8 2 Brazos Electric (T.Kroskey) | The Load Forecasting functionsystem is a sub-system of the Energy Management System (EMS). The primary purpose of the Load Forecasting system is to provide forecasted Mid-Term and Long-Term load demand information to various ERCOT systems and business processes. | Accepted | Bill Blevins | Add clarification. Additionally, suggest removing the word "demand" because of redundancy.
3 | NRG (D.S.Mai) | 8 | 2 |  | 3 p. 8 2 NRG (D.S.Mai) | The Mid-Term Load Forecast (MTLF) consists of hourly loads for each Weather Zone and the ERCOT system for the remainder of the current day and the next 8 days note: should it be “next 7 days” instead of 8, according to FR3?. … | Accepted | Bill Blevins | Mid-Term Load Forecast” (MTLF) generates forecasted hourly Load over the next 168 hours for each of the Weather Zones.
4 | Brazos Electric (T.Kroskey) | 8 | 2 |  | 4 p. 8 2 Brazos Electric (T.Kroskey) | ... The Reliability Unit Commitments processes also use the MTLF to commit resources to meet anticipated load. | Accepted | Bill Blevins | Add clarification
5 | NRG (D.S.Mai) | 8 | 2 |  | 5 p. 8 2 NRG (D.S.Mai) | The Long Term Load Forecast (LTLF) consists of the daily minimum and maximum demand for each Weather Zone for the next 365 days and beyond. … | Accepted | Bill Blevins | (LTLF) that provides a daily minimum and maximum forecast for the next 365 days for each of the Weather Zones.
6 | Brazos Electric (T.Kroskey) | 8 | 2 |  | 6 p. 8 2 Brazos Electric (T.Kroskey) | The MTLF and LTLF are also inputs that provide load pattern information to the outage evaluation process of assessing that assesses the various impacts of requested outages to the ERCOT system. | Accepted | Bill Blevins | Add clarification
7 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  | 7 p. 8 2.1 Brazos Electric (T.Kroskey) | This section provides a summary of inputs and outputs to the Load Forecasting function. Table 1 lists all the required input data to the Load Forecasting processfunction. … | Accepted | Bill Blevins | Add clarification
8 | Brazos Electric (T.Kroskey) | 8 | 2.1 |  | 8 p. 8 2.1 Brazos Electric (T.Kroskey) | Table 2 lists all the required output data of the Load Forecasting processfunction. … | Accepted | Bill Blevins | Add clarification
9 | NRG (D.S.Mai) | 8 | 2.1 | Table 1 | 9 p. 8 2.1 Table 1 NRG (D.S.Mai) |  | Accepted | Bill Blevins | Add clarification
10 | NRG (D.S.Mai) | 8 | 2.1 | Table 2 | 10 p. 8 2.1 Table 2 NRG (D.S.Mai) |  | Clarification Provided* | Bill Blevins | Texas Nodal Energy Management System Requirements Specification For Network Security and Stability Analysis provide additional description of the Load forecasting systems input for STNET VSAT and TSAT.
11 | Brazos Electric (T.Kroskey) | 9 | 2.2.1 |  | 11 p. 9 2.2.1 Brazos Electric (T.Kroskey) | 2.2.1. To Be Sub-Process for Mid-Term Load Forecast Sub-Process | Accepted | Bill Blevins | Add clarification
12 | Brazos Electric (T.Kroskey) | 9 | 2.2.1 |  | 12 p. 9 2.2.1 Brazos Electric (T.Kroskey) | Brief Description: ERCOT receives current actual load data from SCADA and weather data from a weather service. Based on the current and historical load and weather data and the hourly weather forecast from weather service, the load forecasting system shall create the MTLF hourly containing forecasted loads for each hour for the remainder of the current day and the next 7 days. | Accepted | Bill Blevins | Delete for clarity.
13 | Brazos Electric (T.Kroskey) | 10 | 2.2.2 |  | 13 p. 10 2.2.2 Brazos Electric (T.Kroskey) | 2.2.2 To Be Sub-Process for Long-Term Load Forecast Sub-Process | Accepted | Bill Blevins | Add clarification
14 | Brazos Electric (T.Kroskey) | 11 | 3.1 | LF-FR1 | 14 p. 11 3.1 LF-FR1 Brazos Electric (T.Kroskey) | Description: The Load Forecasting function shall receive automatically the following data at least once every hour, automatically or on request by an ERCOT operator: | Accepted | Bill Blevins | improve wording
15 | Brazos Electric (T.Kroskey) | 11 | 3.1 | LF-FR2 | 15 p. 11 3.1 LF-FR2 Brazos Electric (T.Kroskey) | Description: The Load Forecasting funtion shall have the capability to support the following: | Accepted | Bill Blevins | Delete for clarity.
16 | ERCOT | 11 | 3.1 | LF-FR2 | 16 p. 11 3.1 LF-FR2 ERCOT | Description: The Load Forecasting function shall … | Accepted | Bill Blevins | typo correction
17 | Brazos Electric (T.Kroskey) | 12 | 3.2 | LF-FR3 | 17 p. 12 3.2 LF-FR3 Brazos Electric (T.Kroskey) | Description: Each hour Tthe Load Forecasting function shall generate each hour a MTLF that consists of hourly MWh loads for the reminder of the current day and the next 7 days for each of the Weather Zones, and the ERCOT system. | Accepted | Bill Blevins | improve wording
18 | Brazos Electric (T.Kroskey) | 12 | 3.2 | LF-FR3 | 18 p. 12 3.2 LF-FR3 Brazos Electric (T.Kroskey) | ... ● Weather forecast for each weather zone for the next 7 days | Accepted | Bill Blevins | typo correction
19 | Brazos Electric (T.Kroskey) | 12 | 3.2 | LF-FR4 | 19 p. 12 3.2 LF-FR4 Brazos Electric (T.Kroskey) | Description: Ecah day Tthe Load Forecasting function shall produce and update once a day a LTLF consisting of a daily minimum and maximum demand forecast for the next 365 days for each Weather Zone and the ERCOT system. | Accepted | Bill Blevins | Improve wording. Additionally correct the spelling of Each.
20 | Brazos Electric (T.Kroskey) | 12 | 3.2 | LF-FR4 | 20 p. 12 3.2 LF-FR4 Brazos Electric (T.Kroskey) | ... ● Model Ttraining based on historic daily minimum and maximum hourly integrated loads by Weather Zone | Accepted | Bill Blevins | Add clarification
21 | Brazos Electric (T.Kroskey) | 16 | 4 | LF-SR1 | 21 p. 16 4 LF-SR1 Brazos Electric (T.Kroskey) | Description: The execution time of the following load forecasting functions shall be completed in five (5) minutes or less: | Accepted | Bill Blevins | Add clarification
22 | NRG (D.S.Mai) | 16 | 4 | LF-SR3 | 22 p. 16 4 LF-SR3 NRG (D.S.Mai) | … greater than 2%.%. | Accepted | Bill Blevins | typo correction
23 | Brazos Electric (T.Kroskey) | 16 | 4 | LF-SR3 | 23 p. 16 4 LF-SR3 Brazos Electric (T.Kroskey) | … greater than 2%.%. | Accepted | Bill Blevins | typo correction
24 | Brazos Electric (T.Kroskey) | 16 | 4 | LF-SR5 | 24 p. 16 4 LF-SR5 Brazos Electric (T.Kroskey) | Description: Based upon the MTLF produced at 0600 dDay-aAhead, the RMS error of (actual load – forecast load) divided by the actual value shall not be greater than 3% for the next day. | Accepted | Bill Blevins | typo correction What is ercots intention if this is not met.
25 | Brazos Electric (T.Kroskey) | 18 | 4 | LF-SR13 | 25 p. 18 4 LF-SR13 Brazos Electric (T.Kroskey) | Description: Customization to suit ERCOT REQUIREMENTS (must define xx) 1. Provide the ability to load input data from 1 to xx load forecast models. 2. Provide the ability to designate one forecast model as Active and all others as Alternates 3. Provide the ability to store load forecast data from all xx load forecast models 4. Provide a screen which simultaneously displays the forecast from each forecast model. 5. Provide a screen that displays corresponding weather forecast information for each of the xx load forecasts. | Clarification Provided* | Bill Blevins | 2 models are used currently. A Standard integrated Load Forecasting EMS system that is integrated with other systems. An offline data server that can be run offline for comparison or manually loaded into the online standard system. Will change the wording to specify the ability to load models from an offline means which will allow the current capability and any future needs as well. Additionally remove the '1 to xx', and 'xx's. these values will be defined in future documents. Make clear intent to integrate with 3rd party vendor forecast. Needs to be clear that as far as the market is concerned there is only one forecast (i.e. at any one time all applications are running off a single forecast)
26 | NRG (D.S.Mai) | 18 | 4 | LF-SR13 | 26 p. 18 4 LF-SR13 NRG (D.S.Mai) | 6. Provide the ability to select which forecast model will be active fore each of the following forecast intervals. | Accepted | Bill Blevins | typo correction
27 | NRG (D.S.Mai) | 19 | 4 | LF-SR14 | 27 p. 19 4 LF-SR14 NRG (D.S.Mai) | Description: The Load Forecasting function shall create and enforce reasonability limitis as follows: | Accepted | Bill Blevins | typo correction
28 | NRG (D.S.Mai) | 19 | 4 | LF-SR15 | 28 p. 19 4 LF-SR15 NRG (D.S.Mai) | Description: The Load Forecasting function shall create and enforce rate of change limits as follows. Note: how does LF “enforce” ROC limits? | Clarification Provided | Bill Blevins | The system will not enforce ROC limits merely notify when they are exceeded. The rate of change limit will be a configurable parameter that provides notice to the analyst when an unreasonable Rate of Change is exceeded. The Nodal Rate of Change function is expected to be used for information when performing load forecasting. It is anticipated that they will help reasonability checks in coordination with weather variables and loads. Make clear that the Rate of Change is used for alarming, not enforcement.
29 | Brazos Electric (T.Kroskey) | 19 | 4 | LF-SR16 | 29 p. 19 4 LF-SR16 Brazos Electric (T.Kroskey) | Description: Weather input data shall be verified against reasonability limits. Each check will allow an optionality substitution of the tested value. | Accepted | Bill Blevins | typo correction
30 | Brazos Electric (T.Kroskey) | 20 | 4 | LF-SR18 | 30 p. 20 4 LF-SR18 Brazos Electric (T.Kroskey) | Description: The Load Forecasting function shall provide a set of data to the archive which includes all input weather data utilized by the Load forecasting functionalgorithium. | Accepted | Bill Blevins | Add clarification
31 | Brazos Electric (T.Kroskey) | 20 | 4 | LF-SR19 | 31 p. 20 4 LF-SR19 Brazos Electric (T.Kroskey) | Description: The Load Forecasting function shall perform an automated method of excluding abnormally behaved days … | Accepted | Bill Blevins | typo correction
32 | Brazos Electric (T.Kroskey) | 20 | 4 | LF-SR19 | 32 p. 20 4 LF-SR19 Brazos Electric (T.Kroskey) | … An Operations analysist will have the option to override the software decision and force processing for either model update or statistics processing. | Accepted | Bill Blevins | Add clarification
[5 empty] | SR 17 | Comment in TPTF not to a written comment - what is our intention if the requirment of SR 17 are not met? |  |  | Use case must be written describing the business process for failure of the health check.

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.