## Slide 1: Update on GATF Activities
Wholesale Market Subcommittee
February 21, 2007
Henry Durrwachter
GATF Vice-Chair

## Slide 2: GATF Recommendations
Load Forecast – No Change
Demand Response - No Change
DC Ties - No Change
“Switchable” Capacity - No Change
Wind Capacity – Change
“Mothballed” Capacity - No Change
Retired Capacity - No Change
Private Network Capacity – No Change
New Generating Capacity - Change

## Slide 3: Wind Capacity Value
Existing Methodology:
  Based on actual historical (i.e., rolling average over 10 years) wind generation performance at peak load hours (HE 1600 to 1800, weekdays only) coupled with an EFOR of 8% (i.e., a confidence band of 92%)
  Capacity value for wind for 2006 CDR (based on data from 2002-2005) was 2.6%
GATF concerned that the application of the EFOR effectively “double-counted” forced outage rates, since use of actual wind generation performance data already included impacts of wind turbine forced outages.
Also concerned about the impact of applying the methodology to a limited set of actual performance data.

## Slide 4: Wind Capacity Value
GATF considered several other methodologies based on actual wind turbine performance
GATF became aware of the new ERCOT LOLP study (January 2007) which includes a determination of the Effective Load Carrying Capability (ELCC) of wind in its analysis.
  Wind volatility was developed using AWS Truewind wind generation patterns (from the recently completed Analysis of Competitive Renewable Energy Zones).
  Software randomly selected hourly aggregate wind generation patterns in 24-hour increments.
  Random selections were made only from the energy patterns developed by AWS Truewind for the month being simulated.

## Slide 5: ELCC
Process:
Run the LOLP model with the base set of generating units and a generic thermal generator (550 MW) and determine the expected unserved energy.
Remove the generic thermal generator and add new wind generation until the same expected unserved energy is achieved.
The amount of new wind generation will have the same effective load-carrying capability as the 550-MW generic thermal generator
Results:
6,300 MW of wind had the same load carrying capacity as 550 MW of thermal generation (i.e., 8.7%).

## Slide 6: Recommendation
GATF believes that a change in methodology is warranted and that the ELCC methodology should be used until better (i.e., more) actual performance data becomes available to make an accurate determination of the true capacity value of wind in ERCOT.
Recommendation: Use the ELCC for wind as determined in the ERCOT LOLP study (8.7%) and update the ELCC value every two years.

## Slide 7: New Generating Capacity (Fossil)
New Generating Capacity
  Existing methodology: Requires signed Generation Interconnect Agreement (SGIA) to count in the CDR
  GATF was concerned a SGIA alone would not ensure that a new planned fossil capacity addition would actually be built (since new coal units require air permits from the TCEQ prior to construction)
  In order to provide a reasonable likelihood that a new fossil-fueled generating project will be built, GATF recommends adding the requirement for a project to have a SGIA and a TCEQ-approved air permit.
Recommendation: Include future fossil-fueled generating projects in the CDR if the project has both an SGIA and an air permit from the TCEQ

## Slide 8: Format Changes to CDR
GATF also recommends two format changes to the CDR summary page:
Delete additional reserve margin percentages for “high” , “low”, and “publicly announced” to avoid confusion on what is the “official” ERCOT reserve margin
Add line item for “uncommitted” resources, which would include:
  Remaining “mothballed” capacity not included in the “official” reserve margin calculation
  Remaining “switchable” capacity not included in the “official” reserve margin calculation
  Remaining DC tie capacity not included in the “official” reserve margin calculation
  New generating units that have initiated transmission interconnection studies (new wind generating units would be discounted appropriately)

## Slide 9: 2007 Example CDR
 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Firm Load Forecast (MW): | 60,544 | 62,110 | 63,206 | 64,838 | 66,436 | 67,922
Total Resources (MW): | 70,756 | 71,573 | 70,690 | 70,628 | 71,205 | 71,242
RESERVE MARGIN: | 16.9% | 15.2% | 11.8% | 8.9% | 7.2% | 4.9%
Uncommitted Resources | 0 | 6,575 | 8,300 | 10,535 | 14,000 | 12,302
Total Potential Resources (MW) (Uncommitted Generation + Total Resources) | 70,756 | 78,148 | 78,990 | 81,163 | 85,205 | 83,544
The numbers below are for illustrative purposes only:

## Slide 10
Questions?