# ERCOT Operations Report for ROS & OWG

# February 2007

## Frequency Control Disturbance (Less than 59.9 Hz or higher than 60.1Hz)

| Disturbance Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ID | Time | Frequency (Hz) | Duration (mm:ss) | Details | Notes |
| 1 | 02/04/2007 07:39:34 | 59.885 | 00:08 | Unit trip. 350MW lost |  |
| 2 | 02/07/2007 00:21:22 | 60.109 | 00:26 | Positive schedule change and low load |  |
| 3 | 02/08/2007 12:01:18 | 59.861 | 00:04 | Unit trip. 375MW lost | EECP step 1 |
| 4 | 02/12/2007 17:45:46 | 59.899 | 00:04 | Unit trip. 730MW lost |  |
| 5 | 02/12/2007 23:36:10 | 59.886 | 00:09 | Unit trip. 135MW lost |  |
| 6 | 02/13/2007 04:59:18 | 59.896 | 00:04 | Unit trip. 490MW lost |  |
| 7 | 02/13/2007 06:12:00 | 59.879 | 01:41 | Units slow to start |  |
| 8 | 02/16/2007 08:01:04 | 60.116 | 01:56 | QSE exceeded schedule by 300MW |  |
| 9 | 02/16/2007 15:51:22 | 59.886 | 00:02 | Unit trip. 440MW lost |  |
| 10 | 02/18/2007 21:54:30 | 59.800 | 01:16 | Unit trip. 800MW lost |  |
| 11 | 02/20/2007 08:01:16 | 59.894 | 00:08 | Unit trip. 600MW lost |  |
| 12 | 02/22/2007 19:31:18 | 59.810 | 00:12 | Unit trip. 630MW lost |  |
| 13 | 02/24/2007 12:02:10 | 60.142 | 01:56 | SCE Change (600MW)due to wind farms | EECP step 1 |
| 14 | 02/24/2007 19:03:32 | 60.108 | 00:18 | Poor QSE control and load drop off |  |
| 15 | 02/25/2007 01:04:30 | 59.862 | 00:08 | Unit trip. 450MW lost |  |
| 16 | 02/26/2007 18:34:22 | 59.886 | 00:24 | Bad load forecast & evening load pick up |  |
| 17 | 02/26/2007 22:22:18 | 60.115 | 01:40 | Load drop and positive SCE change |  |
| 18 | 02/28/2007 01:41:54 | 60.102 | 00:04 | Non conforming load drop and positive SCE change |  |

## Deployed Responsive (24) (Reported Above)

| ID | Time of deployed | Duration (h:mm:ss) | Max Deployed (MW) |
| --- | --- | --- | --- |
| 1 | 02/02/2007 06:05:38 | 0:11:18 | 253.76 |
| 2 | 02/02/2007 07:10:10 | 0:05:58 | 291.20 |
| 3 | 02/04/2007 07:39:36 | 0:05:56 | 353.61 |
| 4 | 02/06/2007 21:22:40 | 0:07:50 | 270.41 |
| 5 | 02/08/2007 11:21:20 | 0:09:48 | 253.76 |
| 6 | 02/08/2007 12:01:20 | 0:12:52 | 453.44 |
| 7 | 02/10/2007 10:01:48 | 0:19:12 | 253.76 |
| 8 | 02/12/2007 17:45:48 | 0:13:42 | 369.22 |
| 9 | 02/12/2007 23:36:10 | 0:04:32 | 436.80 |
| 10 | 02/13/2007 04:59:18 | 0:10:46 | 384.81 |
| 11 | 02/13/2007 06:01:42 | 0:45:10 | 473.20 |
| 12 | 02/16/2007 15:51:24 | 0:11:08 | 436.80 |
| 13 | 02/16/2007 23:58:50 | 0:05:08 | 257.92 |
| 14 | 02/18/2007 21:54:32 | 0:16:38 | 884.01 |
| 15 | 02/20/2007 06:02:04 | 0:13:14 | 338.01 |
| 16 | 02/20/2007 08:01:18 | 0:08:00 | 395.20 |
| 17 | 02/21/2007 06:07:34 | 0:09:12 | 338.01 |
| 18 | 02/22/2007 19:31:20 | 0:16:28 | 832.00 |
| 19 | 02/23/2007 07:04:08 | 0:03:18 | 317.20 |
| 20 | 02/24/2007 10:01:08 | 0:17:00 | 332.82 |
| 21 | 02/24/2007 12:00:24 | 0:05:48 | 364.00 |
| 22 | 02/25/2007 01:04:32 | 0:15:14 | 561.61 |
| 23 | 02/26/2007 18:30:52 | 0:27:06 | 349.44 |
| 24 | 02/27/2007 22:04:10 | 0:03:24 | 274.57 |

## Day-Ahead RMR and OOMC Capacity Purchases

| Historical RMR & OOMC Totals | Feb-06 | Jan-07 | Feb-07 |
| --- | --- | --- | --- |
| Austin | 3 | 48 | 4 |
| Bryan Area | 24 | 0 | 0 |
| Corpus | 6 | 0 | 1 |
| DFW | 19 | 51 | 16 |
| E RIO | 72 | 5 | 3 |
| Houston | 0 | 21 | 2 |
| Laredo | 41 | 91 | 48 |
| North | 11 | 10 | 3 |
| Northeast | 0 | 3 | 0 |
| San Antonio | 38 | 3 | 1 |
| South | 0 | 4 | 0 |
| W RIO | 75 | 60 | 58 |
| Western | 18 | 16 | 0 |
| Total | 307 | 312 | 136 |

| Data in detail | RMR | OOMC | RPRS | Total |
| --- | --- | --- | --- | --- |
| Austin | 0 | 4 | 10 | 14 |
| Bryan Area | 0 | 0 | 1 | 1 |
| Corpus | 0 | 1 | 0 | 1 |
| DFW | 0 | 16 | 1 | 17 |
| E RIO | 0 | 3 | 4 | 7 |
| Houston | 0 | 2 | 0 | 2 |
| Laredo | 48 | 0 | 0 | 48 |
| North | 0 | 3 | 1 | 4 |
| Northeast | 0 | 0 | 0 | 0 |
| San Antonio | 0 | 1 | 0 | 1 |
| South | 0 | 0 | 6 | 6 |
| W RIO | 0 | 58 | 1 | 59 |
| Western | 0 | 0 | 0 | 0 |
| Total | 48 | 88 | 24 | 160 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

## OOME / Congestion Management Activity:

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days of Occurrences |
| --- | --- | --- |
| Temple Pecan Creek - Tradinghouse & Lake Creek - Temple Switch 345kV | Lake Creek - Temple Pecan Creek 138 kV | 8 |
| Austrop Auto T2 345/138 kV | Austrop Auto T1 345/138 kV | 7 |
| Temple Pecan Creek - Tradinghouse & Lake Creek - Temple Switch 345kV | Evant - Goldthwaite 138 kV | 4 |
| STP - Whitepoint 345 kV | Blessing - Lolita 138 kV | 2 |
| STP - Whitepoint & STP - Skyline 345 kV | Blessing - Lolita 138 kV | 2 |
| Austrop Auto T1 345/138 kV | Austrop Auto T2 345/138 kV | 2 |
| Zorn - McCarty Lane 138 kV | McCarty Lane - Henne 138 kV | 2 |
| Zorn/Lytton Springs & Austrop 345 kV | Zorn - Luling 138 kV | 2 |
| Duke - North Edinburg 138 kV | Duke - Aderhold 138 kV | 2 |
| Cagnon/Calaveras & Braunig 345 kV | Medical Center Hamilton Wolfe 138 kV | 2 |
| Skyline - Walzam Rd. 138 kV | Calavers - Skyline 138 kV | 2 |
| Gibbons Creek Auto T2 345/138 kV | Greens Prairie - Gibbons Creek 138 kV | 2 |
| Kirkland Park - Centerville Switch 138 kV | East Zacha - White Rock 138 kV | 2 |
| Menard - Gillespie 138 kV | Menard Auto 138/69 kV | 1 |
| Trinidad - Stryker Creek & Mount Enterprise 345 kV | Athens Tap - Athens North Switch 138 kV | 1 |
| Watermill - Tricorner/Trinidad 345 kV | Garland Rd. - Centerville Rd. 138 kV | 1 |
| Lon Hill - Coleto Creek 345 kV | Coleto Creek - Victoria 138 kV | 1 |
| Sandow - Austrop 345 kV | Austrop Auto T1 345/138 kV | 1 |
| Big Brown - Richland Chamber 345 kV | Forest Grove Switch - Mabank 138 kV | 1 |
| Comanche Switch - Comanche Peak SES 345 kV | Lampasas - Adamsville 138 kV | 1 |
| Everman Switch - Kennedale 345 kV | Oak Hill 1 Tap - Tate West Tap | 1 |
| Morgan Creek Auto T1 345/138 kV | Morgan Creek Auto T2 345/138 kV | 1 |

## Zonal OC1’s

| CSC | Days |
| --- | --- |
| South - North | 3 |
| North - West | 2 |
| South - Houston | 2 |
| North - Houston | 0 |
| West - North | 0 |

## New RAPs

PCAP: Under heavy import into the Houston metropolitan area, several Houston import contingencies will show post contingent overloads of the Waller – Prairie View 138kV line. Opening Macedonia – Seaway 138kV line relieves the overload and allows greater transfers into Houston.

## New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 02/14/2007 | Frequency Control Desk - V3R51 | 316 |
| 02/14/2007 | Shift Supervisor Desk - V3R33 | 315 |
| 02/02/2007 | SS desk update EECP Public appeals | 314 |
| 02/02/2007 | Day Ahead desk OOMC for long lead time resources | 313 |

## Blackout/Load Shed incidences

None

## EECP

02/08 Implemented EECP

02/24 Implemented EECP

## Major system voltage problems

## None

## Voltage Instructions

None

## Major Computer Problems, Enhancements & Fixes

RTB:  100% available

Frequency control:  Unavailable for 4 minutes

## Communication

None

## ERCOT peak (Unofficial)

02/16/2007	08:00	50488MW

## Yearly Mid-Term Load Forecast Error Comparison

| Month | MAPE for MTLF run at 16:00 Day Ahead (2004) | MAPE for MTLF run at 16:00 Day Ahead (2005) | MAPE for MTLF run at 16:00 Day Ahead (2006) | MAPE for MTLF run at 16:00 Day Ahead (2007) |
| --- | --- | --- | --- | --- |
| January | 4.76 | 5.02 | 4.79 | 4.55 |
| February | 4.81 | 3.47 | 4.81 | 3.75 |
| March | 2.89 | 3.41 | 4.95 | N/A |
| April | 3.23 | 3.37 | 5.59 | N/A |
| May | 3.93 | 4.21 | 3.59 | N/A |
| June | 4.85 | 3.91 | 2.65 | N/A |
| July | 5.07 | 5.22 | 2.62 | N/A |
| August | 4.10 | 4.86 | 2.09 | N/A |
| September | 3.66 | 6.24 | 4.03 | N/A |
| October | 3.85 | 4.51 | 3.63 | N/A |
| November | 3.60 | 4.53 | 3.28 | N/A |
| December | 4.18 | 5.95 | 3.44 | N/A |
| Average MAPE for Year | 4.08 | 4.56 | 3.79 | N/A |

## OCN, Advisory, Alerts, and Emergency Notices:

### Generation:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 2/2/07 | 6:05 | 6:17 | XXXX SCE -700, XXXX SCE -330 and XXXX SCE -240. The 06:00 schedule ramp was 3400 MW. |
| 2/2/07 | 7:10 | 7:16 | Out of Up Regulation Service. |
| 2/6/07 | 21:22 | 21:31 | Deployed Responsive Reserve 270.41 MW due to the loss of XXXX |
| 2/8/07 | 12:02 |  | XXXX tripped with 374mw |
| 2/10/07 | 10:02 | 10:21 | A large change in the base power schedule coupled with a 615 MW generation schedule change after the offset was entered for IE 10:15. |
| 2/12/07 | 17:45 | 17:48 | XXXX tripped at 750 MW, ERCOT Load 31720 MW |
| 2/12/07 | 23:36 | 23:38 | XXXX tripped at 275 MW, ERCOT Load 26860 MW |
| 2/13/07 | 4:59 | 5:10 | XXXX tripped 300 MW, ERCOT Load 27,500 MW. |
| 2/13/07 | 6:02 | 6:46 | Deployed 473 MW of Responsive Reserve Service at 59.91hz due to large schedule changes and SCEs. ERCOT Load 31,430. |
| 2/16/07 | 8:02 | 8:36 | VDI XXXX for fleet deployment down due to high frequency |
| 2/16/07 | 8:02 | 8:36 | VDI XXXX for fleet deployment down due to high frequency |
| 2/16/07 | 15:51 | 15.53 | XXXX tripped at 436 MW, ERCOT load 33578 MW |
| 2/16/07 | 23:58 | 24:00 | ERCOT load 34042. Generation change of 3600MW's for 00:15 interval. |
| 2/18/07 | 21:54 | 22:02 | XXXX tripped with 800MW's. ERCOT load 31811. |
| 2/20/07 | 6:02 | 6:15 | XXXX had an SCE of -500mw. Nonconforming load operation contributed to the negative ACE. |
| 2/20/07 | 801 | 809 | XXXX coming offline due to a tube leak and XXXX tripped with 224mw. |
| 2/22/07 | 19:31 | 19:35 | XXXX tripped, unit at 626 MW, ERCOT Load 33900 MW |
| 2/23/07 | 7:04 | 7:07 | Frequency spiked to 59.909hz. Deployed 317 MW of responsive reserve during the 07:15 interval ramp while the nonconforming loads were loading up. ERCOT load of 30999MW's. |
| 2/24/07 | 10:01 | 10:18 | Frequency spiked to 59.906hz. Deployed 332 MW of responsive reserve during the 10:15 interval ramp. Insufficient amount of regulation available. ERCOT load of 29925MW's. |
| 2/24/07 | 12:00 | 12:06 | XXXX tripped with 226MW's. ERCOT load of 30044MW's. |
| 2/25/07 | 1:04 | 1:07 | XXXX tripped with 453MW's. ERCOT load 24348. |
| 2/27/07 | 22:04 | 22:07 | Frequency spiked to 59.904hz due to generation schedule change for 22:15 interval. Deployed 275MW's of responsive reserve. ERCOT load 30437 MW. |

### Insufficient Capacity:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 2/1/07 | 0:25 | 14:42 | Adjusted Responsive Reserve below 3000 MW. |
| 2/1/07 | 17:45 | 22:25 | Adjusted Responsive Reserve below 3000 MW. |
| 2/2/07 | 6:20 | 7:03 | Adjusted Responsive Reserve below 3000 MW. |
| 2/2/07 | 7:03 | 12:45 | Adjusted Responsive Reserve below 2500 MW |
| 2/2/07 | 18:23 | 22:30 | Adjusted Responsive Reserve below 3000 MW. |
| 2/3/07 | 5:00 | 10:10 | Adjusted Responsive Reserve below 3000 MW. |
| 2/3/07 | 18:42 | 21:17 | Adjusted Responsive Reserve below 3000 MW. |
| 2/4/07 | 7:02 | 7:41 | Adjusted Responsive Reserve below 3000 MW. |
| 2/4/07 | 7:41 | 10:15 | Adjusted Responsive Reserve below 2500 MW. |
| 2/4/07 | 8:30 | 9:45 | OOME Laredo #3 due to Alert for Adjusted Responsive Reserve. |
| 2/5/07 | 6:30 | 8:43 | Adjusted Responsive Reserve below 3000 MW. |
| 2/6/07 | 6:38 | 10:35 | Adjusted Responsive Reserve below 3000 MW. |
| 2/7/07 | 1:23 | 17:39 | Adjusted Responsive Reserve below 3000 MW. |
| 2/7/07 | 18:50 | 21:49 | Adjusted Responsive Reserve below 3000 MW. |
| 2/8/07 | 9:15 | 10:34 | Adjusted Responsive Reserve below 3000 MW. |
| 2/8/07 | 10:34 | 22:07 | Adjusted Responsive Reserve below 2500 MW. |
| 2/8/07 | 12:08 | 12:38 | EECP step #1 for Adjusted Responsive Reserve under 2300 MW. |
| 2/9/07 | 0:09 | 7:11 | Adjusted Responsive Reserve below 3000 MW. |
| 2/9/07 | 7:11 |  | Adjusted Responsive Reserve below 2500 MW. |
| 2/10/07 | 0:00 | 2:05 | Adjusted Responsive Reserve below 2500 MW. |
| 2/10/07 | 5:41 | 12:31 | Adjusted Responsive Reserve below 3000 MW. |
| 2/11/07 | 3:00 | 6:21 | Adjusted Responsive Reserve below 3000 MW. |
| 2/11/07 | 8:13 | 13:38 | Adjusted Responsive Reserve below 3000 MW. |
| 2/11/07 | 18:10 | 22:00 | Adjusted Responsive Reserve below 3000 MW. |
| 2/12/07 | 18:45 | 20:50 | Adjusted Responsive Reserve below 3000 MW. |
| 2/13/07 | 5:20 | 6:00 | Adjusted Responsive Reserve below 3000 MW. |
| 2/13/07 | 6:45 | 11:45 | Adjusted Responsive Reserve below 3000 MW. |
| 2/13/07 | 18:40 | 23:58 | Adjusted Responsive Reserve below 3000 MW. |
| 2/14/07 | 6:40 | 12:30 | Adjusted Responsive Reserve below 3000 MW. |
| 2/14/07 | 7:10 | 8:05 | Adjusted Responsive Reserve below 2500 MW. |
| 2/14/07 | 18:35 | 21:00 | Adjusted Responsive Reserve below 3000 MW. |
| 2/15/07 | 6:35 | 07:45 | Adjusted Responsive Reserve below 3000 MW. |
| 2/16/07 | 6:40 | 8:20 | Adjusted Responsive Reserve below 3000 MW. |
| 2/17/07 | 23:01 | 24:00 | Adjusted Responsive Reserve below 3000 MW. |
| 2/18/07 | 0:01 | 1:52 | Adjusted Responsive Reserve below 3000 MW. |
| 2/18/07 | 6:35 | 8:50 | Adjusted Responsive Reserve below 3000 MW. |
| 2/19/07 | 5:37 | 8:10 | Adjusted Responsive Reserve below 3000 MW. |
| 2/21/07 | 7:07 | 10:18 | Adjusted Responsive Reserve below 3000 MW |
| 2/21/07 | 14:24 | 22:15 | Adjusted Responsive Reserve below 3000 MW |
| 2/22/07 | 14:24 | 22:30 | Adjusted Responsive Reserve below 3000 MW |
| 2/22/07 | 7:33 | 20:10 | Alert Adjusted Responsive less than 2500 MW |
| 2/23/07 | 10:07 | 14:45 | Adjusted Responsive Reserve below 3000 MW |
| 2/23/07 | 23:06 | 0:00 | Adjusted Responsive Reserve below 3000 MW. |
| 2/24/07 | 0:00 | 2:00 | Adjusted responsive reserve below 3000 MW. |
| 2/24/07 | 10:20 | 15:15 | Adjusted responsive reserve below 3000 MW. |
| 2/24/07 | 11:43 | 12:15 | EECP step one initiated due to adjusted responsive reserve below 2300MW's. |
| 2/24/07 | 11:15 | 15:15 | Alert for issued for adjusted responsive reserve below 2500 MW. |
| 2/24/07 | 23:19 | 0:00 | Adjusted Responsive Reserve below 3000 MW. |
| 2/24/07 | 18:43 | 21:00 | Adjusted responsive reserve below 3000 MW. |
| 2/25/07 | 0:00 | 5:48 | Adjusted responsive reserve below 3000 MW. |
| 2/25/07 | 18:45 | 20:56 | Adjusted responsive reserve below 3000 MW. |
| 2/26/07 | 6:35 | 7:28 | Adjusted Responsive Reserve below 3000 MW. |
| 2/26/07 | 13:44 | 22:38 | Adjusted Responsive Reserve below 3000 MW. |
| 2/27/07 | 13:44 | 15:20 | Adjusted Responsive Reserve below 3000 MW. |
| 2/27/07 | 18:46 | 21:03 | Adjusted Responsive Reserve below 3000 MW. |

### Transmission:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 2/13/07 | 20:24 | 22:00 | Transmission Alert for the loss of Holder – Brownwood Switch 138kV overloads Hasse 138/69kV Autotransformer beyond first contingency limits. |
| 2/14/07 | 4:20 | 24:00 | Transmission Emergency for the Del Rio area due to the loss of Asherton - West Conoco 138kV. |
| 2/14/07 | 16:40 | 24:00 | South - North CSC limit changed from 1040 MW to 850 MW per ERCOT engineers, loss of Sandow - Austrop 345kV overloads Gideon - Butler 138kV in RTCA. |
| 2/15/07 | 0:15 | 24:00 | Transmission Emergency for the Del Rio area due to the loss of Asherton - West Conoco 138kV. |
| 2/16/07 | 0:15 | 24:00 | Transmission Emergency for the Del Rio area due to the loss of Asherton - West Conoco 138kV. |
| 2/17/07 | 0:15 | 12:00 | Transmission Emergency for the Del Rio area due to the loss of Asherton - West Conoco 138kV. |
| 2/18/07 | 0:15 | 12:00 | Transmission Emergency for the Del Rio area due to the loss of Asherton - West Conoco 138kV. |
| 2/20/07 | 9:30 | 21:00 | ERCOT issues a Transmission Emergency due to the loss of the Laredo-University or North Laredo-Wormser Rd 138kV line causes low voltage at numerous locations in Laredo and Cotulla area. |
| 2/21/07 | 9:30 | 20:45 | Transmission Emergency issued due to the post contingency loss of the Laredo-University or North Laredo-Wormser Rd 138kV line causes low voltage at numerous locations in Laredo and Cotulla area. |
| 2/22/07 | 14:52 |  | South to Houston limit changed to 1300MW at 14:52 due to XXXX line trip. |
| 2/22/07 | 15:20 |  | South to Houston limit changed to 1210MW at 15:20 per Operations engineer calculation. |
| 2/22/07 | 23:00 | 24:00 | ERCOT is issued a Transmission Alert, Loss of Sandow Switch 345/138 Transformer overloads the Sandow 345/138 KV transformer with no market solution |
| 2/23/07 | 0:15 | 22:30 | Transmission Alert for the loss of Sandow Switch 345/138 autotransformer overloads the Sandow 345/138 KV autotransformer with no market solution. |
| 2/23/07 | 6:55 | 22:30 | Transmission alert for the loss of Sandow Switch - Sandow SES overloads Sandow SES 345/138kV autotransformer with no market solution. |
| 2/23/07 | 11:25 | 14:08 | Transmission alert for the loss Everman Switch - Kennedale 345kV or Kennedale - Century 345kV or Sherry Switch - Everman Switch or Century - Sherry Switch 345kV overloads Oak Hill 1 Tap - Tate West Tap 138kV beyond first contingency limits. |
| 2/23/07 | 12:00 | 22:30 | South to North CSC limit changed to 600MW's as a result of system topology changes per ERCOT engineers. |

### Weather:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 2/12/07 | 11:30 | 24:00 | Weather OCN issued for anticipated low temps. Effective Wed. 01:00 2-14-07 till Friday 08:00 2-16-07. |
| 2/13/07 | 0:00 | 24:00 | Weather OCN issued for anticipated low temps. Effective Wed. 01:00 2-14-07 till Friday 08:00 2-16-07. |
| 2/14/07 | 0:15 | 24:00 | Weather OCN issued for anticipated low temperatures effective Wednesday 2-14-07 01:00 till Friday 2-16-07 08:00. |
| 2/15/07 | 0:15 | 20:30 | Weather OCN issued for anticipated low temperatures effective Wednesday 2-14-07 01:00 till Friday 2-16-07 10:00. |
| 2/15/07 | 20:30 | 24:00 | Winter Weather Advisory, some of the coldest temperatures of the season is expected across Texas overnight. Currently the forecasted ERCOT load would be a new Winter Peak for Friday morning. |
| 2/16/07 | 0:15 | 20:00 | Winter Weather Advisory, some of the coldest temperatures of the season are across Texas this morning. Currently the forecasted ERCOT load would be a new Winter Peak. |

### Miscellaneous:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 2/1/07 | 9:20 |  | EMS Data Base Load |
| 2/1/07 | 15:20 |  | EMS Data Base Load |
| 2/15/07 | 10:05 | 10:55 | ERCOT planned site to site failover from Austin to Taylor complete |
| 2/15/07 | 18:00 | 20:40 | Emergency Notification due to ERCOT unable to clear and close the Day Ahead Replacement Reserve Market by the 1800 dead line due to system issues. ERCOT personnel are currently working on the problem. |
| 2/18/07 | 13:00 | 13:30 | Ancillary Service Market Close for 02/19/07 was extended to 13:30 due to Market Participant communication issues to ERCOT |
| 2/22/07 | 13:30 | 14:09 | Day Ahead Ancillary Market cleared on time but approval was delayed until 1409 due to software problem. |