## Slide 1: ROS Report to TAC
March 8, 2007
By
Stuart Nelson

## Slide 2: Outline
EILS
Power System Stabilizers
Reserve Discount Factor
RRS Deployment on January 16, 2007
EECP Events
ROS WG Analyzing EECP Events

## Slide 3: EILS
Formed ad hoc work group
Endorsed PRR701
Passed motion concerning PRR705
Drafted response to PRS questions
Working to develop cost effective alternatives to PRR705

## Slide 4: Power System Stabilizers
ERCOT requires new units to have PSS
Identified as potential compliance issue
Compliance monitored on critical units
OWG will develop PSS testing procedures
NERC requires periodic PSS study
ERCOT Operations must develop PSS log

## Slide 5: Reserve Discount Reduction Factor
Proposal to reduce factor from 7% to 4% between October and March
ROS opted not to reduce factor at this time
Factor not yielding expected difference in capacity under all conditions
Reduced factor would only be used for a few weeks
ROS will review the Reserve Discount Factor again at its September 2007 meeting

## Slide 6: RRS Deployment – January 16, 2007
Outage of distribution feeder at ERCOT in Taylor
Primary frequency sensing device had no signal
EMS triggers RRS below 59.91 HZ
Full Deployment of RRS (1150 MW)
Feed power restored (2 seconds)
EMS recalls RRS when frequency is above 59.97 Hz

## Slide 7: Conclusions and Next Steps
Second occurrence in 3 years
ERCOT has multiple frequency sources available
No “fail-over” mechanism for loss of primary frequency source
PR-50021 will address using multiple sources of frequency to avoid future occurrences

## Slide 8: EECP Events December 2006 – February 2007
December 13, 22 and 23, January 20, February 8 and February 24
Triggered when Adjusted Responsive Reserve (ARR) dropped below 2300 MW
None of the events required firm load shedding
Interruptible load was shed December 22, 2006
  Potential NERC Disturbance Control Standard Event
Lost 1500MW of wind power production on February 24, 2007

## Slide 9: December 13 and 23
Occurred during typical winter peak periods (morning and evening)
December 13, 2006 event lasted from 6:52 to 7:16
  Three units totaling 786 MW tripped between 4:20 and 6:14
  ARR dipped to 2178 MW during morning load pick-up
  Event quickly resolved in 24 minutes by market in response to EECP
December 23, 2006 event lasted from 18:15 to 20:45
  Evening load exceeded forecast by about 1000 MW (34,000 actual vs 33,000 forecast)
  ARR dipped to 2206 MW
  Event resolved in 2½hours by increasing RMR unit output, OOMing on off-line gas turbines and market response to EECP Step 1

## Slide 10: January 20, 2007 and February 8, 2007
January 20, 2007 event lasted from 11:01 to 12:00
  Cold front caused load to increase
  ARR dipped to 2246 MW
  Event resolved in one hour by arranging emergency imports over North and East DC ties, OOMing on-line six gas turbines and market response during EECP Step 1
February 8, 2007 event lasted from 12:08 to 12:38
  At 12:01 a unit carrying 345 MW tripped
  453 MW Responsive Reserve automatically deployed, dropping ARR to 2199 MW
  Event resolved within 30 minutes by OOMing on-line two gas turbines and market response during EECP Step 1

## Slide 11: December 22, 2006
Potential NERC Disturbance Control Standard Event
Between 2:53 and 3:00 five generating units either tripped or ran-back, totaling a loss of 1900 MW
System frequency reached a low point of 59.691 Hz at 2:55
All LaaRs did not trip automatically. Some LaaRs were deployed manually by ERCOT at 2:58
Frequency recovered to 60 HZ at 3:03
EECP Step 1 was declared at 3:03 when reserves dropped below 2300 MW
LaaRs restored at 3:48 after frequency stabilized
EECP ended at 4:07 when reserves were restored

## Slide 12: Total MW Output Wind Farms Combined – EECP 2/24/2007

## Slide 13: Different Behavior of wind farms geographically close

## Slide 14: Geographically Distributed Wind Farm Tripping

## Slide 15: ROS Work Groups Analyzing Events
December 22, 2006 and February 24, 2007 events require further study
ERCOT staff does not have expertise in all fields needed for analysis
ERCOT staff does not have detailed knowledge of TO and Generation protection systems
ERCOT Staff Constraints
Confidentiality Requirements

## Slide 16: Questions?