## Slide 1: Review of Regulation Procurement Quantities in 2006
ERCOT Technical Advisory Committee Meeting
March 8, 2007
Dan L. Jones

## Slide 2: Historical Regulation Procurement

## Slide 3: Background
ERCOT’s procedures for determining the quantities of Regulation Up and Down are specified in ERCOT Methodologies for Determining Ancillary Service Requirements
The Regulation Procurement Methodology has the following reliability objectives:
  “By arranging for 2.5 standard deviations times the historic average usage for each hours requirement; ERCOT provides the mathematical expectation that sufficient regulation will be available 98.8% of all periods.”
  “This requirement . . . implies that 1.2% of every month . . . ERCOT expects to exhaust available regulation services.”

## Slide 4: 2006 Monthly Reg Up Depletion Rates

## Slide 5: 2006 Monthly Reg Down Depletion Rates

## Slide 6: 2006 Hourly Reg Up Depletion Rates
June
January
No exhaustion in any month for this hour

## Slide 7: 2006 Hourly Reg Down Depletion Rates

## Slide 8: Observations
In 2006, ERCOT Regulation exhaustion rate for RegUp and RegDn each averaged around 0.5%, which is significantly less than the reliability objective of 1.2%.
Issues with the methodology
  The raw data distribution is not normal
  The methodology manipulates the raw data through steps of averaging and grouping that distort the statistical results
  The grouping of hours results in the calculated requirement for the highest hour in the group setting the quantity for the entire group
Alternate Methodologies
  A 98.8th percentile method using the same historical data with no grouping among hours appears to produce results that are more efficient and closer to the reliability objectives
  An adjusted 2.5 standard deviation method using raw, unadjusted 1-minute data for Regulation Up and Down and eliminating the minutes with zero deployment with no grouping among hours produces results that are very similar to the percentile method

## Slide 9: Back Testing of Percentile Method November 2006
Depletion Rates
Actual: 0.4%
Modified: 1.1%
Cost Reduction @ Actual Clearing Prices
$3.2 million
Depletion Rates
Actual: 0.6%
Modified: 1.1%
Cost Reduction @ Actual Clearing Prices
$0.8 million

## Slide 10: Back Testing of Percentile Method December 2006
Depletion Rates
Actual: 0.5%
Modified: 1.1%
Cost Reduction @ Actual Clearing Prices
$1.3 million
Depletion Rates
Actual: 0.5%
Modified: 1.1%
Cost Reduction @ Actual Clearing Prices
$1.3 million

## Slide 11: Back Testing of Adjusted STDEV Method November 2006
Depletion Rates
Actual: 0.5%
Modified: 1.2%
Depletion Rates
Actual: 0.5%
Modified: 1.3%

## Slide 12: Back Testing of Adjusted STDEV Method December 2006
Depletion Rates
Actual: 0.5%
Modified: 1.1%
Depletion Rates
Actual: 0.5%
Modified: 1.0%