## Slide 1: TAC Briefing on: - Report on Constraints and Needs: Five Year Plan Development - Long Term System Assessment (LTSA) - Entergy Integration Study
2/1/2007

## Slide 2
Coordinated, comprehensive transmission plan for the ERCOT region
  Identifies all upgrades that would not require RPG review which were included by TSPs in SSWG cases
  For “larger” projects that meet the criteria for RPG review, includes the projects which passed an analysis that was similar to what would be performed on project proposed to RPG
The intent is to streamline and to provide a well documented basis for the RPG review of projects
Five Year Plan

## Slide 3
Begin with SSWG powerflow cases
Identify all system improvements included in future years
Remove projects that would require RPG review
Identify minimum set of projects needed to meet reliability criteria
Identify set of projects that are economic
Evaluate combined set of projects to minimize overlap
Five Year Plan Process

## Slide 4
Report includes listing of major projects included in Five Year Plan, in body
  Includes listing of all projects, in appendix
Report includes projection of remaining congested elements and indication of marginal congestion for 2007-2011
Report on Constraints and Needs

## Slide 5
Long Term System Assessment (LTSA) Summary

## Slide 6: Long Term System Assessment (LTSA)
Goal:
  Meet the legislative requirement to “study the need for increased transmission and generation capacity”
  Extend the planning horizon out to 10 years, in order to guide near-term decisions
Process:
  Identified Drivers for new transmission and generation, with stakeholder input
  Developed discrete scenarios under which to study the G&T needs
  Developed proxy new generation to meet load growth for each scenario (amount, type and locations determined by economics)
  Identified local transmission constraints that will need to be solved
  Identified bulk transmission needs and potential line concepts

## Slide 7: Scenarios for ~2016 Timeframe
Gas Prices
  $4, $7, $10 (per MMBtu, delivered to generating plants)
Load Growth
  Base: Peak and Energy Grow at 2%/year from 2006
  High Growth: Peak and Energy Grow at 4%/year from 2006
  High Energy: Peak grows at 2%/year and energy grows at 3%/year
Environmental Regulations
  All cases have regulations currently being implemented
  Current Case: No additional environmental regulations
  Low Carbon Case: Current regulations plus $8/ton for CO2 emissions
  High Carbon Case: Current regulations plus $16/ton for CO2 emissions
Scenario | Gas Price | Load | Environmental
1 | Low | Base | Low
2 | High | High | Current
3 | Medium | High Energy | High
4 | Medium | Base | Current

## Slide 8: Generation Additions Summary
 |  | New Build |  |  |  | 
 | Scenario | Coal | CCGT | CT | Total | ReserveMargin
High Wind 12000MW | 1 |  | 13,570 | 4,500 | 18,070 | 12.0%
 | 2 | 30,000 |  | 8,700 | 38,700 | 14.2%
 | 3 | 24,000 |  | 600 | 24,600 | 19.6%
 | 4 | 18,000 |  | 2,700 | 20,700 | 15.1%
Low Wind 6000MW | 1 |  | 15,930 | 3,000 | 18,930 | 12.6%
 | 2 | 33,000 |  | 8,400 | 41,400 | 16.7%
 | 3 | 28,250 |  | 300 | 28,550 | 24.3%
 | 4 | 21,000 |  | 1,500 | 22,500 | 17.0%
Likely retirements were not yet considered in these numbers
In scenarios 2-4, CT additions may indicate need for additional import capacity into the area where those CTs were sited

## Slide 9: Lower Voltage Constraints:
Lower voltage lines (<345kV lines)
Improvement needed for reliability shown in black
Improvements needed for economics shown in yellow

## Slide 10: 345 kV Projects

## Slide 11: Example Highlights
Current generation interconnection activity is consistent with 3 of 4 scenarios
Significant additional upgrades of the 138kV system and additional 345kV support (particularly in DFW and along the I-35 cities from the west) will be required in years 6-10 even with moderate load growth
Installation of switching stations at points where existing 345kV circuits intersect (Singleton, Navarro, Zenith and Paint Creek) may result in better distribution of power and increase transfer capacities
At lease one additional bulk circuit will be needed into the Houston and DFW areas for reliability, and additional circuits may be economically justified

## Slide 12
Entergy Integration Study Summary

## Slide 13: Impetus for Study
Entergy required to file transition to competition plan for Texas area with PUCT by 1/1/2007
One option is to disconnect Entergy Texas area from Eastern Interconnect and connect to ERCOT
ERCOT was asked to study technical requirements to reliably and efficiently interconnect this area

## Slide 14: Requirements
Identify transmission projects necessary to:
  Meet ERCOT/NERC reliability criteria
  Allow efficient operation of the system
Allow existing contractual requirements to be met through asynchronous ties
Minimize cost of “tie backs” on Eastern Interconnect

## Slide 15: Min Set of Reliability and Contractual Projects
Quarry Sub and 150MW DC Tie
Quarry-Rivtrin &Rivtrin Sub
Substation Improvements at Grimes
Porter Sub and Loop
Bon Wier-Kirbyville
Etoile tie
Hartburg 300MW DC
Hartburg-Sabine
Total Capital Cost
$248 M

## Slide 16: Economic Projects
The minimum reliability projects set met ERCOT steady state reliability criteria but not efficient
Evaluated economic projects against the set of minimum reliability projects
Incremental production cost savings must be greater than the incremental annualized capital cost of the projects

## Slide 17: Economic Projects Nacogdoches-Houston Loop
CHINA – CB 345KV DBL. CKT.
CYPRESS - CHINA 345KV DBL. CKT.
LUFKIN – CYPRESS 345KV DBL. CKT.
LUFKIN – NACOGDOCHES 345kV
Total Capital Cost
$278 M
Annual Production Cost Savings:
$63M @ $5 gas
$95M @ $7 gas

## Slide 18: QUESTIONS?