## Slide 1: TXU Electric Delivery Anna – Collin – NW Carrollton 345 kV Line Upgrades TAC – 03/08/2007

## Slide 2: Description of Project
Upgrade 13.2 mile Anna – Collin 345 kV line from 2-795 kcmil ACSR to 959.6 kcmil ACSS/TW for 3200 Amp capacity.
Cost: Approx. $4 M.
Upgrade 19.3 mile Collin – NW Carrollton 345 kV line by raising towers for 2292 Amp capacity.
Cost: Approx $3 M.

## Slide 3
Economic Analysis 1st Part of Project
Anna – Collin 345 kV Upgrade
  Identified as economic in ERCOT 2006 5-Year Transmission Study.
  Confirmed as economic in this study saving $7.6 M in 2007-08.
  Part of Valley 345 kV SPS exit strategy.

## Slide 4
Economic Analysis 2nd Part of Project
Collin – NW Carrollton 345 kV Upgrade
  Insufficient economic savings to warrant upgrade unless additional low-cost generation is added in northeast.
  Only one minor overload for one contingency in SSWG case.
  Will be re-studied with revised DFW-area unit assumptions as part of Coal Plant Integration Study.

## Slide 5
Stakeholder Review
The Stakeholder review period for this project was held in October 2006
There were no dissenting comments on this package of projects and TXUED resolved all questions

## Slide 6
ERCOT Support for the Project
ERCOT supports the need for the Anna to Collin 345 kV line upgrade and will be requesting that it be endorsed by the Board.