## Classes
Package | Class | Inheritance Path | Name Space | Documentation | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data | Internal Class Name
61970 | iec61970CIMVersion |  | cim | This is the IEC 61970 CIM version number assigned to this UML model file. cim61970_v002 was created from cim10_v000_WG13cimIssues_61968_Rev6_22Feb2005 that is the merged wg13 and wg14 models. The content has a number of wg13 issue resolutions. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMGeneration | GenerationVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit |  | cim | A generating unit whose prime mover could be a steam turbine, combustion turbine, or diesel engine. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroGeneratingUnit |  | cim | A generating unit whose prime mover is a hydraulic turbine (e.g., Francis, Pelton, Kaplan) | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant |  | cim | A hydro power station which can generate or pump. When generating, the generator turbines receive there water from an upper reservoir. When pumping, the pumps receive their water from a lower reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit |  | cim | A single or set of synchronous machines for converting mechanical power into alternating-current power. For example, individual machines within a set may be defined for scheduling purposes while a single control signal is derived for the set. In this case there would be a GeneratingUnit for each member of the set and an additional GeneratingUnit corresponding to the set. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GenUnitOpSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The generating unit's Operator-approved current operating schedule (or plan), typically produced with the aid of unit commitment type analyses. The X-axis represents absolute time. The Y1-axis represents the status (0=off-line and unavailable: 1=available: 2=must run: 3=must run at fixed MW value: etc.). The Y2-axis represents the must run fixed MW value where required. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CombinedCyclePlant |  | cim | A set of combustion turbines and steam turbines where the exhaust heat from the combustion turbines is recovered to make steam for the steam turbines, resulting in greater overall plant efficiency | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CogenerationPlant |  | cim | A set of thermal generating units for the production of electrical energy and process steam (usually from the output of the steam turbines). The steam sendout is typically used for industrial purposes or for municipal heating and cooling. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir |  | cim | A water storage facility within a hydro system, including: ponds, lakes, lagoons, and rivers. The storage is usually behind some type of dam. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | LevelVsVolumeCurve | Curve; IdentifiedObject | cim | Relationship between reservoir volume in millions of cubic meters and reservoir level in meters. The curve values are: x axis - Level, y 1 axis - Volume. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GrossToNetMWCurve | Curve; IdentifiedObject | cim | Relationship between the generating unit's gross MW output on the X-axis (measured at the terminals of the machine(s)) and the generating unit's net MW output on the Y-axis (based on utility-defined measurements at the power station). Station service load. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | TargetLevelSchedule |  | cim | Reservoir water level targets from advanced studies or 'rule curves'. Typically in one hour increments for up to 10 days. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | TailbayLossCurve | Curve; IdentifiedObject | cim | Relationship between tailbay head loss (in meters on the Y-axis) and the total discharge into the power station's tailbay (in m3/sec on the X-axis) . There could be more than one curve depending on the level of the tailbay reservoir or river level. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | SteamSendoutSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The cogeneration plant's steam sendout schedule in klb/hour versus time. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel |  | cim | Unit start up characteristics depending on how long the unit has been off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | AccountBalance | Curve; IdentifiedObject | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | AirCompressor |  | cim | Combustion turbine air compressor which is an integral part of a compressed air energy storage (CAES) plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CAESPlant |  | cim | Compressed air energy storage plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionAccount |  | cim | Accounts for tracking emissions usage and credits for thermal generating units. A unit may have zero or more emission accounts, and will typically have one for tracking usage and one for tracking credits. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionCurve |  | cim | Relationship between the unit's emission rate in units of mass per hour (Y-axis) and output in MW (X-axis) for a given type of emission. This curve applies when only one type of fuel is being burned. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel |  | cim | The fossil fuel consumed by the non-nuclear thermal generating units, e.g., coal, oil, gas. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule |  | cim | The amount of fuel of a given type which is allocated for consumption over a specified period of time. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GenUnitOpCostCurve |  | cim | Relationship between unit operating cost in. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatInputCurve |  | cim | Relationship between unit heat input in MBtu per hour for main fuel (Y1-axis) and supplemental fuel (Y2-axis) versus unit output in MW (X-axis). The quantity of main fuel used to sustain generation at this output level is prorated for throttling between definition points. The quantity of supplemental fuel used at this output level is fixed and not prorated. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatRateCurve |  | cim | Relationship between unit heat rate in MBtu/hour per MW (Y-axis) and unit output in MW (X-axis). The heat input is from all fuels. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroGeneratingEfficiencyCurve | Curve; IdentifiedObject | cim | Relationship between unit efficiency in percent and unit output in MW for a given net head in meters. The relationship between efficiency, discharge, head, and power output is expressed as follows: E =KP/HQ Where: (E=%) (P=MW) (H=m) (Q=m3/s) (K=constant) For example, a curve instance for a given net head could relate efficiency (Y-axis) versus MW output (X-axis) or versus discharge on the X-axis. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroGenEfficiencyCurve
CIMProduction | HydroPump |  | cim | A synchronous motor-driven pump, typically associated with a pumped storage plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPumpOpSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The hydro pump's Operator-approved current operating schedule (or plan), typically produced with the aid of unit commitment type analyses.The unit's operating schedule status is typically given as: (0=unavailable) (1=avilable to startup or shutdown) (2=must pump). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | IncrementalHeatRateCurve |  | cim | Relationship between unit incremental heat rate in (delta MBtu/hour) per (delta MW )and unit output in MW. The IHR curve represents the slope of the HeatInputCurve. Note that the 'incremental heat rate' and the 'heat rate' have the same engineering units, i.e., MBtu/MWh. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | PenstockLossCurve | Curve; IdentifiedObject | cim | Relationship between penstock head loss (in meters) and total discharge through the penstock (in cubic meters per second). One or more turbines may be connected to the same penstock. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ShutdownCurve |  | cim | Relationship between the rate in gross MW/minute (Y-axis) at which a unit should be shutdown and its present gross MW output (X-axis). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartIgnFuelCurve |  | cim | The quantity of ignition fuel (Y-axis) used to restart and repay the auxiliary power consumed versus the number of hours (X-axis) the unit was off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartMainFuelCurve |  | cim | The quantity of main fuel (Y-axis) used to restart and repay the auxiliary power consumed versus the number of hours (X-axis) the unit was off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartRampCurve |  | cim | Rate in gross MW/minute (Y-axis) at which a unit can be loaded versus the number of hours (X-axis) the unit was off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | InflowForecast | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | Natural water inflow to a reservoir, usually forecasted from predicted rain and snowmelt. Typically in one hour increments for up to 10 days. The forecast is given in average cubic meters per second over the time increment. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PrimeMover |  | cim | The machine used to develop mechanical energy used to drive a generator. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine |  | cim | A prime mover that is typically fueled by gas or light oil. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamSupply |  | cim | Steam supply for steam turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine |  | cim | Steam turbine | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine |  | cim | A water driven prime mover. Typical turbine types are: Francis, Kaplan, and Pelton. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical |  | cim | Once-through supercritical boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical |  | cim | Once-through subcritical boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler |  | cim | Drum boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply |  | cim | Fossil fueled boiler (e.g., coal, oil, gas) | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply |  | cim | Pressurized water reactor used as a steam supply to a steam turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply |  | cim | Boiling water reactor used as a steam supply to a steam turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CTTEMPMWCurve |  | cim | Relationship between the combustion turbine's power output rating in gross MW (X-axis) and the ambient air temperature in temperature units (Y-axis). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HeatRecoveryBoiler |  | cim | The heat recovery system associated with combustion turbines in order to produce steam for combined cycle plants. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | CommunicationLink | PowerSystemResource; IdentifiedObject | cim | The connection to remote units is through one or more communication links. Reduntant links may exist. The CommunicationLink class inherit PowerSystemResource. The intention is to allow CommunicationLinks to have Measurements. These Measurements can be used to model link status as operational, out of service, unit failure etc. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteControl |  | cim | Remote controls are ouputs that are sent by the remote unit to actuators in the process. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemotePoint | IdentifiedObject | cim | For a RTU remote points correspond to telemetered values or control outputs. Other units (e.g. control centers) usually also contain calculated values. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteSource |  | cim | Remote sources are state variables that are telemetered or calculated within the remote unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteUnit |  | cim | A remote unit can be a RTU, IED, substation control system, control center etc. The communication with the remote unit can be through various standard protocols (e.g. IEC 61870, IEC 61850) or non standard protocols (e.g. DNP, RP570 etc.). A remote unit contain remote data points that might be telemetered, collected or calculated. The RemoteUnit class inherit PowerSystemResource. The intention is to allow RemotUnits to have Measurements. These Measurements can be used to model unit status as operational, out of service, unit failure etc. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | SCADAVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer |  | cim | An electrical device consisting of two or more coupled windings, with or without a magnetic core, for introducing mutual coupling between electric circuits. Transformers can be used to control voltage and phase shift (MW flow). The typeName attribute indicates type of transformer. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor |  | cim | Combination of conducting material with consistent electrical characteristics, building a single electrical system, used to carry current between points in the power system. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | BusbarSection |  | cim | A conductor, or group of conductors, that serve to connect conducting equipment. Voltage measurements are typically obtained from PTs that are connected to busbar sections. A bus bar section may have one or more terminals. The typeName attribute indicates the type of bus bar section, e.g.: Main, Transfer. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ACLineSegment |  | cim | A wire or combination of wires, with consistent electrical characteristics, building a single electrical system, used to carry alternating current between points in the power system. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Switch |  | cim | A generic device designed to close, or open, or both, one or more electric circuits. The typeName attribute may be used to indicate that the database switch does not represent a corresponding real device but has been introduced for modeling purposes only. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Breaker |  | cim | A mechanical switching device capable of making, carrying, and breaking currents under normal circuit conditions and also making, carrying for a specified time, and breaking currents under specified abnormal circuit conditions e.g. those of short circuit. The typeName is the type of breaker, e.g., oil, air blast, vacuum, SF6. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Disconnector | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A manually operated or motor operated mechanical switching device used for changing the connections in a circuit, or for isolating a circuit or equipment from a source of power. It is required to open or close circuits when negligible current is broken or made. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer |  | cim | Generic user of energy - a point of consumption on the power system model | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | CapacitorBank |  | cim | A shunt capacitor or switchable bank of shunt capacitors. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | DCLineSegment |  | cim | A wire or combination of wires not insulated from one another, with consistent electrical characteristics, used to carry direct current between points in the DC region of the power system. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PhaseShifter |  | cim | A conducting device (e.g., transformer, rotating machine) that advances or retards the voltage phase-angle relationship of one circuit with respect to another | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ReactorBank |  | cim | A shunt switchable bank of reactors. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding |  | cim | A winding is associated with each defined terminal of a transformer (or phase shifter). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ConductorType |  | cim | Wire or cable conductor (per IEEE specs). A specific type of wire or combination of wires not insulated from one another, suitable for carrying electric current. It may be bare or insulated. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger |  | cim | Mechanism for changing transformer winding tap positions. The typeName attribute indicates type of changer, designated as 'Fixed' or 'LTC.' | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | LoadBreakSwitch |  | cim | A mechanical switching device capable of making, carrying, and breaking currents under normal operating conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | MVArCapabilityCurve |  | cim | Describes MVAR limits for the unit over the complete MW range of the unit. The curve values are: x axis - Unit MW output, y1 axis - Minimum MVAR limit, y2 axis - Maximum MVAR limit | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransmissionCorridor | Domain | cim | A corridor containing one or more rights of way. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine |  | cim | An electromechanical device that operates synchronously with the network. It is a single machine operating either as a generator or synchronous condenser or pump. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Feeder | PowerSystemResource; IdentifiedObject | cim | A static collection of conducting equipment originating at a main distribution center and supplying one or more secondary distribution centers, one or more branch-circuit distribution centers, or any combination of these two types of equipment. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RegulatingCondEq | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | RegulatingCondEq is a type of ConductingEquipment that can regulate Measurements and have a RegulationSchedule. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RegulationSchedule |  | cim | A pre-established pattern over time for a controlled variable, e.g., busbar voltage. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | GroundDisconnector | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A manually operated or motor operated mechanical switching device used for isolating a circuit or equipment from Ground. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | CompositeSwitch |  | cim | A model of a set of individual Switches normally enclosed within the same cabinet and possibly with interlocks that restrict the combination of switch positions. These are typically found in medium voltage distribution networks. A CompositeSwitch could represent a Ring-Main-Unit (RMU), or pad-mounted switchgear, with primitive internal devices such as an internal bus-bar plus 3 or 4 internal switches each of which may individually be open or closed. A CompositeSwitch and a set of contained Switches can also be used to represent a multi-position switch e.g. a switch that can connect a circuit to Ground, Open or Busbar. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Connector | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A conductor, or group of conductors, with negligible impedance, that serve to connect other conducting equipment within a single substation and are modelled with a single logical terminal. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource |  | cim | A generic equivalent for an energy supplier on a transmission or distribution voltage level. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Fuse |  | cim | An overcurrent protective device with a circuit opening fusible part that is heated and severed by the passage of overcurrent through it. A fuse is considered a switching device because it breaks current. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Ground | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A common point for connecting grounded conducting equipment such as shunt capacitors. The power system model can have more than one ground. The typeName indicates the type of ground, e.g., mesh, earth rod. It is recommended to use GroundDisconnector instead of Ground class when applying CIM. In case of grounding a shunt compensator use Compensator of type SHUNT. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | HeatExchanger | Equipment; PowerSystemResource; IdentifiedObject | cim | Equipment for the cooling of electrical equipment and the extraction of heat. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Jumper | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A short section of conductor with negligible impedance which can be manually removed and replaced if the circuit is de-energized. Note that zero-impedance branches can be modelled by an ACLineSegment with a zero impedance ConductorType. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Junction | Connector; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A point where one or more conducting equipments are connected with zero resistance. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Line | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A component part of a system extending between adjacent substations or from a substation to an adjacent interconnection point. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter |  | cim | Bi-directional AC-DC conversion equipment that can be used to control DC current, DC voltage, DC power flow, or firing angle. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | StaticVarCompensator |  | cim | A facility for providing variable and controllable shunt reactive power. The SVC typically consists of a stepdown transformer, filter, thyristor-controlled reactor, and thyristor-switched capacitor arms. The SVC may operate in fixed MVar output mode or in voltage control mode. When in voltage control mode, the output of the SVC will be proportional to the deviation of voltage at the controlled bus from the voltage setpoint. The SVC characteristic slope defines the proportion. If the voltage at the controlled bus is equal to the voltage setpoint, the SVC MVar output is zero. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | VoltageControlZone | PowerSystemResource; IdentifiedObject | cim | An area of the power system network which is defined for secondary voltage control purposes. A voltage control zone consists of a collection of substations with a designated bus bar section whose voltage will be controlled. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest |  | cim | Physical winding test data for the winding/tap pairs of a transformer (or phase shifter). This test data can be used to derive other attributes of specific transformer or phase shifter models. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireArrangement |  | cim | Identification, spacing and configuration of the wires of a ConductorType, with reference to their type. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireType |  | cim | Wire conductor (per IEEE specs). A specific type of wire or combination of wires, not insulated from each other, suitable for carrying electrical current. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | FrequencyConverter |  | cim | A device to convert from one frequency to another (e.g., frequency F1 to F2) comprises a pair of FrequencyConverter instances. One converts from F1 to DC, the other converts the DC to F2. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Plant | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A Plant is a collection of equipment for purposes of generation. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ProtectedSwitch | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A ProtectedSwitch is a switching device that can be operated by ProtectionEquipment. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SeriesCompensator |  | cim | A Series Compensator is a series capacitor or reactor or an AC transmission line without charging susceptance. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator |  | cim | A shunt capacitor or reactor or switchable bank of shunt capacitors or reactors. A section of a shunt compensator is an individual capacitor or reactor. Negative values for mVArPerSection and nominalMVAr indicate that the compensator is a reactor. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WiresVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadArea | PowerSystemResource; IdentifiedObject | cim | A Load Area is a subdivision of a network company. Group of loads (i.e., energy consumers). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | AreaLoadCurve | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | A curve relating power versus time. showing the values of a specific load for each unit of the period covered. The curve can be based on 'absolute' time or on 'normalized' time. An instance of this curve could represent the absolute area load forecast. An other instance could represent a normalized daily load curve for a particular day type. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | AreaLossCurve | Curve; IdentifiedObject | cim | The relationship between total area MW losses (Y-axis) and total area MW load (X-axis). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | CustomerLoad | EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A meter for measuring customer energy consumption. The typeName attribute indicates the type of customer meter. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | DayType | IdentifiedObject | cim | Group of similar days, e.g., Mon/Tue/Wed, Thu/Fri, Sat/Sun, Holiday1, Holiday2 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | EquivalentLoad |  | cim | A generic equivalent for an energy consumer on a transmission or distribution voltage level. It may be under load management and also has cold load pick up characteristics. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | InductionMotorLoad |  | cim | Large three phase induction motor load. The typeName attribute indicates the type of induction motor (1 = wound rotor) (2 = squirrel cage). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadDemandModel | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | A curve of load versus time (X-axis) showing the values of MW (Y1-axis) and MVAr (Y2-axis) for each unit of the period covered. This curve represents a typical pattern of load over the time period for a given day type and season. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | NonConformLoadSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | A MW (Y1-axis) and MVAr (Y2-axis) schedule (curves) versus time (X-axis) for non-conforming loads, e.g., large industrial load or power station service (where modeled). The schedule values are: x axis - Hour (1 - 24), y 1 axis - Total MW, y2 axis - Total MVAr, y3 axis - Phase A MW, y4 axis - Phase A MVAr, y5 axis - Phase B MW, y6 axis - Phase B MVAr, y7 axis - Phase C MW, y8 axis - Phase C MVAr | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | PowerCutZone |  | cim | An area or zone of the power system which is used for load shedding purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | Season |  | cim | A specified time period of the year, e.g., Spring, Summer, Fall, Winter. Season Types may be defined with starting and ending month and day. All defined season types must make up one year. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | StationSupply | EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | Station supply. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadModelVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | ConnectivityNode |  | cim | Connectivity nodes are points where terminals of conducting equipment are connected together with zero impedance. | TRUE | FALSE | FALSE | FALSE |  | TRUE
CIMTopology | TopologicalIsland | IdentifiedObject | cim | An electrically connected subset of the network. Topological islands can change as the current network state changes (i.e., disconnect switches, breakers, etc. change state). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode |  | cim | A set of connectivity nodes that, in the current network state, are connected together through closed switches. Topological nodes can change as the current network state changes (i.e., switches, breakers, etc. change state). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologyVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | SynchrocheckRelay |  | cim | A device that operates when two AC circuits are within the desired limits of frequency, phase angle, and voltage, to permit or to cause the paralleling of these two circuits. Used to prevent the paralleling of non-synchronous topological islands. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionEquipment |  | cim | An electrical device designed to respond to input conditions in a prescribed manner and after specified conditions are met to cause contact operation or similar abrupt change in associated electric control circuits, or simply to display the detected condition. Protection equipment are associated with conducting equipment and usually operate circuit breakers. For protection relays, the typeName attribute is a type identifier as specified by IEC 61850 with a Pro_ prefix, e.g. Pro_OVR for overvoltage relay. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | RecloseSequence |  | cim | A reclose sequence (open and close) is defined for each possible reclosure of a breaker. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay |  | cim | A device that checks current flow values in any direction or designated direction. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ControlHouseEquipement |  | cim | Equipment in a substation control house. Covers things such as fire alarms, ambient temperature, door alarms, and spares. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | PSRType | IdentifiedObject | cim | Classifying instances of the same class, e.g. overhead and underground ACLineSegments. This classification mechanism is intended to provide flexibility outside the scope of this standard, i.e. provide customisation that is non standard. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Terminal | IdentifiedObject | cim | An electrical connection point to a piece of conducting equipment. Terminals are connected at physical connection points called 'connectivity nodes'. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Bay |  | cim | A collection of power system resources (within a given substation) including conducting equipment, protection relays, measurements, and telemetry. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | VoltageLevel |  | cim | A collection of equipment at one common system voltage forming a switchgear. The equipment typically consist of breakers, busbars, instrumentation, control, regulationand protection devices as well as assemblies of all these. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Unit | IdentifiedObject | cim | Quantity being measured. The Unit.name shall be unique among all specified quantities and describe the quantity. The Unit.aliasName is meant to be used for localization. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Substation |  | cim | A collection of equipment for purposes other than generation or utilization, through which electric energy in bulk is passed for the purposes of switching or modifying its characteristics. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | PowerSystemResource | IdentifiedObject | cim | A power system resource can be an item of equipment such as a Switch, an EquipmentContainer containing many individual items of equipment such as a Substation, or an organisational entity such as Company or SubControlArea. This provides for the nesting of collections of PowerSystemResources within other PowerSystemResources. For example, a Switch could be a member of a Substation and a Substation could be a member of a division of a Company. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IdentifiedObject |  | cim | This is a root class to provide common naming attributes for all classes needing naming attributes. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | IdentifiedObject
CIMCore | EquipmentContainer | PowerSystemResource; IdentifiedObject | cim | A modeling construct to provide a root class for all Equipment classes. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Equipment |  | cim | The parts of a power system that are physical devices, electronic or mechanical. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | CurveData |  | cim | Data point values for defining a curve or schedule. Note: The DMS NonConformingLoadSchedule has eight y axis values scheduled against the x axis (hour of the day) to describe the total MW and MVAR and the MW and MVAR for each phase. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Curve |  | cim | Relationship between an independent variable (X-axis) and one or two dependent variables (Y1-axis and Y2-axis). Curves can also serve as schedules. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Company |  | cim | A company is a legal entity that owns and operates power system resources and is a party to interchange and transmission contracts. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BasePower |  | cim | The BasePower class defines the base power and base voltages that are used in the per unit calculations. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BaseVoltage |  | cim | Collection of BaseVoltages which is used to verify that the BusbarSection.BaseVoltage and other voltage attributes in the CIM are given a value existing in the collection. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ConductingEquipment |  | cim | The parts of the power system that are designed to carry current or that are conductively connected therewith. ConductingEquipment is contained within an EquipmentContainer that may be a Substation, or a VoltageLevel or a Bay within a Substation. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | SubControlArea |  | cim | An area defined for the purpose of tracking interchange with surrounding areas via tie points; may or may not serve as a control area. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | CoreVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ModelingAuthoritySet | IdentifiedObject | cim | A Modeling Authority Set is a group of objects in a network model where the data is supplied and maintained by the same Modeling Authority. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ModelingAuthority | IdentifiedObject | cim | A Modeling Authority is an entity responsible for supplying and maintaining the data defining a specific set of objects in a network model. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | GeographicalRegion | IdentifiedObject | cim | A geographical region of a power system network model. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | SubGeographicalRegion | IdentifiedObject | cim | A subset of a geographical region of a power system network model. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BasicIntervalSchedule |  | cim | Schedule of values at points in time. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IrregularIntervalSchedule | BasicIntervalSchedule; IdentifiedObject | cim | The schedule has TimePoints where the time between them varies. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularIntervalSchedule |  | cim | The schedule has TimePoints where the time between them is constant. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IrregularTimePoint |  | cim | TimePoints for a schedule where the time between the points varies. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularTimePoint |  | cim | TimePoints for a schedule where the time between the points is constant. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag |  | cim | A clearance tag that is used to authorize and schedule work on conducting equipment in the field. Tagged equipment is not available for commercial service. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | OutageSchedule | IrregularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The period of time that a piece of equipment is out of service, for example, for maintenance or testing; including the equipment's MW rating while under maintenance. The X-axis represents absolute time and the Y-axis represents the equipment's available rating while out of service. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | SwitchingOperation |  | cim | A SwitchingOperation is used to define individual switch operations for an OutageSchedule. This OutageSchedule may be associated with another item of Substation such as a Transformer, Line, or Generator; or with the Switch itself as a PowerSystemResource. A Switch may be referenced by many OutageSchedules. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | OutageVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Control |  | cim | Control is used for supervisory/device control. It represents control outputs that are used to change the state in a process, e.g. close or open breaker, a set point value or a raise lower command. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Control
CIMMeas | ControlType | IdentifiedObject | cim | Specifies the type of Control, e.g. BreakerOn/Off, GeneratorVoltageSetPoint, TieLineFlow etc. The ControlType.name shall be unique among all specified types and describe the type. The ControlType.aliasName is meant to be used for localization. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Limit |  | cim | Specifies one limit value for a Measurement. A Measurement typically has several limits that are kept together by the LimitSet class. The actual meaning and use of a Limit instance (i.e., if it is an alarm or warning limit or if it is a high or low limit) is not captured in the Limit class. However the name of a Limit instance may indicate both meaning and use. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | LimitSet |  | cim | Specifies a set of Limits that are associated with a Measurement. A Measurement may have several LimitSets corresponding to seasonal or other changing conditions. The condition is captured in the name and description attributes. The same LimitSet may be used for several Measurements. In particular percentage limits are used this way. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Measurement |  | cim | A Measurement represents any measured, calculated or non-measured non-calculated quantity. Any piece of equipment may contain Measurements, e.g. a substation may have temperature measurements and door open indications, a transformer may have oil temperature and tank pressure measurements, a bay may contain a number of power flow measurements and a Breaker may contain a switch status measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementType | IdentifiedObject | cim | Specifies the type of Measurement, e.g. IndoorTemperature, OutDoorTemperature, BusVoltage, GeneratorVoltage, LineFlow etc. The MeasurementType.name shall be unique among all specified types and describe the type. The MeasurementType.aliasName is meant to be used for localization. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValue |  | cim | The current state for a measurement. A state value is an instance of a measurement from a specific source. Measurements can be associated with many state values, each representing a different source for the measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValueQuality | Quality61850 | cim | Measurement quality flags. Bits 0-10 are defined for substation automation in draft IEC 61850 part 7-3. Bits 11-15 are reserved for future expansion by that document. Bits 16-31 are reserved for EMS applications. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValueSource | IdentifiedObject | cim | MeasurementValueSource describes the alternative sources updating a MeasurementValue. User conventions for how to use the MeasurementValueSource attributes are described in the introduction to IEC 61970-301. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 |  | cim | Quality flags in this class are as defined in IEC 61850, except for estimatorReplaced, which has been included in this class for convenience. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | ValueAliasSet | IdentifiedObject | cim | Describes the translation of a set of values into a name. Each ValueAliasSet has a name, description etc. A specific Measurement may represent a discrete state like Open, Closed, Intermediate etc. This requires a translation from the MeasurementValue.value number to a string, e.g. 0-]'Invalid', 1-]'Open', 2-]'Closed', 3-]'Intermediate'. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | ValueToAlias |  | cim | Describes the translation of one particular value into a name, e.g. 1-]'Open'. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Analog |  | cim | Analog represents an analog Measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Accumulator |  | cim | Accumulator represents a accumulated (counted) Measurement, e.g. an energy value. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorLimit |  | cim | Limit values for Accumulator measurements. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorLimitSet | LimitSet; IdentifiedObject | cim | An AccumulatorLimitSet specifies a set of Limits that are associated with an Accumulator measurement. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorValue |  | cim | AccumulatorValue represents a accumulated (counted) MeasurementValue. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogLimit |  | cim | Limit values for Analog measurements. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogLimitSet | LimitSet; IdentifiedObject | cim | An AnalogLimitSet specifies a set of Limits that are associated with an Analog measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogValue |  | cim | AnalogValue represents an analog MeasurementValue. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Command |  | cim | A Command is a discrete control used for supervisory control. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Discrete |  | cim | Discrete represents a discrete Measurement, i.e. a Measurement reprsenting discrete values, e.g. a Breaker position. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | DiscreteValue |  | cim | DiscreteValue represents a discrete MeasurementValue. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | SetPoint |  | cim | A SetPoint is an analog control used for supervisory control. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | StringMeasurement | Measurement; IdentifiedObject | cim | StringMeasurement represents a measurement with values of type string. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | StringMeasurementValue |  | cim | StringMeasurementValue represents a measurement value of type string. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMDomain | DomainVersion |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | ServicePoint | Domain | cim | The defined termination points of a transmission path. Service points are defined from the viewpoint of the transmission service. Each service point is contained within (or on the boundary of) an interchange area. CTM - A service point is source or destination of a transaction. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | TransmissionPath | Domain | cim | An electrical connection, link, or line consisting of one or more parallel transmission elements between two areas of the interconnected electric systems, or portions thereof. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | TiePoint | Domain | cim | Site of an interface between interchange areas. The tie point can be a network branch (e.g., transmission line or transformer) or a switching device. For transmission lines, the interchange area boundary is usually at a designated point such as the middle of the line. Line end metering is then corrected for line losses. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | AreaReserveSpec |  | cim | The control area's reserve specification. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | EnergyTransaction |  | cim | Specifies the schedule for energy transfers between interchange areas that are necessary to satisfy the associated interchange transaction. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMFinancial | BusinessUnit | IdentifiedObject | cim | A business unit of a company that operates as an independent entity in interactions with other business units. Though a single company may own more than one kind of business unit, for example a control area operator and a transmission provider, these individual business units deal with each other in the same way that they would deal with business units belonging to different companies. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMFinancial | ControlAreaOperator | BusinessUnit; IdentifiedObject | cim | A business unit that operates a control area. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMFinancial | Marketer | BusinessUnit; IdentifiedObject | cim | Matches buyers and sellers, and secures transmission (and other ancillary services) needed to complete the energy transaction. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMFinancial | TransmissionProvider | BusinessUnit; IdentifiedObject | cim | Provider of the transmission capacity (interconnecting wires between Generation and Consumption) required to fulfill and Energy Transaction's energy exchange. Posts information for transmission paths and AvailableTransmissionCapacities on a reservation node. Buys and sells its products and services on the same reservation node. | FALSE | FALSE | FALSE | FALSE |  | FALSE
EnergyScheduling | HostControlArea |  | spc | A HostControlArea has a set of tie points and a set of generator controls (i.e., AGC). It also has a total load, including transmission and distribution losses. | FALSE | TRUE | TRUE | FALSE |  | FALSE
ETXContingency | ContingencyGroupMember | IdentifiedObject | etx | Used for the many to many relationship between Contigency and ContigencyGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXContingency | ContingencyGroup |  | etx | Used for activation of groups of contingencies. Contingencies can belong to multiple groups. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX | PerformanceModelingGroup | PowerSystemResource; IdentifiedObject | etx | Performance modeling group. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX | QualifiedServiceEntity | PowerSystemResource; IdentifiedObject | etx | Qualified Service Entity | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX | TransmissionServiceProvider | PowerSystemResource; IdentifiedObject | etx | Transmission Service Provider | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | EnergyConsumerAlternateConnection |  | etx | Alternate connection of load. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | LoadGroup | PowerSystemResource; IdentifiedObject | etx | Weatherstation | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | LoadGroupSchedule | PowerSystemResource; IdentifiedObject | etx | Load group schedule | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | LoadZone | PowerSystemResource; IdentifiedObject | etx | Weatherzone | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | AngleDifference | Monitored; IdentifiedObject | etx | The angle difference between two points in the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | AngleDifferenceLimit | AnalogLimit; Limit; IdentifiedObject | etx | A limit on the angle difference. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | AngleDifferenceLimitSet | AnalogLimitSet; LimitSet; IdentifiedObject | etx | Limit set on angle difference. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup |  | etx | Directed sum of terminal flows. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroupTerminal |  | etx | Directed terminal flow to add into BranchGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | Monitored |  | etx | Something that is monitored. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | MonitoredGroup |  | etx | Groups monitored elements. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | VLSBusBarMonitored | Monitored; IdentifiedObject | etx | BusBarSection is monitored. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | VoltageLimit | AnalogLimit; Limit; IdentifiedObject | etx | A voltage limit of a specific level. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | VoltageLimitSet | AnalogLimitSet; LimitSet; IdentifiedObject | etx | Set of potentially shared voltage limits at various levels. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | VoltageMonitored | Monitored; IdentifiedObject | etx | Voltage level is monitored. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass |  | etx | Holds accuracy information for measurement, generation and load schedules. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | PhaseShifterImpedanceCurve | Curve; IdentifiedObject | etx | phase shifter impedance as a function of the phase shifter's angle in degrees. X is the phase shift in degrees, and Y is multiplied by a phase shifter's nominal impedance to get the corrected impedance. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | StationSupplyWRCurve | Curve; IdentifiedObject | etx | StationSupply real and reactive curve on generation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | TransformerImpedanceCurve | Curve; IdentifiedObject | etx | Transformer impedance correction.Model transformer impedance as a function of the LTC tap position in per unit. The data pattern is similar to PhaseShifterImpedanceCurve. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXPlanning | ConnectivityNodeGroup | IdentifiedObject | etx | Group of connectivity node | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXPlanning | PlanningArea | IdentifiedObject | etx | Planning area. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXPlanning | PlanningZone | IdentifiedObject | etx | Planning zone. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate |  | etx | Special protection scheme gate. Evaluates to boolean. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | GateInputPin |  | etx | Input pin for a special protection scheme gate. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinBranchGroup | GateInputPin; IdentifiedObject | etx | Branch flow summation input pin for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinFlow |  | etx | Network solution flow input pin for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinGate | GateInputPin; IdentifiedObject | etx | Input pin that maps to a Gate for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinSwitch | GateInputPin; IdentifiedObject | etx | Input pin that maps to network solution switch status for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinTriggerCondition | GateInputPin; IdentifiedObject | etx | Input pin that maps to a TriggerCondition for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinVoltage | GateInputPin; IdentifiedObject | etx | Input pin that maps to a network voltage for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PrivateProtectiveActions | ProtectiveActions; IdentifiedObject | etx | Protective actions that are private to a RemedialActionScheme trigger condition. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveAction |  | etx | Base class for a protective action for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionAnalog |  | etx | Base class for protective actions that are non-switching. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionEnergyConsumer | ProtectiveActionAnalog; ProtectiveAction; IdentifiedObject | etx | RAS protective action associated with a load instance. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | ProtectActEnergyConsumer
ETXRASE | ProtectiveActions | IdentifiedObject | etx | Base class for RAS protective actions sets. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionShare | ProtectiveAction; IdentifiedObject | etx | Protective action that references a shared protective action. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionsShared | ProtectiveActions; IdentifiedObject | etx | Protective actions that can be shared among triggers. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionStationReduction | ProtectiveActionAnalog; ProtectiveAction; IdentifiedObject | etx | Protective action to reduce station generation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | ProtectActStationReduction
ETXRASE | ProtectiveActionSwitch |  | etx | Protective action to move a switch. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionSynchronousMachine | ProtectiveActionAnalog; ProtectiveAction; IdentifiedObject | etx | Protective action to change output of a synchronous machine. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | ProtectActSynchronousMachine
ETXRASE | RemedialActionScheme |  | etx | Remedial action scheme or special protection scheme. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | SharedProtectiveActions | ProtectiveActions; IdentifiedObject | etx | Protective actions that are shared among RemedialActionScheme trigger conditions. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Stage | IdentifiedObject | etx | State of a remedial action scheme. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | StageTrigger | IdentifiedObject | etx | Condition that is triggered within a stage and has remedial actions. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | TriggerCondition | IdentifiedObject | etx | A set of gates that can trigger remedial actions. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | AnalogLimitType |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | AnalogValueLimit | AnalogValue; MeasurementValue | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | DynamicRatingAnalogValue | AnalogValue; MeasurementValue | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Operator | IdentifiedObject | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OperatorShare |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Owner | IdentifiedObject | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OwnerShare |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OwnerShareRatings | OwnerShare; IdentifiedObject | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Rating |  | etx | Rating set for static or dynamic limits. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRegulation | LoadBasedRegulationCurve | Curve; IdentifiedObject | etx | Curve used to adjust voltage based on system load. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AccumulatorName | IdentifiedObject | etx | A reference table used define valid names for accumulator type measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AccumulatorType | IdentifiedObject | etx | A reference table used to define the types of accumulator measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AlternateLimit |  | etx | specify alternate limits that apply when external conditions. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AlternateLimitSet | IdentifiedObject | etx | Describes a set of alternate limits that apply under the same external condition | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogAlarmCategory | IdentifiedObject | etx | A reference table used to define analog alarm category information for the SCADA subsystem. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogLimitName | IdentifiedObject | etx | A reference table used to define valid Limit names and parameters to be used when defining Limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogMeasMsg |  | etx | Message for analog measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogName | IdentifiedObject | etx | A reference table used to define valid names for analog type measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit |  | etx | used to model SCADA rate of change limits for analog values. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | Calculation | IdentifiedObject | etx | Calculation is a type of MeasurementValueSource. It provides the calculated value for the measurement. The caculation is based on the formula defined in the referenced Function. A Calculation contains multiple CalculationArgument, each referencing a Measurement and assigned to a FunctionArgument. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationArgument | IdentifiedObject | etx | CalculationArgument serves the base class for argument of Calculation. Each CalculationArgument must be assigned to CalculationArgument serves the base class for argument of Calculation. Each CalculationArgument must be assigned to a FunctionArgument. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant |  | etx | used to store seven bits of logical values, one real floating point. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationTriggerTimer | IdentifiedObject | etx | A reference table used to model SCADA calculation trigger timer. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CommandLock | ControlLock; IdentifiedObject | etx | Command Interlock. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CommandName | IdentifiedObject | etx | A reference table used to define valid names for Commands, and their mapping identifiers to the advanced applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ConstantArgument | CalculationArgument; IdentifiedObject | etx | Reference to a ConstatntArgument used in a Calculation as a constant argument. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlEvent |  | etx | Argument of the control sequence. Reverences a command. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlLock |  | etx | Base class for CommandLock and SetPointLock. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlSeq | IdentifiedObject | etx | This class describes a sequence of controls issued in sequence or simulationously. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ConversionTable | IdentifiedObject | etx | specify a method of data conversion for measurements. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | DiscreteAlarmCategory | IdentifiedObject | etx | A reference table used to model SCADA Discrete Alarm Category information. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | DiscreteMeasMsg |  | etx | contains messages with information about the SCADA analog value. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | DiscreteName | IdentifiedObject | etx | A reference table used to define valid states for discrete measurements. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | DiscreteType | IdentifiedObject | etx | A reference tabl used to define parameters for switching devices, such as breakers or disconnects, in the SCADA topology model. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ExceptionListDisplay | IdentifiedObject | etx | Display groups. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | Function | IdentifiedObject | etx | A Function defines a numeric computation formula that can be reused by many Calculations. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | FunctionArgument | IdentifiedObject | etx | FunctionArgument defines the input arguments that are used in the computation defined by Function. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | GenericEquipment | Equipment; PowerSystemResource; IdentifiedObject | etx | A GenericEquipment is an Equipment that is not explicitly modeled in CIM, such as battery. Such equipments may need be modeled in SCADA, since they are tel-measured. A GenericEquipment may also represent a virtual or conceptual entity, such as TIE as modeled as a device in SCADA. Each GenericEquipment must be specified by a GenericEquipmentType. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | GenericEquipmentType | IdentifiedObject | etx | Type of GenericStationEquipment | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | LimitAlarmCategory | IdentifiedObject | etx | A reference table used to define parameters for SCADA limit alarm categories. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementAlias |  | etx | Base class for all types of measurement alias. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementGroup | IdentifiedObject | etx | A MeasurementGroup is a group of related measurements. Not all of Measurements need to be grouped. Only SCADA measurements need to be grouped. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation |  | etx | A MeasurementLocation represents a physical location where a SCADA measurement is located. It could be a Terminal, an Equipment, or TapChanger, etc. Measurements resided in the same MeasurementLocation MUST contain the same association to the PSR or Terminal. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | PermissionArea | IdentifiedObject | etx | A reference table used to define valid areas of responsibility for SCADA measurements. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SCADAConditionAlarm | IdentifiedObject | etx | A reference table used to conditionally issue Discrete and Analog alarms. The Reference Table is linked to a selected Discrete record that is used to dynamically determine whether associated alarms should or should not be issued. Any number of Discrete and Analog records may be associated with the Conditional Alarm Reference entry, and will respond according to the current state of the referenced Discrete measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SCADAHistory | IdentifiedObject | etx | A reference table used to model the required information for saving Analog, Discrete, and Accumulator information in the SCADA Short Term History database. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SetPointLock | ControlLock; IdentifiedObject | etx | Setpoint Interlock. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SetPointName | IdentifiedObject | etx | A reference table used to define Setpoint names and connectivity for switching devices, such as breakers or disconnects, in the SCADA topology model. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | Site | IdentifiedObject | etx | The Sites table is used to define valid SCADA sites, including the local site. Each Point, Analog, and Count record in the model must be associated with a SCADA Site record in this table. Only data retrieved via intersite data will be associated with any site other than the local site name. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SitePermission | IdentifiedObject | etx | Permission of Site | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadType | IdentifiedObject | etx | Shared attributes for a loads of the same type. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ControlZone |  | etx | A control zone with control zone members. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ForbiddenZone |  | etx | A forbidden zone in for operation of the unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType |  | etx | A kind of a fossile fuel. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | GenerationType |  | etx | The type of generation used for totals. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | InadvertentInterchangeDay |  | etx | Day added to inadvertent interchange profile. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | InadvertentInterchgDay
ETX_Areva | InadvertentInterchangeProfile | IdentifiedObject | etx | Inadvertent interchange profile. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | InadvertentInterchgProfile
ETX_Areva | LoadActingAsResource |  | etx | A load acting as a resource | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadReliefLevel |  | etx | A named load relief level for a control area. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementMappingName | IdentifiedObject | etx | mapping name used for measurement type mapping. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage |  | etx | specific usage of a measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsageType | IdentifiedObject | etx | a specific type of measurement usage | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUser | IdentifiedObject | etx | A generic user of measurements via MeasurementUsage. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | PhysicalTiePoint | PowerSystemResource; IdentifiedObject | etx | specific tie point in one control area. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController |  | etx | A plant controller. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | StartGroup |  | etx | A generator startup group. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | TieEnd |  | etx | A group of tie lines terminating in one control area. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_ABB | SyncMachineSchedule | Curve; IdentifiedObject | etx | Curve for representing generator real and reactive power schedules. | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | SwitchSchedule | Curve; IdentifiedObject | etx | Curve for representing breaker schedules. | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | TapSchedule | Curve; IdentifiedObject | etx | Curve to represent tap position schedules. | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | LimitLogicType |  | etx | Limit Logic Type (LLT) can be a special class that defines which limits are to be applied to monitored facilities (i.e., branches and transformers) during nominal contingency configuration. A monitored branch can be associated with up to three different LLTs, corresponding to the DAM and RUC processes. | FALSE | TRUE | FALSE | FALSE |  | FALSE
MarketOperations | Contingency |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE

## Attributes
Package | Class | Attribute | Data Type | Initial Value | Name Space | Documentation | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data | Internal Attribute Name
61970 | iec61970CIMVersion | version | String30 | cim6197011v00 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
61970 | iec61970CIMVersion | date | String30 | 2006-12-18 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMGeneration | GenerationVersion | version | String30 | Generation_v003_02 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMGeneration | GenerationVersion | date | String30 | 2006-10-06 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit | oMCost | CostPerHeatUnit |  | cim | Operating and maintenance cost for the thermal unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit | boilerColdStartEnergy | Float |  | etx | Boiler cold start engergy (MBTU). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit | boilerEfficiency | Float |  | etx | (%) BOILER EFFICIENCY FACTOR. THE HEAT RATE CURVE WILL BE DIVIDED BY THIS FACTOR TO ACCOUNT FOR A DIRTY BOILER OR ANY OTHER CAUSE FOR LOSS OF EFFICIENCY OF THE HEAT CYCLE. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit | turbineColdStartEnergy | Float |  | etx | Turbine cold start energy MBTU (used by UC only). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | HydroGeneratingUnit | hydroUnitWaterCost | Float |  | cim | The equivalent cost of water that drives the hydro turbine, expressed as (dollars/cubic meter). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | HydroUnitWaterCost
CIMProduction | HydroPowerPlant | dischargeTravelDelay | Seconds |  | cim | Water travel delay from tailbay to next downstream hydro power station. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | hydroPlantType | EnumHydroPlantType |  | cim | The type of hydro power plant, e.g.: Run-of-River, Pumped Storage, Major Storage, Minor Storage. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | penstockType | EnumPenstockType |  | cim | Type and configuration of hydro plant penstock(s). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | plantDischargeCapacity | Float |  | cim | Total plant discharge capacity in cubic meters per second. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | plantMWGenRating | ActivePower |  | cim | The hydro plant's generating rating in MW for rated head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | plantMWPumpRating | ActivePower |  | cim | The hydro plant's pumping rating in MW for rated head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | plantRatedHead | Float |  | cim | The plant's rated gross head in meters. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | surgeTankCode | EnumSurgeTankCode |  | cim | A code describing the type (or absence) of surge tank that is associated with the hydro power plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPowerPlant | surgeTankCrestLevel | WaterLevel |  | cim | The level at which the surge tank spills. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | controlDeadband | ActivePower |  | cim | Unit control error deadband. When a unit's desired MW change is less than this deadband, then no control pulses will be sent to the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | controlPulseHigh | Seconds | 0.5 | cim | Pulse high limit which is the largest control pulse that the unit can respond to. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | ControlPulseHigh
CIMProduction | GeneratingUnit | controlPulseLow | Seconds | 0.5 | cim | Pulse low limit which is the smallest control pulse that the unit can respond to. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | ControlPulseLow
CIMProduction | GeneratingUnit | controlResponseRate | PowerROCPerSec | 2 | cim | MW change for a control pulse of one second in the most responsive loading level of the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | efficiency | PU | 1 | cim | The efficiency of the unit in converting mechanical energy, from the prime mover, into electrical energy. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Efficiency
CIMProduction | GeneratingUnit | genControlMode | EnumGeneratorControlMode |  | cim | Select the unit control mode as Setpoint (S) or Pulse (P). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | genControlSource | EnumGeneratorControlSource |  | cim | The source of controls for a generating unit, i.e., Unavailable, Off-AGC, On-AGC, Plant Control. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | governorMPL | PU | 1 | cim | Governor motor position limit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | GovernorMPL
CIMProduction | GeneratingUnit | governorSCD | PerCent | 5 | cim | Governor Speed Changer Droop. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | GovernorSCD
CIMProduction | GeneratingUnit | highControlLimit | ActivePower |  | cim | High limit for secondary (AGC) control. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | initialMW | ActivePower |  | cim | Default generation for use when the operating type is fixed. An entry is required because the unit may later be placed in a fixed operating type mode even though that may not be the initial selection. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | lowControlLimit | ActivePower |  | cim | Low limit for secondary (AGC) control. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumAllowableSpinngReserve | ActivePower |  | cim | Maximum allowable spinning reserve. Spinning reserve will never be considered greater than this value regardless of the current operating point. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | maxAllowableSpinngReserve
CIMProduction | GeneratingUnit | maximumEconomicMW | ActivePower |  | cim | Maximum high economic MW limit, that should not exceed the maximum operating MW limit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | MaximumEconomicMW
CIMProduction | GeneratingUnit | maximumOperatingMW | ActivePower |  | cim | This is the maximum operating MW limit the dispatcher can enter for this unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | MaximumOperatingMW
CIMProduction | GeneratingUnit | minimumEconomicMW | ActivePower | 0 | cim | Low economic MW limit that must be greater than or equal to the minimum operating MW limit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | MinimumEconomicMW
CIMProduction | GeneratingUnit | minimumOperatingMW | ActivePower | 0 | cim | This is the minimum operating MW limit the dispatcher can enter for this unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | MinimumOperatingMW
CIMProduction | GeneratingUnit | modelDetail | Classification | 3 | cim | Detail level of the generator model data. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | ratedGrossMaxMW | ActivePower |  | cim | The unit's gross rated maximum capacity (Book Value). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | ratedGrossMinMW | ActivePower |  | cim | The gross rated minimum generation level which the unit can safely operate at while delivering power to the transmission grid. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | ratedNetMaxMW | ActivePower |  | cim | The net rated maximum capacity determined by subtracting the auxiliary power used to operate the internal plant machinery from the rated gross maximum capacity. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | startupTime | Seconds |  | cim | Time it takes to get the unit on-line, from the time that the prime mover mechanical power is applied. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | autoCntrlMarginMW | ActivePower |  | cim | The planned unused capacity which can be used to support automatic control overruns, in MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | allocSpinResMW | ActivePower |  | cim | The planned unused capacity (spinning reserve) which can be used to support emergency load. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | baseMW | ActivePower |  | cim | For dispatchable units, this value represents the economic MW basepoint, for units that are not dispatchable, this value represents the fixed generation value. The value must be between the operating low and high limits. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | dispReserveFlag | Boolean |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | energyMinMW | HeatPerHour |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | fastStartFlag | Boolean |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | fuelPriority | Priority |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | genOperatingMode | EnumGeneratorOperatingMode | 0 | cim | Operating mode for secondary control, e.g.: Off, Manual, Fixed, LFC, AGC, EDC, RPN, MRN, or REG. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | OperatingMode
CIMProduction | GeneratingUnit | longPF | ParticipationFactor |  | cim | Additional information is not available. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | lowerRampRate | PowerROCPerMin |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | normalPF | ParticipationFactor | 1 | cim | Economic participation factor based on the slope of the unit incremental cost curve at the current operating point of the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | penaltyFactor | PenaltyFactor | 1 | cim | The unit's penalty factor as calculated by the Network Sensitivity function. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | PenaltyFactor
CIMProduction | GeneratingUnit | raiseRampRate | PowerROCPerMin |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | shortPF | ParticipationFactor |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | spinReserveRamp | PowerROCPerMin |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | stepChange | DoubleFloat | 5 | cim | Unit allowable step change which specifies the maximum stored energy in the boiler. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | StepChange
CIMProduction | GeneratingUnit | tieLinePF | ParticipationFactor | 1 | cim | Unit frequency and tie-line regulation participation factor. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | minimumOffTime | Seconds |  | cim | Minimum time interval between unit shutdown and startup. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | ratedNetMaxMW | DoubleFloat | 100 | cim | The net rated maximum capacity determined by subtracting the auxiliary power used to operate the internal plant machinery from the rated gross maximum capacity. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | RatedNetMaxMW
CIMProduction | GeneratingUnit | RatedNetMinMW | DoubleFloat | 0 | cim | The net rated minimum capacity determined by subtracting the auxiliary power used to operate the internal plant machinery from the rated gross minimum capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumEconomicMWRef | Float |  | etx | Maximum economic dispatch reference value. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | alarmThresholdHourlyMWH | Float |  | etx | Alarm threshold limit at end of hour. (MWH). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | minimumEmergencyMW | Float |  | etx | Emergency capacity minimum (Operator enterable). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumEmergencyMW | Float |  | etx | Emergency capaciity maximum (Operating enterable). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumCurrentCapacity | Float |  | etx | (MW) DEFAULT CURRENT MAX CAPACITY. OPERATOR ENTERABLE. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumCurrentCapacityRef | Float |  | etx | (MW) Reference value for Advisory ECO maximum. Entered in modeling. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | minimumEconomicMWOper | Float |  | etx | (MW) DEFAULT CURRENT ECONOMIC MIN LIMIT. OPERATOR ENTERABLE. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | minimumEconomicMWRef | Float |  | etx | (MW) Reference value for ECO minimum. Entered in modeling. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumEconomicMWOper | Float |  | etx | (MW) DEFAULT CURRENT ECONOMIC MAX LIMIT. OPERATOR ENTERABLE. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | minimumSecurityMW | Float |  | etx | (MW) ECO MIN as determiend by Security Constrained dispatch. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumSecurityMW | Float |  | etx | (MW) ECO MAX as determiend by Security Constrained dispatch. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | frequencyDeadBandHz | Float |  | etx | Allowable deviation of the unit frequency. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | lowControlLimitRef | Float |  | etx | LFC min limit. Reference value. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | highControlLimitRef | Float |  | etx | LFC max limit. Reference value. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maintenanceCostPerHour | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maintenanceCostPerMWHour | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maintenanceStartCost | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | minimumUpTime | Float |  | etx | Minium up time, synchronoization to off-line (seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maxBasepointCarryOver | Float |  | etx | Maximum basepoint cary over from end of hour to next. MWH. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | alarmLimitDeadBand | Float |  | etx | Unit limit alarms deadband (% of alarm limit) (EG: 1%) (AGC only). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | percentCapOff | Float |  | etx | Percent of unit capacitity for which unit is considered offline. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumPumpOperatingReserve | Float |  | etx | (MW) Maximum allowedable operating reserve from this unit when in the pumping mode. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | pumpThreshold | Float |  | etx | (MW) Threshold test if unit is in pump back mode. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | energyRecoveryFactor | Float |  | etx | Factor of 60 means energy mismatch is made up over the next 60 minutes. (Minutes). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumShortTermDownMW | Float |  | etx | Maximum change in MW at short term ramp rate down. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | maximumShortTermUpMW | Float |  | etx | Maximum change in MW at short term ramp rate up. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | lowerRampRateNom | Float |  | etx | Default ramp rate in down direction MW/MIN. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | raiseRampRateNom | Float |  | etx | Default ramp rate in up direction MW/MIN. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | spinningReserveMax | Float |  | etx | Max spinning reserve from this unit. Usuallly derived from response rate. Applicable only to non-peakers. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | scrubCO2 | Float |  | etx | Percent of CO2 out scribbed out. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | scrubNOX | Float |  | etx | Percent of NOX out scrubbed out by unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | thresholdSynchronousCondenserMW | Float |  | etx | (MW) Threshold to test if unit is in synchronous condenser mode. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | thresholdSynchCondenserMW
CIMProduction | GeneratingUnit | startEnergy | Float |  | etx | Start up energy in MBTU's. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | scrubSO2 | Float |  | etx | Percent of SO2 out scrubbed out by unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | startRampRate | Float |  | etx | MW/HR ramp rate from scychronization to ED minimum (UC only). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | thresholdSynchronousCondenserMVAR | Float |  | etx | (MVAR) threshold to test if unit is in synchronous condenser mode. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | thresholdSynchCondenserMVAR
CIMProduction | GeneratingUnit | spinningReserveMaxSyncCond | Float |  | etx | (MW) Max spinning reserve from this unit when in sychronous condensor mode. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | offlineDeadbandPercentage | Float |  | etx | Unit online threshold percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | windupDownMax | Float |  | etx | (MW) Unit windup limit in the down drection is generation output minus this parameter. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | windupUpMax | Float |  | etx | (MW) Unit windup limit in the up direction is this parameter plus generation output. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | CombinedCyclePlant | combCyclePlantRating | ActivePower |  | cim | The combined cycle plant's output rating, in MW | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CogenerationPlant | cogenHPSendoutRating | Float |  | cim | The high pressure steam sendout, in klb/hour | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CogenerationPlant | cogenHPSteamRating | Float |  | cim | The high pressure steam rating, in psi | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CogenerationPlant | cogenLPSendoutRating | Float |  | cim | The low pressure steam sendout, in klb/hour | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CogenerationPlant | cogenLPSteamRating | Float |  | cim | The low pressure steam rating, in psi | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CogenerationPlant | cogenPlantMWRating | ActivePower |  | cim | The rated output MW of the cogeneration plant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | activeStorageCapacity | Volume |  | cim | Storage volume (in Mm3) between the full supply level and the normal minimum operating level. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | energyStorageRating | Float |  | cim | The reservoir's energy storage rating in MWh for given head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | fullSupplyLevel | WaterLevel |  | cim | Full supply level, above which water will spill. This can be the spillway crest level or the top of closed gates. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | grossCapacity | Volume |  | cim | Total capacity of reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | normalMinOperateLevel | WaterLevel |  | cim | Normal minimum operating level below which the penstocks will draw air. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | riverOutletWorks | String100 |  | cim | River outlet works for riparian right releases or other purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | spillTravelDelay | Seconds |  | cim | The spillway water travel delay to the next downstream reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | spillwayCapacity | Float |  | cim | The flow capacity of the spillway in cubic meters per second. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | spillwayCrestLength | Float |  | cim | The length of the spillway crest in meters. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | spillwayCrestLevel | WaterLevel |  | cim | Spillway crest level above which water will spill. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | spillWayGateType | EnumSpillwayGateType |  | cim | Type of spillway gate, including parameters. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | TargetLevelSchedule | highLevelLimit | WaterLevel |  | cim | High target level limit, above which the reservoir operation will be penalized. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | TargetLevelSchedule | lowLevelLimit | WaterLevel |  | cim | Low target level limit, below which the reservoir operation will be penalized. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | fixedMaintCost | CostPerHour |  | cim | Fixed Maintenance Cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | hotStandbyHeat | HeatPerHour |  | cim | The amount of heat input per hour required for hot standby operation. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | incrementalMaintCost | CostPerEnergyUnit |  | cim | Incremental Maintenance Cost | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | minimumDownTime | Hours |  | cim | The minimum number of hours the unit must be down before restart. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | minimumRunTime | Hours |  | cim | The minimum number of hours the unit must be operating before being allowed to shut down. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | riskFactorCost | Money |  | cim | The opportunity cost associated with the return in dollars. This represents the restart's 'share' of the unit depreciation and risk of an event which would damage the unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | startupCost | Money |  | cim | Total miscellaneous start up costs. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | startupDate | AbsoluteDateTime |  | cim | The date and time of the most recent generating unit startup. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | startupPriority | Priority |  | cim | Startup priority within control area where lower numbers indicate higher priorities. More than one unit in an area may be assigned the same priority. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | stbyAuxPowerMW | ActivePower |  | cim | The unit's auxiliary power consumption to maintain standby mode. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | AirCompressor | airCompressorRating | Float |  | cim | Rating of the CAES air compressor. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CAESPlant | energyStorageCapacity | EnergyAsMWh |  | cim | The rated energy storage capacity in megawatt-hours. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | CAESPlant | ratedCapacityMW | ActivePower |  | cim | The CAES plant's gross rated generating capacity in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionAccount | emissionType | EnumEmissionType |  | cim | The type of emission, for example sulfur dioxide (SO2). The y1AxisUnits of the curve contains the unit of measure (e.g. kg) and the emissionType is the type of emission (e.g. sulfer dioxide). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionAccount | emissionValueSource | EnumEmissionValueSource |  | cim | The source of the emission value: Measured or Calculated. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionCurve | emissionContent | Emission |  | cim | The emission content per quantity of fuel burned. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionCurve | emissionType | EnumEmissionType |  | cim | The type of emission, which also gives the production rate measurement unit. The y1AxisUnits of the curve contains the unit of measure (e.g. kg) and the emissionType is the type of emission (e.g. sulfer dioxide). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionCurve | netGrossMWFlag | Boolean |  | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fossilFuelType | EnumFuelType |  | cim | The type of fossil fuel, such as coal, oil, or gas. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fuelCost | CostPerHeatUnit |  | cim | The cost in terms of heat value for the given type of fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fuelDispatchCost | CostPerHeatUnit |  | cim | The cost of fuel used for economic dispatching which includes: fuel cost, transportation cost, and incremental maintenance cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fuelEffFactor | PU |  | cim | The efficiency factor for the fuel (per unit) in terms of the effective MBtu absorbed. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fuelHandlingCosgt | CostPerHeatUnit |  | cim | Handling and processing cost associated with this fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fuelHeatContent | Float |  | cim | The amount of heat (Btu) per weight (or volume) of the given type of fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fuelMixture | PerCent |  | cim | The amount in percent of the given type of fuel , when multiple fuels are being consumed. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | fuelSulfur | PU |  | cim | The fuel's fraction of pollution credit per unit of heat content (MBtu). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | highMWBreakpoint | ActivePower |  | cim | The MW output level of the unit at which the given type of fuel is switched on. This fuel (e.g., oil) is sometimes used to supplement the base fuel (e.g., coal) at high MW output levels. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | lowMWBreakpoint | ActivePower |  | cim | The MW output level of the unit at which the given type of fuel is switched off. This fuel (e.g., oil) is sometimes used to stabilize the base fuel (e.g., coal) at low MW output levels. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule | fuelAllocationEndDate | AbsoluteDateTime |  | cim | The end time and date of the fuel allocation schedule. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule | fuelAllocationStartDate | AbsoluteDateTime |  | cim | The start time and date of the fuel allocation schedule. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule | fuelType | EnumFuelType |  | cim | The type of fuel, which also indicates the corresponding measurement unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule | maxFuelAllocation | Float |  | cim | The maximum amount fuel that is allocated for consumption for the scheduled time period. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule | minFuelAllocation | Float |  | cim | The minimum amount fuel that is allocated for consumption for the scheduled time period, e.g., based on a 'take-or-pay' contract. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GenUnitOpCostCurve | netGrossMWFlag | Boolean |  | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatInputCurve | auxPowerOffset | ActivePower |  | cim | Power output - auxiliary power offset adjustment factor in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatInputCurve | auxPowerMult | PU |  | cim | Power output - auxiliary power multiplier adjustment factor in per unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatInputCurve | heatInputEff | PU |  | cim | Heat input - efficiency multiplier adjustment factor in per unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatInputCurve | heatInputOffset | HeatPerHour |  | cim | Heat input - offset adjustment factor in MBtu/hr. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatInputCurve | netGrossMWFlag | Boolean |  | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatRateCurve | netGrossMWFlag | Boolean |  | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatRateCurve | baseHeat | Float |  | etx | (MBTU/HR) The amount of heat required at first MW point to maintain synchronization. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | HydroPump | pumpDischAtMaxHead | Float |  | cim | The pumping discharge (m3/sec) under maximum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPump | pumpDischAtMinHead | Float |  | cim | The pumping discharge (m3/sec) under minimum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPump | pumpPowerAtMaxHead | ActivePower |  | cim | The pumping power (MW) under maximum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPump | pumpPowerAtMinHead | ActivePower |  | cim | The pumping power (MW) under minimum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | IncrementalHeatRateCurve | netGrossMWFlag | Boolean |  | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ShutdownCurve | shutdownCost | Money |  | cim | Fixed shutdown cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ShutdownCurve | shutdownDate | AbsoluteDateTime |  | cim | The date and time of the most recent generating unit shutdown. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartIgnFuelCurve | ignitionFuelType | EnumFuelType |  | cim | Type of ignition fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartMainFuelCurve | mainFuelType | EnumFuelType |  | cim | Type of main fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartRampCurve | hotStandbyRamp | PowerROCPerMin |  | cim | The startup ramp rate in gross MW/minute for a unit that is on hot standby. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PrimeMover | primeMoverRating | Float |  | cim | Rating of prime mover. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | ambientTemp | Temperature | 15 | cim | Default ambient temperature to be used in modeling applications | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | auxPowerVersusFrequency | PowerVersusFrequency |  | cim | Off-nominal frequency effect on turbine auxiliaries. Per unit reduction in auxiliary MW consumption versus per unit reduction in frequency (from rated frequency). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | auxPowerVersusVoltage | PowerVersusVoltage |  | cim | Off-nominal voltage effect on turbine auxiliaries. Per unit reduction in auxiliary MW consumption versus per unit reduction in auxiliary bus voltage (from a specified voltage level). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | capabiltiyVersusFrequency | PowerVersusFrequency |  | cim | Off-nominal frequency effect on turbine capability. Per unit reduction in unit MW capability versus per unit reduction in frequency (from rated frequency). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | heatRecoveryFlag | Bool |  | cim | Flag that is set to true if the combustion turbine is associated with a heat recovery boiler | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | powerVariationByTemp | PU | 0.11 | cim | Per unit change in power per (versus) unit change in ambient temperature | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | referenceTemp | Temperature | 15 | cim | Reference temperature at which the output of the turbine was defined. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | timeConstant | Seconds | 0.25 | cim | The time constant for the turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamSupply | steamSupplyRating | Float |  | cim | Rating of steam supply. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | crossoverTC | Seconds | 0 | cim | Crossover Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | reheater1TC | Seconds | 8 | cim | First Reheater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | reheater2TC | Seconds | 0 | cim | Second Reheater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft1PowerHP | Fraction | 0.3 | cim | Fraction Of Power From Shaft 1 High Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft1PowerIP | Fraction | 0.7 | cim | Fraction Of Power From Shaft 1 Intermediate Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft1PowerLP1 | Fraction | 0 | cim | Fraction Of Power From Shaft 1 First Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft1PowerLP2 | Fraction | 0 | cim | Fraction Of Power From Shaft 1 Second Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft2PowerHP | Fraction |  | cim | Fraction Of Power From Shaft 2 High Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft2PowerIP | Fraction | 0 | cim | Fraction Of Power From Shaft 2 Intermediate Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft2PowerLP1 | Fraction | 0 | cim | Fraction Of Power From Shaft 2 First Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | shaft2PowerLP2 | Fraction | 0 | cim | Fraction Of Power From Shaft 2 Second Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamTurbine | steamChestTC | Seconds | 0 | cim | Steam Chest Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | gateRateLimit | RateOfChange |  | cim | Gate Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | gateUpperLimit | PU |  | cim | Gate Upper Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | maxEffMWatMinHead | ActivePower |  | cim | Maximum efficiency MW at minimum head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | maxEffMWatMaxHead | ActivePower |  | cim | Maximum efficiency MW at maximum head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | speedRating | Integer |  | cim | Rated speed in revolutions per minute. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | speedRegulation | PU |  | cim | Speed Regulation | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | transientDroopTime | Seconds | 64 | cim | Transient Droop Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | transientRegulation | PU | 0.125 | cim | Transient Regulation | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | turbineRating | ActivePower |  | cim | Rated turbine power in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | turbineType | EnumTurbineType |  | cim | Type of turbine, e.g.: Francis, Pelton, Kaplan. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HydroTurbine | waterStartingTime | Seconds | 2 | cim | Water Starting Time | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | ControllC | DoubleFloat | 0 | cim | Integral Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | controlMWEB | DoubleFloat |  | cim | MW Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | controlPC | DoubleFloat |  | cim | Proportional Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | controlPEB | DoubleFloat |  | cim | Pressure Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | controlPED | DoubleFloat |  | cim | Pressure Error Deadband | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | controlTC | DoubleFloat | 175 | cim | Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | feedWaterIG | DoubleFloat | 0.0214 | cim | Feedwater Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | feedWaterPG | DoubleFloat | 0.9881 | cim | Feedwater Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | feedWaterTC | DoubleFloat | 20 | cim | Feedwater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | pressureCtrlDG | DoubleFloat | 44 | cim | Pressure Control Derivative Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | pressureCtrlIG | DoubleFloat | 0.115 | cim | Pressure Control Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | superHeater1Capacity | DoubleFloat | 6.59 | cim | Drum/Primary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | superHeater2Capacity | DoubleFloat | 3.86 | cim | Secondary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Supercritical | superHeaterPipePD | DoubleFloat | 13.25 | cim | Superheater Pipe Pressure Drop Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | ControllC | DoubleFloat |  | cim | Integral Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | controlMWEB | DoubleFloat |  | cim | MW Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | controlPC | DoubleFloat |  | cim | Proportional Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | controlPEB | DoubleFloat |  | cim | Pressure Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | controlPED | DoubleFloat |  | cim | Pressure Error Deadband | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | controlTC | DoubleFloat | 200 | cim | Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | feedWaterIG | DoubleFloat | 0.0214 | cim | Feedwater Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | feedWaterPG | DoubleFloat | 0.45 | cim | Feedwater Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | feedWaterTC | DoubleFloat | 20 | cim | Feedwater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | pressureCtrlDG | DoubleFloat | 44 | cim | Pressure Control Derivative Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | pressureCtrlIG | DoubleFloat | 0.03 | cim | Pressure Control Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | superHeater1Capacity | DoubleFloat | 27 | cim | Drum/Primary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | superHeater2Capacity | DoubleFloat | 6 | cim | Secondary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | Subcritical | superHeaterPipePD | DoubleFloat | 6.11 | cim | Superheater Pipe Pressure Drop Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | drumBoilerRating | DoubleFloat |  | cim | Rating of drum boiler in steam units. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | ControllC | DoubleFloat | 0 | cim | Integral Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | controlMWEB | DoubleFloat | 0 | cim | MW Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | controlPC | DoubleFloat |  | cim | Proportional Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | controlPEB | DoubleFloat | 0 | cim | Pressure Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | controlPED | DoubleFloat | 0 | cim | Pressure Error Deadband | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | controlTC | DoubleFloat | 100 | cim | Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | fuelSupplyDelay | DoubleFloat | 9 | cim | Fuel Delay | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | fuelSupplyTC | DoubleFloat | 6 | cim | Fuel Supply Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | pressureCtrlDG | DoubleFloat | 40 | cim | Pressure Control Derivative Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | pressureCtrlIG | DoubleFloat | 0.015 | cim | Pressure Control Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | pressureCtrlPG | DoubleFloat | 0.9 | cim | Pressure Control Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | superHeater1Capacity | DoubleFloat | 25.6 | cim | Drum/Primary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | superHeater2Capacity | DoubleFloat | 11.12 | cim | Secondary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | DrumBoiler | superHeaterPipePD | DoubleFloat | 11.4 | cim | Superheater Pipe Pressure Drop Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | auxPowerVersusFrequency | PowerVersusFrequency |  | cim | Off nominal frequency effect on auxiliary real power. Per unit MW variation versus per unit frequency variation. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | auxPowerVersusVoltage | PowerVersusVoltage |  | cim | Off nominal voltage effect on auxiliary real power. Per unit MW variation versus per unit kV variation. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | controlIC | Float |  | cim | Integral Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | boilerControlMode | EnumBoilerControlMode |  | cim | The control mode of the boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | controlMWEB | Ratio |  | cim | MW Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | controlPC | Float |  | cim | Proportional Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | controlPEB | Ratio |  | cim | Pressure Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | controlPED | PU |  | cim | Pressure Error Deadband | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | controlTC | Float |  | cim | Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | feedWaterIG | Ratio |  | cim | Feedwater Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | feedWaterPG | Ratio |  | cim | Feedwater Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | feedWaterTC | Seconds |  | cim | Feedwater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | fuelDemandLimit | DoubleFloat | 1 | cim | Fuel Demand Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | fuelSupplyDelay | Seconds |  | cim | Fuel Delay | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | mechPowerSensorLag | DoubleFloat | 1 | cim | Mechanical Power Sensor Lag | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | fuelSupplyTC | Seconds |  | cim | Fuel Supply Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | mWMaximumER | RateOfChange | 0.13 | cim | MW Maximum Error Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | mWMinimumER | RateOfChange | -0.13 | cim | MW Minimum Error Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | pressureCtrlDG | Ratio |  | cim | Pressure Control Derivative Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | pressureCtrlG | Ratio |  | cim | Pressure Control Integratl Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | pressureCtrlPG | Ratio |  | cim | Pressure Control Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | pressureFeedback | LongInt | 1 | cim | Pressure Feedback Indicator | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | superHeater1Capacity | Float |  | cim | Drum/Primary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | superHeater2Capacity | Float |  | cim | Secondary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | superHeaterPipePD | Float |  | cim | Superheater Pipe Pressure Drop Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | FossilSteamSupply | throttlePressureSP | PU | 1 | cim | Throttle Pressure Setpoint | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coldLegFBLagTC | PU | 4.065 | cim | Cold Leg Feedback Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coldLegFBLeadTC1 | PU | 3.56 | cim | Cold Leg Feedback Lead Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coldLegFBLeadTC2 | PU | 3.94 | cim | Cold Leg Feedback Lead Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coldLegFG1 | PU | 8.05 | cim | Cold Leg Feedback Gain 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coldLegFG2 | PU | 0.974 | cim | Cold Leg Feedback Gain 2 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coldLegLagTC | PU | 4.67 | cim | Cold Leg Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coreHTLagTC1 | PU | 2.105 | cim | Core Heat Transfer Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coreHTLagTC2 | PU | 20.835 | cim | Core Heat Transfer Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coreNeutronicsEffTC | PU | 12.195 | cim | Core Neutronics Effective Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | coreNeutronicsHT | PU | 0.032 | cim | Core Neutronics And Heat Transfer | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | feedbackFactor | PU | 7.25 | cim | Feedback Factor | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | hotLegLagTC | PU | 3.19 | cim | Hot Leg Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | hotLegSteamGain | PU | 1.3 | cim | Hot Leg Steam Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | hotLegToColdLegGain | PU | 0.397 | cim | Hot Leg To Cold Leg Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | pressureCG | PU | 0.75 | cim | Pressure Control Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | steamFlowFG | PU | 0.54 | cim | Steam Flow Feedback Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | steamPressureDropLagTC | PU | 1.56 | cim | Steam Pressure Drop Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | steamPressureFG | PU | 1 | cim | Steam Pressure Feedback Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | throttlePressureFactor | PU | 0.613 | cim | Throttle Pressure Factor | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | PWRSteamSupply | throttlePressureSP | PU | 1 | cim | Throttle Pressure Setpoint | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | highPowerLimit | PU | 0.1 | cim | High Power Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | inCoreThermalTC | Seconds | 10.9 | cim | In-Core Thermal Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | integralGain | RateOfChange | 0.386 | cim | Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | lowerLimit | PU | 0.56 | cim | Initial Lower Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | lowPowerLimit | PU | 0.1 | cim | Low Power Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | pressureLimit | PU | 0.09 | cim | Pressure Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | pressureSetpointGA | DoubleFloat | 0.222 | cim | Pressure Setpoint Gain Adjuster | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | pressureSetpointTC1 | Seconds | 9 | cim | Pressure Setpoint Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | pressureSetpointTC2 | Seconds | 3 | cim | Pressure Setpoint Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | proportionalGain | DoubleFloat | 0 | cim | Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux1 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux2 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux3 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux4 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux5 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux6 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux7 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rfAux8 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | rodPatternConstant | DoubleFloat | 0.32 | cim | Constant Associated With Rod Pattern | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | BWRSteamSupply | upperLimit | PU | 1.05 | cim | Initial Upper Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CTTEMPMWCurve | temperatureUnits | EnumTemperatureUnits |  | cim | The temperature units (C or F). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | HeatRecoveryBoiler | steamSupplyRating2 | Float |  | cim | The steam supply rating in kilopounds per hour, if dual pressure boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteControl | remoteControlled | Boolean |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteControl | actuatorMaximum | Float |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteControl | actuatorMinimum | Float |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteSource | sensorMaximum | Float |  | cim | The maximum value the telemetry item can return. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteSource | sensorMinimum | Float |  | cim | The minimum value the telemetry item can return. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteSource | scanInterval | Seconds |  | cim | The time interval between scans. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteSource | deadband | Float |  | cim | The smallest change in value to be reported. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteUnit | remoteUnitType | EnumRemoteUnitType |  | cim | A remote unit can be a RTU, IED, substation control system, control center etc. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | SCADAVersion | version | String30 | SCADA_v002_02 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | SCADAVersion | date | String30 | 2004-09-04 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer | bmagSat | PerCent |  | cim | Core shunt magnetizing susceptance in the saturation region, in per cent. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer | magBaseKV | Voltage |  | cim | The reference voltage at which the magnetizing saturation measurements were made. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer | magSatFlux | PerCent |  | cim | Core magnetizing saturation curve knee flux level. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer | phases | PhaseCode | 1 | cim | Describes the phases carried by a power transformer. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer | transfCoolingType | EnumTransformerCoolingType |  | cim | Type of transformer cooling. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer | transformerType | EnumTransformerType |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PowerTransformer | AVR | Boolean |  | etx | T=Automatic Voltage Regulation is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | Conductor | b0ch | Susceptance |  | cim | Zero sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | bch | Susceptance |  | cim | Positive sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | g0ch | Conductance |  | cim | Zero sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | gch | Conductance |  | cim | Positive sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | length | LongLength |  | cim | Segment length for calculating line section capabilities (long length units). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | r | Resistance |  | cim | Positive sequence series resistance of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | r0 | Resistance |  | cim | Zero sequence series resistance of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | x | Reactance |  | cim | Positive sequence series reactance of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | x0 | Reactance |  | cim | Zero sequence series reactance of the entire line section. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | r_pu | DoubleFloat |  | cim | Positive sequence resistance in per unit on a 100 MVA base. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | x_pu | DoubleFloat |  | cim | Positive sequence reactance in per unit on a 100 MVA base. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | bch_pu | DoubleFloat |  | cim | Positive sequence shunt (charging) susceptance in per unit on a 100 MVA base | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | BusbarSection | baseVoltage | DoubleFloat |  | cim | Nominal voltage | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ACLineSegment | seriesDevice | Boolean |  | etx | The device is actually a serices device. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | Switch | normalOpen | Boolean | FALSE | cim | The attribute is used in cases when no Measurement for the status value is present. If the Switch has a status measurment the Measurement.normalValue is expected to match with the Switch.normalOpen. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Switch | switchOnCount | Counter |  | cim | The switch on count since the switch was last reset or initialized. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Switch | switchOnDate | AbsoluteDateTime |  | cim | The date and time when the switch was last switched on. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Breaker | ampRating | CurrentFlow |  | cim | Fault interrupting rating in amperes. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Breaker | InTransitTime | Seconds | 0 | cim | The transition time from open to close, in seconds. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | conformingLoadFlag | Boolean | TRUE | cim | Flag is set to YES if the load is conforming, i.e., tracks the area load to which the energy consumer belongs. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | customerCount | Counter |  | cim | Number of individual customers represented by this Demand. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | pFexp | Exponent |  | cim | Exponent of per unit frequency effecting real power. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | pfixed | ActivePower |  | cim | Real component of the load that is a fixed quantity, MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | pfixedPct | PerCent |  | cim | Fixed MW as per cent of load area fixed MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | pnom | ActivePower |  | cim | Nominal value for real power, MW. Nominal real power is adjusted according to the load profile selected for the consumer. It equates to one per unit in the load profile. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | pnomPct | PerCent |  | cim | Nominal MW as per cent of load group nominal MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | powerFactor | PowerFactor |  | cim | Power factor for nominal portion of load. Defined as MW/MVA. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | pVexp | Exponent |  | cim | Exponent of per unit voltage effecting real power. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | qFexp | Exponent |  | cim | Exponent of per unit frequency effecting reactive power | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | qfixed | ReactivePower |  | cim | Reactive component of the load that is a fixed quantity, MVAr. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | qfixedPct | PerCent |  | cim | Fixed MVAr as per cent of load area fixed MVAr. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | qnom | ReactivePower |  | cim | Nominal value for reactive power, MVAr. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | qnomPct | PerCent |  | cim | Nominal MVAr as per cent of load group nominal MVAr. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | qVexp | Exponent |  | cim | Exponent of per unit voltage effecting reactive power. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | MWMax | Float |  | etx | Maximum REAL POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | EnergyConsumer | MWMin | Float |  | etx | MINIMUM REAL POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | EnergyConsumer | MVARMax | Float |  | etx | Maximum Reactive POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | EnergyConsumer | MVARMin | Float |  | etx | MINIMUM Reative POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | CapacitorBank | MaximumkV | DoubleFloat |  | cim | The maximum voltage at which the capacitor bank should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | CapacitorBank | maximumSections | LongInt | 1 | cim | For a capacitor bank, the maximum number of sections that may be switched in. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | CapacitorBank | MinimumkV | DoubleFloat |  | cim | The minimum voltage at which the capacitor bank should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | CapacitorBank | nominalMVAr | DoubleFloat |  | cim | Nominal MVAr output of the capacitor bank at the nominal kV. This number should be positive. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | CapacitorBank | normalSections | LongInt | 1 | cim | For a capacitor bank, the normal number of sections switched in. This number should correspond to the Nominal MVAr. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | DCLineSegment | dcSegmentInductance | Inductance |  | cim | Inductance of the DC line segment, in millihenries. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | DCLineSegment | dcSegmentResistance | Resistance |  | cim | Resistance of the DC line segment, in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PhaseShifter | r | DoubleFloat |  | cim | Phase Shifter resistance | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PhaseShifter | x | DoubleFloat |  | cim | Phase Shifter reactance | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PhaseShifter | maximumAdvanceAngle | DoubleFloat |  | cim | Maximum phase angle in the advance direction | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PhaseShifter | maximumRetardAngle | DoubleFloat |  | cim | Maximum phase angle in the retard direction | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | PhaseShifter | StepSize | DoubleFloat |  | cim | Phase shifter tap step increment, in degrees per step | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ReactorBank | maximumkV | DoubleFloat |  | cim | The maximum voltage at which the reactor bank should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ReactorBank | maximumSections | LongInt | 1 | cim | For a reactor bank, the maximum number of sections that can be switched in. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ReactorBank | minimumkV | DoubleFloat |  | cim | The minimum voltage at which the reactor bank should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ReactorBank | nominalMVAr | DoubleFloat |  | cim | Nominal MVAr installed capacity of the reactor bank. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ReactorBank | normalSections | LongInt | 1 | cim | For a reactor bank, the normal number of sections switched in. The number should correspond to the nominal MVAr. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ReactorBank | yPerSection | DoubleFloat |  | cim | For a reactor bank, the admittance of each switchable section. Calculated using the MVAr per section and corrected for network voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | b | Susceptance |  | cim | Magnetizing branch susceptance (B mag). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | insulationKV | Voltage |  | cim | Basic insulation level voltage rating. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | connectionType | EnumWindingConnection | 1 | cim | The type of connection of the winding (e.g. Delta, Wye, zigzag). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | emergencyMVA | ApparentPower | 99999 | cim | The MVA that the winding can carry under emergency conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | g | Conductance | 0 | cim | Magnetizing branch conductance (G mag). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | grounded | Boolean | TRUE | cim | Set if the winding is grounded. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | r | Resistance |  | cim | Positive sequence series resistance of the winding. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | r0 | Resistance |  | cim | Zero sequence series resistance of the winding. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | ratedKV | Voltage |  | cim | The rated voltage (phase-to-ground) of the winding, usually the same as the neutral voltage. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | ratedMVA | ApparentPower | 99999 | cim | The normal rating, in MVA, for the winding. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | rground | Resistance | 0 | cim | Ground resistance path through connected grounding transformer. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | shortTermMVA | DoubleFloat | 99999 | cim | MVA that the winding can carry for a short period of time. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | windingType | EnumWindingType |  | cim | The type of winding, i.e., Primary, Secondary, Tertiary, Quaternary. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | x | Reactance |  | cim | Positive sequence series reactance of the winding. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | x0 | Reactance |  | cim | Zero sequence series reactance of the winding. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | xground | Reactance | 0 | cim | Ground reactance path through connected grounding transformer. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | r_pu | DoubleFloat |  | cim | Positive sequence resistance in per unit on a 100 MVA base. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | x_pu | DoubleFloat |  | cim | Positive sequence reactance in per unit on a 100 MVA base. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | b_pu | DoubleFloat |  | cim | Magnetizing Susceptance in per unit on a 100 MVA base. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ConductorType | sheathResistance | Resistance |  | cim | Resistance of the sheath for cable conductors. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ConductorType | sheathReactance | Reactance |  | cim | Reactance of the sheath for cable conductors. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | highStep | TapStep | 0 | cim | Highest possible tap step position, advance from neutral. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | initialDelay | Seconds | 10 | cim | For an LTC, the delay for initial tap changer operation (first step change). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | InitialDelay
CIMWires | TapChanger | lowStep | TapStep | 0 | cim | Lowest possible tap step position, retard from neutral. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | neutralKV | Voltage |  | cim | Voltage at which the winding operates at the neutral tap setting. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | neutralStep | TapStep | 0 | cim | The neutral tap step position for this winding. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | normalStep | TapStep | 0 | cim | The tap step position used in 'normal' network operation for this winding. For a 'Fixed' tap changer indicates the current physical tap setting. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | stepPhaseShiftIncrement | AngleDegrees |  | cim | Phase shift, in degrees, per step position. A positive value indicates a positive phase shift from the winding where the tap is located to the other winding (for a two-winding transformer), or to the ANDquot;TANDquot; point (for a three-winding transformer). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | stepVoltageIncrement | PerCent | 0 | cim | Tap step increment, in per cent of nominal voltage, per step position. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | subsequentDelay | DoubleFloat | 5 | cim | For an LTC, the delay for subsequent tap changer operation (second and later step changes). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | SubsequentDelay
CIMWires | TapChanger | tculControlMode | EnumTransformerControlMode |  | cim | For an LTC, the tap changer control mode, e.g.: Off, Local, Volt, MVAr. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TculControlMode
CIMWires | TapChanger | neutralAngle | Integer |  | etx | The CIM currently has no way of defining the angle associated with the neutral position of a TapChanger belonging to a phase shifter. Thus a neutralAngle attribute (measured in degrees) has been added to the TapChanger class. This attribute only appears in XML when the parent PowerTransformer is a phase shifter, i.e., when PowerTransformer.transformerType = 'phaseControl' or 'voltageAndPhaseControl'. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | maximumkV | Voltage |  | etx | The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | minimumkV | Voltage |  | etx | The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | parRampRate | ActivePower |  | etx | PAR optimiation ramp rate (MW per minute). | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | parOptimization | Boolean |  | etx | PAR optimization flag. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | parMaxMW | ActivePower |  | etx | PAR maximum MW value (MW). | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | parMinMW | ActivePower |  | etx | PAR minimum MW value (MW). | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | LoadBreakSwitch | ampRating | CurrentFlow |  | cim | Current carrying capacity, expressed in amperes, of a wire or cable under stated thermal conditions | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | MVArCapabilityCurve | coolantTemperature | Temperature |  | cim | The machine's coolant temperature in degrees Celsius (e.g., ambient air or stator circulating water). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | MVArCapabilityCurve | hydrogenPressure | Pressure |  | cim | The hydrogen coolant pressure. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | aVRToManualLag | Seconds |  | cim | Time delay, in seconds, required when switching from AVR to manual for a lagging MVAr violation. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | aVRToManualLead | Seconds |  | cim | Time delay, in seconds, required when switching from Automatic Voltage Regulation to Manual for a leading MVAr violation. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | baseMVAr | ReactivePower |  | cim | Default base MVAr value. This value represents the initial MVAr that can be used by any application function. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | coolantCondition | Float |  | cim | Temperature or pressure of coolant medium. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | coolantType | EnumCoolantType |  | cim | Method of cooling the machine, e.g., air, hydrogen gas, water. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | damping | Damping |  | cim | Damping torque coefficient, a proportionality constant that, when multiplied by the angular velocity of the rotor poles with respect to the magnetic field (frequency), results in the damping torque. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | inertia | Inertia | 5 | cim | The energy stored in the rotor when operating at rated speed. This value is used in the accelerating power reference frame for operator training simulator solutions. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | manualToAVR | Seconds |  | cim | Time delay, in seconds, required when switching from Manual to Automatic Voltage Regulation. This value is used in the accelerating power reference frame for powerflow solutions. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | maximumKV | Voltage |  | cim | Maximum kV limit for the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | maximumMVAr | ReactivePower |  | cim | Maximum MVAr limit. This is the maximum (nameplate) limit for the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | minimumKV | Voltage |  | cim | Minimum kV limit for the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | minimumMVAr | ReactivePower |  | cim | Minimum MVAr limit for the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | r | Resistance |  | cim | Positive sequence resistance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | r0 | Resistance |  | cim | Zero sequence resistance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | ratedMVA | ApparentPower |  | cim | Nameplate MVA rating for the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | x | Reactance | 0.12 | cim | Positive sequence reactance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | x0 | Reactance | 0.05 | cim | Zero sequence reactance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | xDirectSubtrans | Reactance |  | cim | Direct-axis subtransient reactance, also known as X'd. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | xDirectSync | Reactance |  | cim | Direct-axis synchronous reactance. The quotient of a sustained value of that AC component of armature voltage that is produced by the total direct-axis flux due to direct-axis armature current and the value of the AC component of this current, the machine running at rated speed. (Xd) | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | xDirectTrans | Reactance |  | cim | Direct-axis transient reactance, also known as X'd. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | xQuadSubtrans | Reactance |  | cim | Quadrature-axis subtransient reactance, also known as X'q. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | xQuadSync | Reactance |  | cim | Quadrature-axis synchronous reactance (Xq) , the ratio of the component of reactive armature voltage, due to the quadrature-axis component of armature current, to this component of current, under steady state conditions and at rated frequency. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | xQuadTrans | Reactance |  | cim | Quadrature-axis transient reactance, also known as X'q. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | operatingMode | EnumSynchronousMachineOperatingMode |  | cim | Current mode of operation, i.e., generator or condenser. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | type | EnumSynchronousMachineType |  | cim | Modes that this synchronous machine can operate in, i.e., as a generator, condenser, or both. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | condenserMW | ActivePower |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | AVR | Boolean |  | etx | T=Automatic Voltage Regulation is enabled | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | SynchronousMachine | ReferencePriority | Integer |  | etx | Priority of unit for reference bus selection. 0 = don t care (default) 1 = highest priority. 2 is less than 1 and so on. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | RegulationSchedule | lineDropCompensation | Boolean |  | cim | Flag to indicate that line drop compensation is to be applied. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RegulationSchedule | lineDropR | Resistance |  | cim | Line drop resistance. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RegulationSchedule | lineDropX | Reactance |  | cim | Line drop reactance. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RegulationSchedule | Season | EnumSeasonName |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | RegulationSchedule | DayType | EnumDayTypeName |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | CompositeSwitch | compositeSwitchType | CompositeSwitchType |  | cim | An alphanumeric code that can be used as a reference to extar information such as the description of the interlocking scheme if any. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | xn | Reactance |  | cim | Negative sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | rn | Resistance |  | cim | Negative sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | nominalVoltage | Voltage |  | cim | Phase-to-phase nominal voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | x | Reactance |  | cim | Positive sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | r | Resistance |  | cim | Positive sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | voltageAngle | AngleRadians |  | cim | Phase angle of a-phase open circuit. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | voltageMagnitude | Voltage |  | cim | Phase-to-phase open circuit voltage magnitude. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | x0 | Reactance |  | cim | Zero sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | r0 | Resistance |  | cim | Zero sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EquivalentSource | activePower | ActivePower |  | cim | High voltage source load. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Fuse | ampRating | CurrentFlow |  | cim | Fault interrupting rating in amperes. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | ratedKV | Voltage |  | cim | Rectifier/inverter primary base voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | bridges | Counter |  | cim | Number of bridges. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | commutatingReactance | Reactance |  | cim | Commutating reactance in ohms at AC bus frequency. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | commutatingResistance | Resistance |  | cim | Commutating resistance in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | compoundResistance | Resistance |  | cim | Compounding resistance in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | minCompoundVoltage | Voltage |  | cim | Minimum compounded DC voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | frequency | Frequency |  | cim | Frequency on the AC side. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | maximumMW | ActivePower |  | cim | The maximum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | minimumMW | ActivePower |  | cim | The minimum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | maximumKV | Voltage |  | cim | The maximum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | minimumKV | Voltage |  | cim | The minimum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RectifierInverter | operatingMode | OperatingMode |  | cim | Operating mode for the frequency converter. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | capacitiveRating | Reactance |  | cim | Maximum available capacitive reactive power. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | CapacitiveRating
CIMWires | StaticVarCompensator | inductiveRating | Reactance |  | cim | Maximum available inductive reactive power. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | InductiveRating
CIMWires | StaticVarCompensator | sVCControlMode | ControlMode |  | cim | SVC control mode: MVAr, Voltage. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | slope | VoltagePerReactivePower |  | cim | The characteristics slope of an SVC defines how the reactive power output changes in proportion to the difference between the regulated bus voltage and the voltage setpoint. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | voltageSetPoint | Voltage |  | cim | The reactive power output of the SVC is proportional to the difference between the voltage at the regulated bus and the voltage setpoint. When the regulated bus voltage is equal to the voltage setpoint, the reactive power output is zero. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | RampDurationThreshold | Float |  | etx | The threshold ramp duration. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | MaxTimeSteadyState | Float |  | etx | The maximum duration allowed to exceed Q range in steady_state. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | HighVoltageChangeThreshold | Float |  | etx | The upper bound of the voltage threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | LowVoltageChangeThreshold | Float |  | etx | The lower bound of the voltage threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | PostContingencyMVARMin | Float |  | etx | Post_contingency minimum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | PostContingencyMVARMax | Float |  | etx | Post_contingency maximum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | SteadyStateMVARMin | Float |  | etx | Steady_state minimum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | SteadyStateMVARMax | Float |  | etx | Steady_state maximum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | b | ReactivePower |  | etx | The StaticVarCompensator class has been extended to include a 'charging' attribute. The units are assumed to be in MVAR, as required by the CPSM Profile. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | maximumkV | Voltage |  | etx | The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | StaticVarCompensator | minimumkV | Voltage |  | etx | The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | excitingCurrent | ExcitingCurrent |  | cim | The exciting current % ('to' winding open-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | fromTapStep | TapStep |  | cim | The tap step number for the 'from' winding of the test pair. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | leakageImpedance | Impedance |  | cim | The leakage impedance measured at the 'from' winding with the 'to' winding short-circuited and all other windings open-circuited. Leakage impedance is expressed in units based on the MVA and kV ratings of the 'from' winding. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | loadLoss | LoadLoss |  | cim | The load loss kW ('to' winding short-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | noLoadLoss | NoLoadLoss |  | cim | The no load loss kW 'to' winding open-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | phaseShift | AngleDegrees |  | cim | The phase shift measured at the open-circuited 'to' winding, with the 'from' winding set to the 'from' winding's rated voltage and all other windings open-circuited. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | toTapStep | TapStep |  | cim | The tap step number for the 'to' winding of the test pair. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WindingTest | voltage | Voltage |  | cim | The voltage measured at the open-circuited 'to' winding, with the 'from' winding set to the 'from' winding's rated voltage and all other windings open-circuited. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireArrangement | mountingPointX | Integer |  | cim | Mounting point where wire One is mounted. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireArrangement | mountingPointY | Integer |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireType | phaseConductorCount | Counter |  | cim | Number of conductor strands in the (symmetrical) bundle (1-12). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireType | phaseConductorSpacing | ShortLength |  | cim | Distance between conductor strands in a (symmetrical) bundle (short length units). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireType | ampRating | CurrentFlow |  | cim | Current carrying capacity, expressed in amperes, of a wire or cable under stated thermal conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireType | gMR | ShortLength |  | cim | Geometric Mean Radius. If we replace the conductor by a thin walled tube of radius GMR, then its reactance is identical to the reactance of the actual conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireType | radius | ShortLength |  | cim | The radius of the conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireType | resistance | Resistance |  | cim | The resistance per unit length of the conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | FrequencyConverter | frequency | Frequency |  | cim | Frequency on the AC side. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | FrequencyConverter | maximumMW | ActivePower |  | cim | The maximum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | FrequencyConverter | maximumKV | Voltage |  | cim | The maximum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | FrequencyConverter | minimumMW | ActivePower |  | cim | The minimum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | FrequencyConverter | minimumKV | Voltage |  | cim | The minimum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | FrequencyConverter | operatingMode | OperatingMode |  | cim | Operating mode for the frequency converter. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SeriesCompensator | r | Resistance |  | cim | Positive sequence resistance of the capacitor bank. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SeriesCompensator | x | Reactance |  | cim | Positive sequence reactance of the capacitor bank. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | aVRDelay | Seconds |  | cim | Time delay in seconds required for the device to be connected or disconnected by automatic voltage regulation (AVR). | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | impedance | Impedance |  | cim | The positive sequence impedance of the capacitor. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | maximumkV | Voltage |  | cim | The maximum voltage at which the capacitor bank should operate. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | maximumSections | Counter |  | cim | For a capacitor bank, the maximum number of sections that may be switched in. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | minimumkV | Voltage |  | cim | The minimum voltage at which the capacitor bank should operate. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | mVArPerSection | ReactivePower |  | cim | For a capacitor bank, the size in MVAr of each switchable section at the Nominal kV. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | nominalkV | Voltage |  | cim | The nominal voltage at which the nominal MVAr was measured. This should normally be within 10% of the voltage at which the capacitor is connected to the network. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | nominalMVAr | ReactivePower |  | cim | Nominal MVAr output of the capacitor bank at the nominal kV. This number should be positive. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | normalSections | Counter |  | cim | For a capacitor bank, the normal number of sections switched in. This number should correspond to the Nominal MVAr. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | switchOnCount | Counter |  | cim | The switch on count since the capacitor count was last reset or initialized. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | switchOnDate | AbsoluteDateTime |  | cim | The date and time when the capacitor bank was last switched on. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | voltSensitivity | PUkVPerMVAr |  | cim | Voltage sensitivity required for the device to regulate the bus voltage, in per unit voltage/MVAr. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | yPerSection | Admittance |  | cim | For a capacitor bank, the admittance of each switchable section. Calculated using the MVAr per section and corrected for network voltage. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | ShuntCompensator | AVR | Boolean |  | etx | T = AUTOMATIC SWITHING IS ENABLED IN CONTINGENCY ANALYSIS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | ShuntCompensator | AVREnable | Boolean |  | etx | T = AUTOMATIC SWITCHING IS ENABLED IN CONTINGENCY ANALYSIS BY USER. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | ShuntCompensator | SwitchingPriority | Integer |  | etx | switching priority number. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | WiresVersion | version | String30 | Wires_v005 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WiresVersion | date | String30 | 2006-12-19 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | EquivalentLoad | feederLoadMgtFactor | PerCent |  | cim | The feeder's contribution to load management, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | EquivalentLoad | mVArColdPickUpFactor | PerCent |  | cim | The amount of nominal feeder MVAr that is picked up cold, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | EquivalentLoad | mWColdPickUpFactor | PerCent |  | cim | The amount of nominal feeder MW that is picked up cold, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | EquivalentLoad | phaseAmpRating | CurrentFlow |  | cim | The rated individual phase amperes. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | EquivalentLoad | loadAllocationFactor | Float |  | cim | Permit assignment of loads on a participation factor basis. Given three equivalent loads with factors of 10, 25 and 15, a feeder load of 100 amps could be allocated on the feeder as 20, 50 and 30 amps. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | InductionMotorLoad | r | Float |  | etx | motor r. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMLoadModel | InductionMotorLoad | x | Float |  | etx | motor x. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMLoadModel | InductionMotorLoad | rtransformer | Float |  | etx | stepup transformer r. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMLoadModel | InductionMotorLoad | xtransformer | Float |  | etx | stepup transformer x. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMLoadModel | InductionMotorLoad | varlowlimit | Float |  | etx | motor var low limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMLoadModel | InductionMotorLoad | varhighlimit | Float |  | etx | motor var high limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMLoadModel | PowerCutZone | cutLevel1 | PerCent |  | cim | First level (amount) of load to cut as a percentage of total zone load. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | PowerCutZone | cutLevel2 | PerCent |  | cim | Second level (amount) of load to cut as a percentage of total zone load. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | Season | name | EnumSeasonName |  | cim | Name of the Season. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | SeasonName
CIMLoadModel | Season | endDate | DateTime |  | cim | Date season ends. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | Season | startDate | DateTime |  | cim | Date season starts. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadModelVersion | version | String30 | LoadModel_v003_02 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadModelVersion | date | String30 | 2006-10-06 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | ConnectivityNode | connectivityNodeNumber | LongInt |  | cim | Numerical identification, indicating electrical location | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | ConnectivityNode | PSSEBusNumber | Integer |  | etx | The PSS/E bus number associated with this point in the network. This attribute should only be used to model ficticious PSS/E busbars that are not associated with physical busbar sections. | FALSE | FALSE | TRUE | FALSE |  | TRUE
CIMTopology | ConnectivityNode | SlackBusPriority | Integer |  | etx | The CIM currently has no way of defining swing buses. This is accomplished by adding an attribute to ConnectivityNode called SlackBusPriority. This is an integer field in which 1 is the highest priority. The value 0 or the absence of the attribute in a particular ConnectivityNode indicates that the node cannot function as a swing bus. The attribute is used by applications to dynamically select a swing bus in each electrical island. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | energized | Boolean |  | cim | True if node energized. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | loadCarrying | Boolean |  | cim | True if node is load carrying. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | netInjectionMVar | ReactivePower |  | cim | Net injection MVAr | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | netInjectionMW | ActivePower |  | cim | Net injection MW | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | observabilityFlag | Boolean |  | cim | The observability status of the node. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | phaseAngle | AngleRadians |  | cim | Phase angle of node. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | voltage | Voltage |  | cim | Voltage of node. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologyVersion | version | String30 | Topology_v002_02 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologyVersion | date | String30 | 2006-09-04 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | SynchrocheckRelay | maxAngleDiff | AngleRadians |  | cim | The maximum allowable voltage vector phase angle difference across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | SynchrocheckRelay | maxFreqDiff | Frequency |  | cim | The maximum allowable frequency difference across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | SynchrocheckRelay | maxVoltDiff | Voltage |  | cim | The maximum allowable difference voltage across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionEquipment | relayDelayTime | Seconds | 0 | cim | The time delay in seconds from detection of abnormal conditions to relay operation | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionEquipment | highLimit | Float |  | cim | The maximum allowable value. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionEquipment | lowLimit | Float |  | cim | The minimum allowable value. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionEquipment | powerDirectionFlag | Boolean |  | cim | Direction same as positive active power flow value. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | RecloseSequence | recloseDelay | Seconds |  | cim | Indicates the time lapse before the reclose step will execute a reclose. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | RecloseSequence | recloseStep | Integer |  | cim | Indicates the ordinal position of the reclose step relative to other steps in the sequence. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay | currentLimit1 | CurrentFlow |  | cim | Current limit #1 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay | currentLimit2 | CurrentFlow |  | cim | Current limit #2 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay | currentLimit3 | CurrentFlow |  | cim | Current limit #3 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay | inverseTimeFlag | Boolean |  | cim | True/False flag that indicates whether or not the current relay has inverse time characteristic. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay | timeDelay1 | Seconds |  | cim | Inverse time delay #1 for current limit #1. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay | timeDelay2 | Seconds |  | cim | Inverse time delay #2 for current limit #2. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | CurrentRelay | timeDelay3 | DoubleFloat |  | cim | Inverse time delay #3 for current limit #3. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionVersion | version | String30 | Protection_v002 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionVersion | date | String30 | 2006-05-23 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ControlHouseEquipement | controlHouseEquipType | EnumControlHouseEquipmentType |  | cim | Type of control house equipment. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Bay | bayEnergyMeasFlag | Bool | FALSE | cim | Indicates the presence/absence of kWh/kvarh measurements. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Bay | bayPowerMeasFlag | Bool | FALSE | cim | Indicates the presence/absence of MW/MVAr measurements. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Bay | breakerConfiguration | EnumBreakerConfiguration |  | cim | Breaker configuration. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Bay | busBarConfiguration | EnumBusbarConfiguration |  | cim | Busbar configuration. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | VoltageLevel | highVoltageLimit | Voltage |  | cim | The bus bar's high voltage limit in kV | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | VoltageLevel | lowVoltageLimit | Voltage |  | cim | The bus bar's low voltage limit in kV. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Substation | abnormalForAlarm | Boolean |  | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | abnormalForSCADA | Boolean |  | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | alarmLocation | String8 |  | etx | Alarm location, must match LOC.ID_LOC in the Alarm database. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | areaOfResponsibility | String8 |  | etx | Permission name of the substation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | audibleTone | Boolean |  | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | inhibitAbnormalForAlarm | Boolean |  | etx | Permanently Inhibit the flag of abnormalForAlarm . | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | inhibitAbnormalForSCADA | Boolean |  | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | inhibitAudibleTone | Boolean |  | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | inhibitLoggingAndAlarmList | Boolean |  | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | inhibitUnacknowledgedAlarmList | Boolean |  | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | inhibitUnackAlarmList
CIMCore | Substation | initiallyInhibit | Boolean |  | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entiry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | loggingAndAlarmList | Boolean |  | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | overrideDefaultInhibitDefinition | Boolean |  | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | overrideDefaultInhibitDef
CIMCore | Substation | unacknowledgedAlarmList | Boolean |  | etx | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | IdentifiedObject | aliasName | String100 |  | cim | Free text name of the object or instance. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IdentifiedObject | description | String1000 |  | cim | Description of the object or instance. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Description
CIMCore | IdentifiedObject | name | Name |  | cim | The name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.name shall not be used, use IdentifiedObject.description instead. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Name
CIMCore | IdentifiedObject | pathName | String500 |  | cim | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IdentifiedObject | mRID | String100 |  | cim | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | DAM_Monitored | Boolean |  | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | RUC_Monitored | Boolean |  | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | DAM_Secured | Boolean |  | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | RUC_Secured | Boolean |  | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | OUSPriority | Integer |  | etx | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | CurveData | xvalue | Float | 0 | cim | The data value of the X-axis variable, depending on the X-axis units | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | xAxisData
CIMCore | CurveData | y1value | Float | 0 | cim | The data value of the first Y-axis variable, depending on the Y-axis units | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | y1AxisData
CIMCore | CurveData | y2value | Float |  | cim | The data value of the second Y-axis variable (if present), depending on the Y-axis units | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | y2AxisData
CIMCore | Curve | curveStyle | EnumCurveStyle |  | cim | The style or shape of the curve. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Curve | xUnit | EnumXAxisUnits |  | cim | The X-axis units of measure. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | xAxisUnits
CIMCore | Curve | y1Unit | EnumY1AxisUnits |  | cim | The Y1-axis units of measure. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | y1AxisUnits
CIMCore | Curve | y2Unit | EnumY2AxisUnits |  | cim | The Y2-axis units of measure. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | y2AxisUnits
CIMCore | Curve | xAxisType | EnumXAxisType |  | cim | The type of independent variable. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Curve | yAxisType | EnumYAxisType |  | cim | The type of dependent variable. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Company | companyType | EnumCompanyType |  | cim | The type of company, e.g.: pool, municipal, private. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CompanyType
CIMCore | BasePower | basePower | ApparentPower |  | cim | Definition of base power. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BaseVoltage | nominalVoltage | Voltage |  | cim | The PowerSystemResource's base voltage. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ConductingEquipment | phases | EnumPhases | 0 | cim | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ConductingEquipment | Remove | Boolean |  | etx | The equipment is removed from the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | ConductingEquipment | RemoveEnable | Boolean |  | etx | The equipment can be removed from the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | SubControlArea | ControlAreaNumber | Integer |  | etx | The SubControlArea is extended to include a ControlAreaNumber attribute to determine ordering of the areas (e.g., for display purposes). The values must be positive, unique, 1-relative, sequential integers without gaps. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | CoreVersion | version | String30 | Core_v005 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | CoreVersion | date | String30 | 2006-12-18 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BasicIntervalSchedule | startTime | AbsoluteDateTime |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BasicIntervalSchedule | value1Unit | String50 |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BasicIntervalSchedule | value2Unit | String50 |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularIntervalSchedule | timeStep | Seconds |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularIntervalSchedule | endTime | AbsoluteDateTime |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IrregularTimePoint | time | Seconds |  | cim | The time is relative the BasicTimeSchedule.startTime. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IrregularTimePoint | value1 | Float |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IrregularTimePoint | value2 | Float |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularTimePoint | sequenceNumber | Integer |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularTimePoint | value1 | Float |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularTimePoint | value2 | Float |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | authorityName | String100 |  | cim | The name of the person who is authorized to issue the tag. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | clearanceTagType | EnumClearanceTagType |  | cim | The type of tag, depending on the purpose of the work to be performed and/or the type of supervisory control allowed. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | deenergizeReqFlag | Boolean |  | cim | Flag = YES if equipment must be deenergized. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | groundReqFlag | Boolean |  | cim | Flag = YES if equipment must be grounded. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | phaseCheckReqFlag | Boolean |  | cim | Flag = YES if equipment phasing must be checked. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | tagIssueTime | AbsoluteDateTime |  | cim | The time at which the clearance tag was issued. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | workDescription | String1000 |  | cim | Description of the work to be performed. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | workEndTime | AbsoluteDateTime |  | cim | The time at which the clearance tag is scheduled to be removed. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | workStartTime | AbsoluteDateTime |  | cim | WorkStartTime | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | SwitchingOperation | operationTime | AbsoluteDateTime |  | cim | Time of operation in same units as OutageSchedule.xAxixUnits. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | SwitchingOperation | newState | EnumSwitchState |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | OutageVersion | version | String30 | Outage_v001_01 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | OutageVersion | date | String30 | 2006-10-06 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Control | timeStamp | AbsoluteDateTime |  | cim | The last time a control output was sent. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Control | operationInProgress | Boolean |  | cim | Indicates that a client is currently sending control commands that has not completed. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Limit | value | Integer |  | cim | The value to supervise against. | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMMeas | LimitSet | isPercentageLimtis | Boolean |  | cim | Tells if the limit values are in percentage of normalValue or the specified Unit for Measurements and Controls. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | LimitSet | type | EnumLimitSetType | 0 | etx | The limit set type is used to distinguish different limit sets of a measurement. For a real project there could be limit sets like Limit Set Summer, Limit Set Winter, etc. or Limit Set High Temperature, Limit Set Low Temperature, etc. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | LimitSetType
CIMMeas | Measurement | positiveFlowIn | Bool |  | cim | If true then this measurement is a MW, MVAR or AMPS with the convention that a positive value measured at the Terminal means power is flowing into the related PowerSystemResource. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValue | timeStamp | AbsoluteDateTime |  | cim | The time when the value was last updated. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValue | sensorAccuracy | PerCent |  | cim | The limit, expressed as a percentage of the sensor maximum, that errors will not exceed when the sensor is used under reference conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValue | Source | EnumMeasurementValueSource | 0 | cim | Source of data e.g. telemetered, state estimator, load flow, manual override. The enumeration is defined as: 0 telemetered 1 calculated Scope: [SCADA] | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | validity | EnumValidity | 0 | cim | Validity may be good, questionable or invalid. Refer to the Validity enumeration for more details. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | overFlow | Boolean |  | cim | Measurement value is beyond the capability of being represented properly. For example, a counter value overflows from maximum count back to a value of zero. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | outOfRange | Boolean |  | cim | Measurement value is beyond a predefined range of value. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | badReference | Boolean |  | cim | Measurement value may be incorrect due to a reference being out of calibration. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | oscillatory | Boolean |  | cim | To prevent some overload of the communication it is sensible to detect and suppress oscillating (fast changing) binary inputs. If a signal changes in a defined time (tosc) twice in the same direction (from 0 to 1 or from 1 to 0) then oscillation is detected and the detail quality identifier 'oscillatory' is set. If it is detected a configured numbers of transient changes could be passed by. In this time the validity status 'questionable' is set. If after this defined numbers of changes the signal is still in the oscillating state the value shall be set either to the opposite state of the previous stable value or to a defined default value. In this case the validity status 'questionable' is reset and 'invalid' is set as long as the signal is oscillating. If it is configured such that no transient changes should be passed by then the validity status 'invalid' is set immediately in addition to the detail quality identifier 'oscillatory' (used for status information only). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | failure | Boolean |  | cim | This identifier indicates that a supervision function has detected an internal or external failure, e.g. communication failure. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | oldData | Boolean |  | cim | Measurement value is old and possibly invalid, as it has not been successfully updated during a specified time interval. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | suspect | Boolean |  | cim | A correlation function has detected that the value is not consitent with other values. Typically set by a network State Estimator. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | test | Boolean | FALSE | cim | Measurement value is transmitted for test purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | operatorBlocked | Boolean | FALSE | cim | Measurement value is blocked and hence unavailable for transmission. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | source | EnumSource | 0 | cim | Source gives information related to the origin of a value. The value may be acquired from the process, defaulted or substituted. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Quality61850 | estimatorReplaced | Boolean | FALSE | cim | Value has been replaced by State Estimator. estimatorReplaced is not an IEC61850 quality bit but has been put in this class for convenience. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | ValueToAlias | value | Integer |  | cim | The value that is mapped. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Analog | maxValue | Float |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Analog | minValue | Float |  | cim | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Analog | normalValue | Float |  | cim | Normal measurement value, e.g., used for percentage calculations. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Analog | positiveFlowIn | Boolean |  | cim | If true then this measurement is a MW, MVAR or AMPS with the convention that a positive value measured at the Terminal means power is flowing into the related PowerSystemResource. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Accumulator | maxValue | Integer |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorLimit | value | Integer |  | cim | The value to supervise against. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | value | Integer |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | blockViaPrimarySite | Boolean |  | etx | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | blockViaSecondaySite | Boolean |  | etx | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | forceCalculationToRun | Boolean |  | etx | T = Any calculations that have this COUNT as a trigger will be performed whenever the value is scanned, even if the value doesn't change. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | historicalRecordingDeadband | Float |  | etx | The threshold (percentage currently recorded accumulator data) above which additional data points should not retained. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | mappedInOAG | Boolean |  | etx | T = This data-point is also represented in the OAG model as a data item (designated member of a data packet). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | rawValue | Boolean |  | etx | T = value received through Intersite Data is a raw value. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | recordHistoricalData | Boolean |  | etx | T = State changes on the point are recorded in the historical data review file. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | saveFractionalPortion | Boolean |  | etx | This feature applies to telemetered accumulator values from an RTU. Accumulator values from other sources, such as from a remote site or from a calculation, may contain the fractional part of the value. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | scaleFactor | Float |  | etx | SCALE FACTOR FOR CONVERTING COUNT VALUE RECVD THROUGH ISD TO ENGINEERING UNITS.SCALE FACTOR FOR CONVERTING COUNT VALUE RECVD THROUGH ISD TO ENGINEERING UNITS. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | value | Float |  | cim | The value to supervise against. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogLimit | deadband | PerCent |  | etx | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an analog value oscillates around a limit. When either threshold is null, the percentage is that of the non?null limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | forbiddenRegion | Boolean |  | etx | T = The analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | ignoreLimitChecking | Boolean |  | etx | T = The limit should be ignored when checking the analog for limit violations. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | lowerThreshold | Float |  | etx | The value below which the analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | upperThreshold | Float |  | etx | The value above which the analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater then the Lower Threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | usePercentage | Boolean |  | etx | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | value | Float |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogValue | abnormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the violated state. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | abnormalForAlarm | Boolean |  | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | abnormalForSCADA | Boolean |  | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | allowSELECTStep | Boolean |  | etx | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | audibleTone | Boolean |  | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | autoAckAndDeleteAlarms | Boolean |  | etx | Automatically acknowledge and delete alarms if the Analog is manually entered or successfully controlled by the operator to a normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | autoAcknowledge | Boolean |  | etx | When set to true, this flag specifies that alarms will be automatically acknowledged on return to normal. This will only occur if the Alarm Return to Violations flag is not set on the Limit Names table. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | blockViaPrimarySite | Boolean |  | etx | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | blockViaSecondarySite | Boolean |  | etx | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | bypassEntry | Boolean |  | etx | When set to true, this flag specifies allowing bypass entry of Suspect values if telemetered from a remote site or SCADA Front End. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | controlDemandScan | Boolean |  | etx | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | controlMMISequence | Boolean |  | etx | true = override any default settings. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | enableAutoSEReplacement | Boolean |  | etx | TRUE = Allow automatic State Estimator replacement. Automatically substitute the display value with a good quality state estimated value if the quality of the telemetered analog becomes SUSPECT. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | fromExternalProgram | Boolean |  | etx | When set to true, this flag specifies the source of the data is an external program. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | fromStateEstimator | Boolean |  | etx | When set to true, this flag specifies the source of the data is state estimator. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | historicalRecordingDeadband | PerCent |  | etx | Threshold (percentage currently recorded analog data) above which additional data points should not retained. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | inhibitAbnormalForAlarm | Boolean |  | etx | Permanently Inhibit the flag of abnormalForAlarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | inhibitAbnormalForSCADA | Boolean |  | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | inhibitAudibleTone | Boolean |  | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | inhibitLoggingAndAlarmList | Boolean |  | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | inhibitUnacknowledgedAlarmList | Boolean |  | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | inhibitUnackAlarmList
CIMMeas | AnalogValue | initiallyInhibit | Boolean |  | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entiry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | invertAnalogViaSecondarySite | Boolean |  | etx | TRUE = Negate the analog value when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | invertSign | Boolean |  | etx | When set to true, this flag specifies that the analog value, as received by SCADA, is inverted before using in other applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | loggingAndAlarmList | Boolean |  | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | mappedInOAG | Boolean |  | etx | When set to true, this flag indicates that this data-point is also represented in the OAG model as a data item (designated member of a data packet). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | measurementNode | String4 |  | etx | The name or identifier of the node where the analog measurement is taken. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | negateValueReceivedFromISD | Boolean |  | etx | When set to true, this flag specifies that the polarity of the analog value received via ISD will be switched. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | negativeUniPolarClamping | Boolean |  | etx | True = positive values will be forced (clamped) to zero before updating into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | notInService | Boolean |  | etx | flag indicating not in service | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | overrideDefaultInhibitDefinition | Boolean |  | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | peakData | Boolean |  | etx | When set to true, this flag specifies that the Peak Data Processing task will sample this analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | positiveUniPowerClamping | Boolean |  | etx | TRUE = negative values will be forced (clamped) to zero before updating into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | recordHistoricalData | Boolean |  | etx | When set to true, this flag specifies that state changes on the analog are recorded in the historical data review file. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | requireEXECUTEStep | Boolean |  | etx | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | requireSELECTStep | Boolean |  | etx | TRUE = a separate SELECT action is required before a supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | returnToNormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | seDeadband | Float |  | etx | Display values of good quality which are different than a good quality state-estimated value by more than this amount are considered anomalous, and automatically substituted with the state-estimated value, if the global Automatic State-Estimator Replacement function is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | skipLimitChecking | Boolean |  | etx | When set to true, this flag specifies disable reasonability limit checking for this analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | tabularDisplayPriority | Integer |  | etx | Priority of tabulay display. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | timeDelay | Integer |  | etx | The number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | unacknowledgedAlarmList | Boolean |  | etx | A flag indicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | zeroClampingDeadband | Float |  | etx | If value is greater than zero, then any value between zero and the entered value will be forced (clamped) to zero for update into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | value | Integer |  | cim | The value representing the actuator output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Command | normalValue | Integer |  | cim | Normal value for Control.value e.g. used for percentage scaling. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Command | contactClosureTime | Integer |  | etx | The time that must elapse before the selected point is activated, in milliseconds. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | ctrlFunc | Boolean |  | etx | Open: When selected, this radio button indicates that this digital control performs an OPEN type supervisory control function. Close: When selected, this radio button indicates that this digital control performs a CLOSE type supervisory control function. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | expectedExtendedStatusBitValue | Boolean |  | etx | T = The expected value is an extended status bit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | expectedExtStatusBitValue
CIMMeas | Command | expectedStatusBitValue | Boolean |  | etx | T = The expected value is a status bit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | tapControl | Boolean |  | etx | T = The digital control performs a tap control function. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | timeToWaitForStatusChange | Integer |  | etx | The number of seconds allowed for the device to respond to the control, and to report the resulting state change to the SCADA subsystem. This value is zero if no timeout check is required (e.g., on a transformer tap changer). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | waitTime | Boolean |  | etx | The time in seconds allowed between consecutive operations of the CTRL. If consecutive controls are issued to the same CTRL before the entered number of seconds as elapsed, the second control request will be rejected. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Discrete | maxValue | Integer |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Discrete | minValue | Integer |  | cim | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Discrete | normalValue | Integer |  | cim | Normal measurement value, e.g., used for percentage calculations. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | DiscreteValue | value | Integer |  | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | DiscreteValue | abnormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the abnormal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | abnormalForAlarm | Boolean |  | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | abnormalForSCADA | Boolean |  | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | allowControlFromForeignSites | Boolean |  | etx | True = Another site may issue a control on this point. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | allowMultipleRaiseOrLower | Boolean |  | etx | True = Multiple Tap Raise and Lower commands may be issued consecutively without re-selecting the... | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | allowSELECTStep | Boolean |  | etx | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | audibleTone | Boolean |  | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | autoAckAndDeleteAlarms | Boolean |  | etx | True = Automatically acknowledge and delete alarms if the Point is manually entered or successfully controlled by the operator to a normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | autoAcknowledgeOnReturnToNormal | Boolean |  | etx | True = alarms will be automatically acknowledged on return to normal. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | autoAckOnReturnToNormal
CIMMeas | DiscreteValue | blockViaPrimarySite | Boolean |  | etx | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | blockViaSecondarySite | Boolean |  | etx | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | byPass | Boolean |  | etx | True = Allow bypass entry of Suspect values if telemetered from a remote site or SCADA Front End. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | controlDemandScan | Boolean |  | etx | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | controlSequence | Boolean |  | etx | True = Override global control execution flags for this point. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | feedbackAnalog | String4 |  | etx | True = The Analog Name which is configured to provide feedback of the associated analog value for control completion checks of Raise/Lower supervisory controls. The chosen Analog must be modeled under the same Device as the controlling Point record. This field is optional. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | fromExternalProgram | Boolean |  | etx | When set to true, this flag specifies the source of the data is an external program. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | inhibitAbnormalForAlarm | Boolean |  | etx | Permanently Inhibit the flag of abnormalForAlarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | inhibitAbnormalForSCADA | Boolean |  | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | inhibitAudibleTone | Boolean |  | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | inhibitLoggingAndAlarmList | Boolean |  | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | inhibitUnacknowledgedAlarmList | Boolean |  | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | inhibitUnackAlarmList
CIMMeas | DiscreteValue | initiallyInhibit | Boolean |  | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entiry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | invertExtendedStatusViaISD | Boolean |  | etx | True = The extended status bit (XIS) will be inverted when received from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | invertExtStatusViaISD
CIMMeas | DiscreteValue | invertExtendedStatusViaSecSite | Boolean |  | etx | True = The extended status bit (XIS) will be inverted when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | invertExtStatusViaSecSite
CIMMeas | DiscreteValue | invertStatus | Boolean |  | etx | True = The status point value, as received by SCADA, is inverted before using in other applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | invertStatusBitReceivedViaISD | Boolean |  | etx | True = The status bit (SIS) will be inverted when received from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | invertStatusBitRcvdViaISD
CIMMeas | DiscreteValue | invertStatusBitReceivedViaSecSite | Boolean |  | etx | True = The status bit (SIS) will be inverted when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | invertStatusBitRcvdViaSecSite
CIMMeas | DiscreteValue | logForControlIssued | Boolean |  | etx | True = Controls issued on this point will be logged in the system activity log. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | loggingAndAlarmList | Boolean |  | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | mappedInOAG | Boolean |  | etx | When set to true, this flag indicates that this data-point is also represented in the OAG model as a data item (designated member of a data packet). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | momentaryChangeDetection | Boolean |  | etx | True = a momentary change detection status will be returned. Momentary change detection status informs the computer of changes that occur between scans. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | noISDDownload | Boolean |  | etx | True = Even though the Point is associated with a remote site, the Point will not be included in the Intersite Data download request for status values to the remote site. The remote site is only used for determining which site to send Supervisory Controls to. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | notInService | Boolean |  | etx | flag indicating not in service. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | noWarningIfHanging | Boolean |  | etx | Don't issue warning message if a lone Topology Node is defined, which is not defined on any other record within the Substation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | overrideDefaultInhibitDefinition | Boolean |  | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | recordHistoricalData | Boolean |  | etx | When set to true, this flag specifies that state changes on the analog are recorded in the historical data review file. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | requireEXECUTEStep | Boolean |  | etx | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | requireSELECTStep | Boolean |  | etx | TRUE = a separate SELECT action is required before a supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | returnToNormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | tabularDisplayPriority | Integer |  | etx | Priority of tabulay display. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | tapChangerTimeout | Integer |  | etx | The timeout between steps of a multiple raise/lower supervisory control sequence for a tap changer. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | threeState | Boolean |  | etx | True = A three-state point is modeled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | timeDelay | Integer |  | etx | Demand Scan After Control is configured for this point, enter the number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | unacknowledgedAlarmList | Boolean |  | etx | A flag indicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | MeasVersion | version | String30 | Meas_v003_02 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasVersion | date | String30 | 2006-10-06 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | SetPoint | value | Float |  | cim | The value representing the actuator output. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | SetPoint | maxValue | Float |  | cim | Normal value range maximum for any of the Control.value. Used for scaling, e.g. in bar graphs. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | SetPoint | minValue | Float |  | cim | Normal value range minimum for any of the Control.value. Used for scaling, e.g. in bar graphs. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | SetPoint | normalValue | Float |  | cim | Normal value for Control.value e.g. used for percentage scaling. | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | SetPoint | allowControlFromForeignSites | Boolean |  | etx | CONTROLLED AT REMOTE SITE: T = Another site may issue this setpoint. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | SetPoint | deadBand | Float |  | etx | SETPOINT ANALOG DEADBAND (STATIC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | SetPoint | noLog | Boolean |  | etx | T = Setpoints issued on this analog are not logged. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | SetPoint | notInService | Boolean |  | etx | Amount by which the analog value may vaFloat. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | SetPoint | timeOut | Integer |  | etx | DEVICE OPERATION TIME LIMIT - This value indicates the device operation time limit in seconds. If the setpoint request was successfully transmitted to the RTU and the associated analog does not show that the device moved to the required value within this period, the setpoint operation is considered failed. A zero indicates an indefinite operation time limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | SetPoint | waitTime | Integer |  | etx | Wait time. | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | StringMeasurementValue | value | String100 |  | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMDomain | DomainVersion | version | String30 | Domain_v005 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMDomain | DomainVersion | date | String30 | 2006-05-23 | cim |  | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | AreaReserveSpec | lowerRegMarginReqt | DoubleFloat | 20 | cim | Lower regulating margin requirement in MW, the amount of generation that can be dropped by control in 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | AreaReserveSpec | opReserveReqt | DoubleFloat | 500 | cim | Operating reserve requirement in MW, where operating reserve is the generating capability that is fully available within 30 minutes. Operating reserve is composed of primary reserve (t less than 10 min) and secondary reserve (10 less than t less than 30 min). | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | AreaReserveSpec | primaryReserveReqt | DoubleFloat | 40 | cim | Primary reserve requirement in MW, where primary reserve is generating capability that is fully available within 10 minutes. Primary reserve is composed of spinning reserve and quick-start reserve. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | AreaReserveSpec | raiseRegMarginReqt | DoubleFloat | 20 | cim | Raise regulating margin requirement in MW, the amount of generation that can be picked up by control in 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | AreaReserveSpec | spinningReserveReqt | DoubleFloat | 200 | cim | Spinning reserve requirement in MW, spinning reserve is generating capability that is presently synchronized to the network and is fully available within 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | EnergyTransaction | firmInterchangeFlag | Bool | FALSE | cim | Firm interchange flag indicates whether or not this energy transaction can be changed without potential financial consequences. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | EnergyTransaction | productLevel | Float | 0 | cim | Additional information is not available. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | EnergyTransaction | dateTime | DateTime | 2000-01-01 | cim | Additional information is not available. | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | EnergyTransaction | state | EnumEnergyTransactionType |  | cim | { Approve ¦ Deny ¦ Study } | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMEnergyScheduling | EnergyTransaction | reason | String100 |  | cim | Additional information is not available. | FALSE | FALSE | FALSE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | FrequencyBiasFactor | DoubleFloat | 50 | cim | Initial frequency bias used in the frequency term of the ACE calculation (MW/0.1 Hz). SCOPE: [OTS] | FALSE | FALSE | FALSE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | AreaControlMode | EnumAreaControlMode | 0 | cim | Indicates the initial ACE control mode. Available values are: 0 - T (Tie Line Bias) 1 - I (Constant Net Interchange) 2 - F (Constant Frequency) SCOPE: [OTS] | FALSE | FALSE | FALSE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandAlarmACE | Float |  | etx | ACE ALARM DEADBAND (EG: 2 MW). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | limitAssistResponseACE | Float |  | etx | ACE LIMIT FOR ASSIST RESPONSE (EG: 20 MW) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandNormalResponseACE | Float |  | etx | ACE DEADBAND; ACE LIMIT FOR NORMAL RESPONSE (EG: 5 MW) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | limitEmergencyResponseACE | Float |  | etx | ACE LIMIT FOR EMERGENCY ASSIST RESPONSE (EG: 40 MW) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | limitNonWindupIntegralACE | Float |  | etx | NON-WINDUP LIMIT ON INTEGRAL OF ACE (MW-HR). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minimumPermissiveACE | Float |  | etx | MINIMUM ACE LEVEL FOR PERMISSIVE CONTROL (MW) (EG: 35 MW). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumTripACE | Float |  | etx | VALUE OF ACE ABOVE WHICH AGC WILL PAUSE. VALUE MUST BE GREATER THAN OR EQUAL TO ACEALM_OPA, OR LESS THAN ZERO | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | assistPriorityLevel | Integer |  | etx | Assist Threshold. When the ACE is in assist region, then all the units up to this Priority level will have the desired priority level =1. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandAutoInadvertent | Integer |  | etx | DEADBAND FOR AUTOMATIC INADVERTENT (PEAK AND OFFPEAK) IN MWHR IF INADVERTENT VALUE IS WITHIN THIS DEADBAND AUTO PAYBACK IS DISABLED | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumAutoInadvertentPayback | Float |  | etx | MAXIMUM VALUE OF AUTOMATIC INADVERTENT PAYBACK PERMITTED PER CYCLE IN MW/AGC-CYCLE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | maxAutoInadvertentPayback
EnergyScheduling | HostControlArea | balanceRampEnd | Float |  | etx | Number of minutes into the period to end the balancing energy schedule ramp. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | balanceRampStart | Float |  | etx | Number of minutes before the end of the period to start the balancing energy schedule ramp. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | costCO2 | Float |  | etx | Cost of CO2 in objective (Cost/UnitsCO2). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | costNOX | Float |  | etx | Cost of NOX in objective (Cost/UnitsCO2). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | costSO2 | Float |  | etx | Cost of SO2 in objective (Cost/UnitsCO2). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandVariableMaximum | Float |  | etx | High limit for the deadband variable (scalar). Used in the variable frequency bias calculation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandVariableMinimum | Float |  | etx | Low limit for the deadband variable (scalar). Used in the variable frequency bias calculation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | defaultLoadRelief | Float |  | etx | The percentage of the breakpoint's control area load MW value to use as the default for the breakpoint's load relief value if that value is null. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deltaTime | Integer |  | etx | TIME DIFFERENCE BETWEEN EMS TIME ZONE AND REPORTING TIME ZONE. WHEN DELTA-TIME IS ADDED TO THE TIME IN THE EMS TIME ZONE, THE RESULT SHOULD BE THE CURRENT TIME IN THE REPORTING TIME ZONE. (Units?) | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsEmergencyDisableJoint | Float |  | etx | Number of seconds ACE can be in emergency region before joint AGC is disabled for all TIEs. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | assistEmergencyPriorityLevel | Integer |  | etx | Assist Threshold. When the ACE is in emergency region, then all the units up to this Pritority level will have the desired priority level =1. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | frequencyAlarmThreshold | Float |  | etx | WARNING ALARM THRESHOLD ON FREQUENCY (E.G. 0.2 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandFrequencyWarningAlarm | Float |  | etx | DEADBAND ON WARNING ALARM THRESHOLD ON FREQUENCY (E.G. 0.05 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | deadbandFreqWarningAlarm
EnergyScheduling | HostControlArea | frequencyNominalMinimum | Float |  | etx | SCHEDULED AREA FREQUENCY MINIMUM (IN HZ; DEFAULT VALUE - 58 HZ). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | frequencyNominalMaximum | Float |  | etx | SCHEDULED AREA FREQUENCY MAXIMUM (IN HZ; DEFAULT VALUE - 62 HZ). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | frequencyTrip | Float |  | etx | FREQUENCY OFFSET TO TRIP AGC OFF AND CREATE AGC CONTROL ALARM (E.G. 0.45 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | gainAssist | Float |  | etx | ASSIST GAIN ON ACE (EG: 3.0) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | gainIntegralAssist | Float |  | etx | ASSIST GAIN ON INTEGRAL ACE. (EG: 0.4) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | gainEmergencyIntegral | Float |  | etx | EMERGENCY GAIN ON INTEGRAL ACE. (EG: 0.6) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | gainNominalIntegral | Float |  | etx | NOMINAL GAIN ON INTEGRAL ACE. (EG: 0.1) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | gainEmergency | Float |  | etx | EMERGENCY GAIN ON ACE. (EG: 10.0) (AGC ONLY) | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | gainNominal | Float |  | etx | NOMINAL GAIN ON ACE (NORMAL REGULATING RESPONSE) (EG: 1.4) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | governorResponseDeadband | Float |  | etx | Expected governor response frequency deviation deadband. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumInterchangeSchedule | Float |  | etx | MAX. INTERCHANGE SCHEDULE MW ALLOWED BEFORE ALARM IS ISSUED (AGC ONLY) (EG: 2000 MW) | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumInterruptableLoadReserve | Float |  | etx | Maximum interruptable load contribution to spinning or operating reserve. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | maxInterruptableLoadReserve
EnergyScheduling | HostControlArea | gainJointAGCPersistancyFeeback | Float |  | etx | Joint agc persistency feedback gain. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | gainJointAGCPersistFeeback
EnergyScheduling | HostControlArea | maximumJointACE | Float |  | etx | Maximum value of ACE before the request percentage is applied. The request percentage is only applied to the incremental value of ACE above this threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minimumJointACE | Float |  | etx | Minimum value of ACE before the request percentage is applied. The request percentage is only applied to the incremental value of ACE above this threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentJointAGCRequest | Float |  | etx | Percentage of area ACE that requester area is asking from other area. This is enterable on the joint AGC display for requester area. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | filterTimeConstantJointACE | Float |  | etx | Joint AGC ACE request filter time constant. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | jointAGCStallMW | Float |  | etx | Joint agc regulation MW amount that'll be issued at detected stall of ACE. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsJointAGCStall | Float |  | etx | Joint agc ACE stall check time threshold (in seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | lamdaDeadband | Float |  | etx | LAMBDA DEADBAND TO BE USED FOR PAYBACK OF INADVERTENT ACCUMULATION IN | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | frequencyBiasFactor | Float |  | etx | AREA LOAD BIAS -LOAD FREQUENCY SENSITIVITY- (MW/0.1HZ) (EG: 0.2% AREA CAP). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | loadReliefFirstMW | Float |  | etx | The control area load MW value for the first breakpoint in the load relief table. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | loadReliefLastMW | Float |  | etx | The control area load MW value for the last breakpoint in the load relief table. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | frequencyBiasFactorManual | Float |  | etx | Manually entered frequency bias in MW/0.1 Hz. Equal to FBIAS_OPA if manual entry of frequency bias is selected, otherwise it contains the most recent manually entered value of frequency bias. Modifiable online. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumMiscReserve | Float |  | etx | Maximum miscellaneous reserve contribution. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | triggerControlEcoDispatchMW | Float |  | etx | MW CHANGE TO TRIGGER CONTROL ED EXECUTION (EG: 25MW) (AGC ONLY) | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | triggerStudyEcoDispatchMW | Float |  | etx | MW CHANGE TO TRIGGER STUDY ED EXECUTION (EG: 50MW) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandMultiplerNotTracking | Float |  | etx | NOT TRACKING DEADBAND MULTIPLIER (EG: 2) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minutesOperatingReserve | Float |  | etx | Time period (in minutes) in which a unit's output can change to contribute to operating reserves. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentMWStepChangeAlarm | Float |  | etx | UNIT MW STEP CHANGE ALARM LEVEL (% OF UNIT CAPACITY) (EG:10%)(AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentUnitNotTrackingAlarm | Float |  | etx | UNIT NOT TRACKING ALARM LEVEL (PERCENT OF EQUIVALENT MSR) (AGC ONLY) (EG: 20% ). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandPercentOpReserveAlarm | Float |  | etx | OPERATING RESERVE ALARM DEADBAND (PERCENT OF OPER RESERVE REQUIREMENT) (EG: 5% ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | deadbandPercentOpRsrvAlarm
EnergyScheduling | HostControlArea | deadbandPercentRegReserveAlarm | Float |  | etx | REGULATING RESERVE ALARM DEADBAND (PERCENT OF REG RESERVE REQUIREMENT) (EG: 5% ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | deadbandPercentRegRsrvAlarm
EnergyScheduling | HostControlArea | deadbandPercentSpinReserveAlarm | Float |  | etx | SPINNING RESERVE ALARM DEADBAND (PERCENT OF ALARM LIMIT) (AGC ONLY) (EG: 5% ). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | deadbandPercentSpinRsrvAlarm
EnergyScheduling | HostControlArea | deadbandPercentTimeError | Float |  | etx | TIME ERROR DEADBAND (PERCENT OF ALARM LIMIT) (EG:5%). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentIntegrationMissing | Float |  | etx | percent threshold of missing samples in a regulation integration interval, if more than this percent samples are missing, quality (TRINBAD) for the interval’s integration will be declared 'bad' . | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandPercentTieLimitAlarm | Float |  | etx | TIE LINE FLOW LIMIT ALARMS DEADBAND (% OF LIMIT) (EG: 1%) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentFrequencyBias | FileName |  | etx | Percentage of frequency bias. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumInterchangeLossModel | Float |  | etx | MAXIMUM INTERCHANGE FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minimumInterchangeLossModel | Float |  | etx | MINIMUM INTERCHANGE FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumLoadLossModel | Float |  | etx | MAXIMUM LOAD FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minimumLoadLossModel | Float |  | etx | MINIMUM LOAD FOR BOUNDARY DEFINITION FOR THE BINS FOR LOSS MODELLING USED IN SETTING UP BOUNDARIES IN GENMODEL. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsEvaluateLossModel | Float |  | etx | IT IS THE NOMINAL TIME BETWEEN RE-EVALUATIONS OF PENALTY FACTORS FROM HISTORICAL LOSS MODEL IF RTNET HAS NOT EXECUTED. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minutesRegulatingReserve | Float |  | etx | Time period (in minutes) in which a unit's output can change to contribute to regulating reserves. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minimumResponseRateAlarm | Float |  | etx | MIN RESPONSE RATE ALARM LEVEL (MW/MIN) (EG: 0.10% AREA CAP) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumObligationImportMW | Float |  | etx | Maximum obligation Mw (Import) value used in the Target MW calculation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | maximumObligationExportMW | Float |  | etx | Maximum obligation Mw (Export) value used in the Target MW calculation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | rampDurationToStop | Float |  | etx | RSG Ramp duration to stop time. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | rampDurationToTarget | Float |  | etx | RSG Ramp duration to target in Minutes. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentCapOpReserveRequirement | Float |  | etx | AREA OPERATING RESERVE REQUIREMENT (MW) (EG 8% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | percentCapOpRsrvRequirement
EnergyScheduling | HostControlArea | percentCapOpReserveReqDefault | Float |  | etx | AREA REGULATING RESERVE REQUIREMENT (MW) (EG: 3% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | percentCapOpRsrvReqDefault
EnergyScheduling | HostControlArea | percentCapSpinReserveRequirement | Float |  | etx | SPINNING RESERVE REQUIREMENT (MW) (EG: 5% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | percentCapSpinRsrvReq
EnergyScheduling | HostControlArea | percentCapSpinRsrvReqDefault | Float |  | etx | AN EXCESSIVE ALARM WILL BE ISSUED IF THE INTEGRATED SCE EXCEEDS THIS THRESHOLD. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | deadbandIntegratedSCEAlarm | Float |  | etx | INTEGRATED SCE ALARM DEADBAND. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minutesSpinngReserve | Float |  | etx | Time period (in minutes) in which a unit's output can change to contribute to spinning reserves. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minutesFutureAdvisoryED | Float |  | etx | The number of minutes in the future to evaluate the load and transaction schedules at for the Advisory ED. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | cycleTimeMultiplier | Float |  | etx | AGC CONTROL CYCLE MULTIPLIER (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsAGCCycle | Float |  | etx | AGC CYCLE PERIOD IN SECONDS (EG: 4 SEC) (AGC ONLY) MUST BE AN INTEGER MULTIPLE OF THE CORRESPONDING SCADA SCAN PERIOD. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsAGCOff | Float |  | etx | AGC WILL START CYCLING THIS MANY SECONDS AFTER INITIALIZATION. (EG: 0 SEC) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsRegulationAllocation | Float |  | etx | Regulation Allocation limit period (in sec). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | tauFrequency | Float |  | etx | AREA FREQUENCY TIME CONSTANT (SECS) (EG: 10 SEC) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | tauLongTerm | Float |  | etx | UNIT LONG TERM ACCOUNT (PULSE CALIBRATION) TIME CONSTANT (SEC) (AGC) (EG: CORRESP TO 1 DAY = 24*3600 = 86400 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | tauRegulating | Float |  | etx | REGULATING (AREA CONTROL) TIME CONSTANT (SEC) (E.G. 30 SEC) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | tauShortTerm | Float |  | etx | UNIT SHORT TERM ACCOUNT (NOT TRACKING TEST) TIME CONSTANT (SEC) (AGC) (EG: 300 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | tauFilterLoad | Float |  | etx | TIME CONSTANT FOR FILTERING LOAD (SECS). (EG: 40 SEC) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsMinimumEcoDispatch | Float |  | etx | MINIMUM TIME PERIOD ALLOWED BETWEEN ECONOMIC DISPATCH EXECUTIONS.(AGC) (EG: 10 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsControlEcoDispatch | Float |  | etx | NOMINAL CONTROL ED RATE (SEC) (EG: 300 SEC) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsTimeErrorAlarm | Float |  | etx | TIME ERROR ALARM LIMIT IN SECONDS (EG: 2 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | timeErrorBias | Float |  | etx | (HZ/SEC) ACE EQUATION VARIABLE LITTLE B: AUTOMATIC TIME ERROR CORRECTION BIAS VALUE. * ENTER ABSOLUTE VALUE: NEGATION DONE IN THE CODE. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsDeadbandTimeError | Float |  | etx | The auto time error correction deadband (SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsMaximumTimeCorrection | Float |  | etx | The maximum amount of auto time error correction allowed (SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsAlarmResponse | Float |  | etx | NOM TIME TO REPEAT ALARM INSUFFICIENT AREA RESPONSE CAPABILITY (SEC) (EG: 600 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsUnitNotTrackingTest | Float |  | etx | NOM TIME TO RUN UNIT NOT TRACKING TEST (SEC) (AGC ONLY) (EG: 120 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsPauseThenSuspend | Float |  | etx | NOMINAL TIME FOR AGC PAUSE BEFORE SUSPEND IF NECESSARY (EG: 20 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsProductionCosting | Float |  | etx | nominal value for the periodicity of the production costing module in seconds. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsPrediction | Float |  | etx | PREDICTED TIME IN SEC FROM TNOW. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsDeadbandDynamicACE | Float |  | etx | DYNAMIC ACE DEADBAND TIME CONSTANT (AGC ONLY) (EG: 4 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsReserveCalculations | Float |  | etx | NOMINAL TIME TO PERFORM RESERVE CALCULATIONS (SEC) (AGC ONLY) (EG: 20 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsMinimumStudyEcoDispatch | Float |  | etx | MINIMUM TIME BETWEEN STUDY ED EXECUTIONS (SEC) (EG: 20 SEC) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | secondsMinStudyEcoDispatch
EnergyScheduling | HostControlArea | secondsStudyEcoDispatch | Float |  | etx | NOMINAL STUDY ED RATE (SEC) (EG: 600 SEC) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | minutesPendingFrequencySchedule | Float |  | etx | MINUTES FOR SENDING PENDING FREQUENCY SCHEDULE MESSAGE. (EG: 5 MIN). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | minutesPendingFreqSchedule
EnergyScheduling | HostControlArea | secondsZeroAssist | Float |  | etx | THRESHOLD TIME FOR ASSIST REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsZeroEmergency | Float |  | etx | THRESHOLD TIME FOR EMERGENCY REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | secondsZeroNormal | Float |  | etx | THRESHOLD TIME FOR NORMAL REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | variableFrequencyBiasMaximu | Float |  | etx | Variable frequency bias high limit in MW/0.1 Hz. Must be greater or equal to VFBMIN_OPA. Enterable offline. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | variableFrequencyBiasMinimum | Float |  | etx | Variable frequency bias low limit in MW/0.1 Hz. Must be less or equal to VFBMAX_OPA. Enterable offline. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentObjectCO2 | Float |  | etx | Weighting factor for CO2 in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentObjectiveFuel | Float |  | etx | Weighting factor for fuel in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentObjectiveNOX | Float |  | etx | Weighting factor for NOX in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | percentObjectiveSO2 | Float |  | etx | Weighting factor for SO2 in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | TRUE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | main | Boolean |  | etx | The MMS applications require that one of the HostControlAreas defined in the model be designated as the 'main' company. ERCOT may also opt for the decomposition of the model into areas, which requires an indication of which HostControlAreas are 'internal'. Note that the main designation is not necessarily synonymous with the internal designation since it is possible to have multiple internal HostControlAreas but only one main HostControlArea. | FALSE | TRUE | FALSE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | internal | Boolean |  | etx | The MMS applications require that one of the HostControlAreas defined in the model be designated as the 'main' company. ERCOT may also opt for the decomposition of the model into areas, which requires an indication of which HostControlAreas are 'internal'. Note that the main designation is not necessarily synonymous with the internal designation since it is possible to have multiple internal HostControlAreas but only one main HostControlArea. | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETXContingency | ContingencyGroup | study | Boolean |  | etx | T=activate the contigencies in the group. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | EnergyConsumerAlternateConnection | percentTransfer | Float |  | etx | Percentage of load transferred from parent load to target load. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | maximumActivePower | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | maximumReactivePower | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | minimumActivePower | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | minimumReactivePower | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | monitorActivePower | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | monitorReactivePower | Float |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | maximumMW | Float |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | minimumMW | Float |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | maximumMVAr | Float |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | minimumMVAr | Float |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETXMonitoring | BranchGroupTerminal | positiveFlowIn | Boolean |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | Monitored | eligible | Boolean |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | MonitoredGroup | active | Boolean |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass | ADConverterError | Float |  | etx | A to D converter error. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass | VoltageTransformerError | Float |  | etx | Voltage tranformer error. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass | CurrentTransformerError | Float |  | etx | Current transformer error. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass | Base | Float |  | etx | Base value. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass | BreakPoint | Float |  | etx | Break point for uncertainty model. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass | StandardDeviation | Float |  | etx | Standard deviation for uncertainty model. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | AccuracyClass | TranducerMaxError | Float |  | etx | Transducer maximum error. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | useLimitThreshold | Boolean |  | etx | Use the branch limit as threashold value, otherwise use Gate::thresholdValue. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | normalThreshold | Boolean |  | etx | Use the branch normal limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | emergencyThreshold | Boolean |  | etx | Use the branch emergency limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | loadshedThreshold | Boolean |  | etx | Use the branch loadshed limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | upperThreshold | Boolean |  | etx | Use upper limit (for FlowSummation and voltage). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | lowerThreshold | Boolean |  | etx | Use lower limit (for FlowSummation and voltage). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | changeThreshold | Boolean |  | etx | Use change limit for voltages. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | gatetype | EnumGateType |  | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | thresholdValue | Float |  | etx | Threshold value for gate type of (GE,GT,LE,LT,NE,EQ) with single gate input | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | limitPercentage | Float |  | etx | Percentage of the limit. 90% should enter 90. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | level | Boolean |  | etx | Level of the gate. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | GateInputPin | flowMW | Boolean |  | etx | If true, the input is a MW. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | GateInputPin | flowMVAR | Boolean |  | etx | If true the input is a MVAR. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | GateInputPin | flowMVA | Boolean |  | etx | If true the input is a MVA. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | GateInputPin | negate | Boolean |  | etx | If true, input is negated first and then input to the gate. only applicable to logical gates. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | GateInputPin | useAbsoluteValue | Boolean |  | etx | Use absolute value of input (only applies to analog inputs). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinFlow | eitherEnd | Boolean |  | etx | True if doing status input on a branch and want to check if either end is out. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinFlow | intoBus | Boolean |  | etx | Flow into the bus is positive. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinFlow | outOfBus | Boolean |  | etx | Flow out of the bus is positive. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinFlow | inputIsFlow | Boolean |  | etx | If true, the input is a flow, otherwise it is branch status. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveAction | enableArming | Boolean |  | etx | Enable arming. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionAnalog | actionValue | Float |  | etx | The value to reduce to or by. Used if no value from SCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionAnalog | isReduceTo | Boolean |  | etx | If true, action is a 'reduce to' otherwise it is a 'reduce by'. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionAnalog | actionValueFromSCADA | Boolean |  | etx | True, the action value is obtained from SCADA otherwise from actionValue attribute. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionSwitch | close | Boolean |  | etx | If true close the switch, otherwise open switch. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | RemedialActionScheme | active | Boolean |  | etx | User specified active. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | RemedialActionScheme | isRAS | Boolean |  | etx | This is a remedial action scheme (RAS). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | RemedialActionScheme | isRAP | Boolean |  | etx | This is a remedial action plan (RAP). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | AnalogLimitType | limitType | EnumLimitType |  | etx | Analog limit type. For ERCOT: normal rating, fifteenminuterating, twohourrating, and conductorrating. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OperatorShare | operatePercent | Float |  | etx | Operator share percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OwnerShare | ownPercent | Float |  | etx | Owner share percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Rating | ratingType | EnumRatingType |  | etx | Rating type: static (planning) or dynamic (temperature). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Rating | activateValue | Float |  | etx | Temperature. It is used to pick the actual rating to supervise againist. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AlternateLimit | highLimit | Float |  | etx | High Limit: The threshold above which the analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. The High Limit must be greater then the Low Limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AlternateLimit | lowLimit | Float |  | etx | Low Limit: The threshold below which the analog is considered in violation of the limit. When the high limit is null, only the low limit is checked for violation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogMeasMsg | message | String40 |  | etx | ANALOG MESSAGE TEXT - An alternate method of identifying a measurement for the alarm. Used instead of | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit | deadBand | Float |  | etx | Deadband: The value used in the rate of change limit comparison to eliminate extraneous alarms generated when the slope oscillates around a limit. The DBAND cannot be null or negative. The acceptable range is less than the magnitude of the smaller of LOWVAL or HIGHVAL if both are not null. Otherwise, it must be less than the absolute value of LOWVAL or HIGHVAL. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit | IgnoreLimitChecking | Boolean |  | etx | T = The rate of change limit is ignored when checking the analog for limit violation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit | lowerThreshold | Float |  | etx | The lower threshold of the rate of change beyond which the ANALOG is considered in violation of the limit. Values should be expressed as engineering units of change per unit of time. The value of the change will be checked for exceeding this threshold. One of HIGH or LOW may be null, but not both. If LOW is not null, then it must be negative. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit | timeConstant | String2 |  | etx | The filtering provided for rate of change limits is specified by this time constant, used to calculate the least squares slope. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit | triggerNetworkTopology | Boolean |  | etx | T = Network programs will be triggered when the rate of change limits are violated. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit | upperThreshold | Float |  | etx | Upper Threshold: Upper threshold of the rate of change beyond which the ANALOG is considered in violation of the limit. Values should be expressed as engineering units of change per unit of time. The value of the change will be checked for exceeding this threshold. One of HIGH or LOW may be null, but not both. If LOW is not null, then it must be negative. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | bitA | Boolean |  | etx | True = Bit A is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | bitB | Boolean |  | etx | True = Bit B is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | bitC | Boolean |  | etx | True = Bit C is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | bitD | Boolean |  | etx | True = Bit D is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | bitE | Boolean |  | etx | True = Bit E is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | bitF | Boolean |  | etx | True = Bit F is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | bitG | Boolean |  | etx | True = Bit G is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | value | Float |  | etx | The value of the SCADA constant argument. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlEvent | sequenceNumber | Integer |  | etx | Sequence of Command events. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlLock | invertLock | Boolean |  | etx | INVERT INTERLOCK (STATIC) T = Invert the sense of the interlocking status point, so a false status permits the setpoint control operation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlLock | lowerLimit | Float |  | etx | THE LOW VALUE OF THE VALID RANGE TO ALLOW SETPOINT ACTION. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlLock | upperLimit | Float |  | etx | THE HIGH VALUE OF THE VALID RANGE TO ALLOW SETPOINT ACTION. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | DiscreteMeasMsg | message | String40 |  | etx | Discrete MESSAGE TEXT: An alternate method of identifying a measurement for the alarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementAlias | deviceName | String4 |  | etx | Device Name: Alias Device name to use when identifying this analog in an ISD download request. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementAlias | deviceType | String6 |  | etx | Device Type: Alias Device Type name to use when identifying this analog in an ISD download request. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementAlias | site | String8 |  | etx | Site: Alias name is to be used when requesting update of value and quality from this site, regardless of whether it is defined as the primary or the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementAlias | substation | String8 |  | etx | Substation: Alias Substation name to use when identifying this analog in an ISD download request. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | abnormalForAlarm | Boolean |  | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | abnormalForSCADA | Boolean |  | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | audibleTone | Boolean |  | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | inhibitAbnormalForAlarrm | Boolean |  | etx | Permanently Inhibit the flag of abnormalForAlarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | inhibitAbnormalForSCADA | Boolean |  | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | inhibitAudibleTone | Boolean |  | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | inhibitLoggingAndAlarmList | Boolean |  | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | inhibitUnacknowledgedAlarmList | Boolean |  | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | inhibitUnackAlarmList
ETXSCADA | MeasurementLocation | initiallyInhibit | Boolean |  | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | loggingAndAlarmList | Boolean |  | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | normallyDead | Boolean |  | etx | A flag indicating whether the location is normally dead. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | overrideDefaultInhibitDefinition | Boolean |  | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | overrideDefaultnhibitDef
ETXSCADA | MeasurementLocation | unacknowledgedAlarmList | Boolean |  | etx | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ControlZone | useTelemeteredCost | Boolean |  | etx | Source for incemental cost to us. True, use telemetered source. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ForbiddenZone | maximumLimit | Boolean |  | etx | (MW) max generator MW of the forbidden zone. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ForbiddenZone | minimumLimit | Boolean |  | etx | (MW) min generator MW of the forbidden zone. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType | units | String15 |  | etx | Units of the fuel type (e.g. barrels, mbtu). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType | fuelEffFactor | PU |  | etx | The efficiency factor for the fuel (per unit) in terms of the effective MBtu absorbed. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType | fuelHeatContent | Float |  | etx | The amount of heat (Btu) per weight (or volume) of the given type of fuel. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType | outputSO2 | Float |  | etx | Amout of SO2 produced by fuel prior to scrubbing per MBTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType | outputCO2 | Float |  | etx | Amount of CO2 produced by fuel prior to scrubbing per MBTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType | outputNOX | Float |  | etx | Amount of NOX produced by fuel prior to scrubbing per MBTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | FossilFuelType | fuelCost | CostPerHeatUnit |  | etx | The cost in terms of heat value for the given type of fuel. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | GenerationType | economicallyDispatchable | Boolean |  | etx | Economically dispatchable. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | GenerationType | excludeFromTotal | Boolean |  | etx | Exclude from the total generation. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | InadvertentInterchgDay | dayOfWeek | EnumDayTypeName |  | etx | The day of the week the profile is in effect. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadActingAsResource | underFrequency | Boolean |  | etx | Of underfrequency relay type. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadActingAsResource | interruptable | Boolean |  | etx | Is interruptable? | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadActingAsResource | controllable | Boolean |  | etx | Is controllable? | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadActingAsResource | powerMeasured | Boolean |  | etx | Power is telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadActingAsResource | breakerMeasured | Boolean |  | etx | Breaker status is telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadReliefLevel | load | Float |  | etx | MW load level for load relieve reserve. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadReliefLevel | spinningReserve | Float |  | etx | Hold load relief spinning reserve contribution for that particular control area. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage | changeThreshold | Float |  | etx | Change to compare two successive values. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage | percentPrimaryBackupComparison | Float |  | etx | comparison threshold for primary backup meas in percent. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | percentPrimBackupComparison
ETX_Areva | MeasurementUsage | filterTimeConstant | Float |  | etx | Filter time constant. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | maxCapacityMW | Float |  | etx | Maximum possible capacitiy in MW. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | poleCompensationFactor | Float |  | etx | POLE COMPENSATION FACTOR USED IN THE CALCULATION OF DESIRED PLC CHANGE (EG: 0.5) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | zeroCompensationFactor | Float |  | etx | ZERO COMPENSATION FACTOR USED IN THE CALCULATION OF DESIRED PLC CHANGE (EG: 2.0) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | signalDiscretizationFactor | Float |  | etx | PLC control signal Discretization factor. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | errorDeadbandMW | Float |  | etx | PLC CONTROL ERROR DEADBAND (MW) (EG: 0.5% PLC CAP). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | percentFrequentBias | Float |  | etx | PLC REGULATING FREQUENCY BIAS (MW/ 0.1HZ) (EG: 3.3% PLC CAP BASED ON A 5% PERMANENT DROOP CHARACTERISTIC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | deadbandFrequencyDeviation | Float |  | etx | Frequency deviation deadband for Feed-Forward correction (in Hz). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | gain | Float |  | etx | Gain of controller. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | gainFirstStage | Float |  | etx | Lead-Lag Compensator gain in first stage. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | gainSecondStage | Float |  | etx | Lead-Lag Compensator gain in second stage. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | kneePointMW | Float |  | etx | Knee-point value (MW). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | percentDeadbandNotTracking | Float |  | etx | DEADBAND FOR NOT TRACKING TEST MW CHANGE REQUIREMENT. IF ACCUMULATED PLC PULSES SINCE LAST NT TEST IS LESS THAN THIS VALUE THE NT TEST IS NOT MEANINGFUL AND SO IS NOT RUN. (EG: 5% PLC CAP). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | deadbandSetpointSignal | Float |  | etx | PLC setpoint signal deadband (defined in MW). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | percentCapDecay | Float |  | etx | Percent of CAPMX to use in decay calculation (affects speed or rate). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | percentTauDecay | Float |  | etx | Percent of tauSmallChangeResponse to use in time-to-wait for decay. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | pendingMWFactor | Float |  | etx | Pending MW weighting factor. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | pulseCalibrationLower | Float |  | etx | PULSE CALIBRATION FOR LOWER CONTROL (ONE SECOND PULSE = X MWS) TYPICAL VALUE: SAME AS FOR PULCALUP_PLC. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | pulseCalibrationRaise | Float |  | etx | PULSE CALIBRATION FOR RAISE CONTROL (ONE SECOND PULSE = X MWS) TYPICAL VALUE: ASSUME MAX PULSE = 1 SECOND MAX PULSE TYPICALLY = 2 TIMES MSR WHICH TYPICALLY IS 4% PLC CAPACITY PER. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | secondsPulseMinimum | FileName |  | etx | (sec) control signal pulse minimum length via scada to the generating plant PLC. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | secondsPulseMaximum | Float |  | etx | (sec) control signal pulse maximum length via scada to the generating plant PLC. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | regulationParticipationFactor | Float |  | etx | REGULATING PARTICIPATION FACTOR (EG: 1.0). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | regulationPriority | Integer |  | etx | Regulation priority within the assigned regulation level (Operator enterable). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | tauSmallChangeResponse | Float |  | etx | PLC RESPONSE TIME CONSTANT FOR SMALL CHANGES (SEC) (EG: 20 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | secondsEnergyDown | Float |  | etx | Timer in seconds representing the time needed by a PLC to build the boiler stored energy after moving in the down direction. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | secondsEnergyUp | Float |  | etx | Timer in seconds representing the time needed by a PLC to build the boiler stored energy after moving in the up direction. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | secondsNoiseRejection | Float |  | etx | Noise Rejection counter limit in seconds (EG: 20 SEC). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | secondsReversal | Float |  | etx | PLC REVERSAL PULSE COUNTER LIMIT IN SECONDS (EG: 20 SEC) MIN TIME AFTER WHICH AGC WILL PERMIT ISSUANCE OF A REVERSE PULSE. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | secondsMinimumForbiddenCrossing | Float |  | etx | PLC MINIMUM TIME BETWEEN FORBIDDEN ZONE CROSSINGS. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | secondsMinForbiddenCrossing
ETX_Areva | StartGroup | maximumSimultaneous | Integer |  | etx | maximum number which can start simultaneously. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | TieEnd | tauJointAGCLoadFollowing | Float |  | etx | Time constant for filtering joint AGC load following component (requester only).. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | TieEnd | participationFactorJointAGC | Float |  | etx | Joint AGC participation factor. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | TieEnd | priorityJointAGC | Integer |  | etx | Joint AGC priority level. Lowest numbered ties will be used first. | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | TieEnd | percentChangeAlarm | Float |  | etx | TiePointEnd MW STEP CHANGE ALARM LEVEL (% OF maximuInMW of TiePointEnd) (EG: 10%) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_ABB | LimitLogicType | preContLimitType | EnumPreContLimitType |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | LimitLogicType | postContLimitType | EnumPostContLimitType |  | etx |  | FALSE | TRUE | FALSE | FALSE |  | FALSE
MarketOperations | Contingency | probabilityOfOccurance | Float |  | etx | A number between 0 and 1. Contingencies with a probability less than 0.5 are considered 'low probability' contingencies. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | responseTime | Integer |  | etx | the time frame of response in seconds for the components associated with this contingency. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | generationLoss | Float |  | etx | The amount (in MW) of generation you expect the contingency to lose. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | loadLoss | Float |  | etx | The amount (in MW) of load you expect the contingency to lose. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | enableRedefinition | Boolean |  | etx | T=enable F=disable dynamic redefinition. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | enableSPS | Boolean |  | etx | T=enable F=disable SPS functions. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | noStudy | Boolean |  | etx | do not study regardless of groups. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | generatorParticipationFactor | EnumGeneratorParticipationFactor |  | etx | Short/Long. | FALSE | FALSE | TRUE | FALSE |  | FALSE
MarketOperations | Contingency | default | Boolean |  | etx | active if in an active group. | FALSE | FALSE | TRUE | FALSE |  | FALSE
Domain

## Associations
Package | ClassA | Association | ClassB | Name Space | ClassARoleName (RDF RoleA) | ClassARoleName (RDF RoleB) | Ac | Aa | Ba | Bc | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data
CIMCore | SubControlArea | Contains | GeneratingUnit | cim | SubControlArea | GeneratingUnits | 0..1 | ---- | ---- | 0..n | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RegulatingCondEq | HasA | RegulationSchedule | cim | RegulatingCondEqs | RegulationSchedule | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | HasA | RegulationSchedule | cim | TapChangers | RegulationSchedule | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValue | HasA | MeasurementValueSource | cim | MeasurementValues | MeasurementValueSource | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | MemberOf | LoadArea | cim | EnergyConsumers | LoadArea | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ConductingEquipment | UsesA | BaseVoltage | cim | ConductingEquipments | BaseVoltage | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | AreaLoadCurve | UsesA | Season | cim | AreaLoadCurves | Season | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Measurement | UsesA | LimitSet | cim | Measurements | LimitSets | 0..n | ---- | ---- | 0..n | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Measurement | UsesA | MeasurementType | cim | Measurements | MeasurementType | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Measurement | UsesA | Unit | cim | Measurements | Unit | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Measurement | MemberOf | PowerSystemResource | cim | Contains_Measurements | MemberOf_PSR | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroGeneratingUnit | MemberOf | HydroPowerPlant | cim | Contain_HydroGeneratingUnit | MemberOf_HydroPowerPlant | 0..n | ---- | <> | 1..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GenUnitOpSchedule | ScheduleFor | GeneratingUnit | cim | GenUnitOpSchedule | GeneratingUnit | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GenUnitOpCostCurve | MemberOf | GeneratingUnit | cim | GenUnitOpCostCurves | GeneratingUnit | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | GrossToNetMWCurve | MemberOf | GeneratingUnit | cim | GrossToNetMWCurves | GeneratingUnit | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | MemberOf | GeneratingUnit | cim | Contains_SynchronousMachines | MemberOf_GeneratingUnit | 0..1 | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | AirCompressor | DrivenBy | CombustionTurbine | cim | Drives_AirCompressor | DrivenBy_CombustionTurbine | 0..1 | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | AirCompressor | MemberOf | CAESPlant | cim | Contain_AirCompressor | MemberOf_CAESPlant | 1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit | MemberOf | CAESPlant | cim | Contain_ThermalGeneratingUnit | MemberOf_CAESPlant | 0..1 | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | SteamSendoutSchedule | MemberOf | CogenerationPlant | cim | SteamSendoutSchedule | CogenerationPlant | 0..1 | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit | MemberOf | CombinedCyclePlant | cim | Contain_ThermalGeneratingUnits | MemberOf_CombinedCyclePlant | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ThermalGeneratingUnit | MemberOf | CogenerationPlant | cim | Contain_ThermalGeneratingUnits | MemberOf_CogenerationPlant | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartMainFuelCurve | MemberOf | StartupModel | cim | StartMainFuelCurve | StartupModel | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartIgnFuelCurve | MemberOf | StartupModel | cim | StartIgnFuelCurve | StartupModel | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartRampCurve | MemberOf | StartupModel | cim | StartRampCurve | StartupModel | 0..1 | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionAccount | MemberOf | ThermalGeneratingUnit | cim | EmmissionAccounts | ThermalGeneratingUnit | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | EmissionCurve | MemberOf | ThermalGeneratingUnit | cim | EmissionCurves | ThermalGeneratingUnit | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | StartupModel | MemberOf | ThermalGeneratingUnit | cim | StartupModel | ThermalGeneratingUnit | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FossilFuel | Fuels | ThermalGeneratingUnit | cim | FossilFuels | ThermalGeneratingUnit | 0..n | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule | MemberOf | ThermalGeneratingUnit | cim | FuelAllocationSchedules | ThermalGeneratingUnit | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | FuelAllocationSchedule | Requires | FossilFuel | cim | FuelAllocationSchedule | FossilFuel | 0..n | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatRateCurve | MemberOf | ThermalGeneratingUnit | cim | HeatRateCurve | ThermalGeneratingUnit | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | ShutdownCurve | MemberOf | ThermalGeneratingUnit | cim | ShutdownCurve | ThermalGeneratingUnit | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | IncrementalHeatRateCurve | MemberOf | ThermalGeneratingUnit | cim | IncrementalHeatRateCurve | ThermalGeneratingUnit | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HeatInputCurve | MemberOf | ThermalGeneratingUnit | cim | HeatInputCurve | ThermalGeneratingUnit | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPumpOpSchedule | HasA | HydroPump | cim | HydroPumpOpSchedule | HydroPump | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | TargetLevelSchedule | HasA | Reservoir | cim | TargetLevelSchedule | Reservoir | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | InflowForecast | HasA | Reservoir | cim | InflowForecast | Reservoir | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPump | MemberOf | HydroPowerPlant | cim | Contain_HydroPumps | MemberOf_HydroPowerPlant | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | SpillsTo | Reservoir | cim | SpillsInto | SpillsFrom | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | Reservoir | ProvidesWaterTo | HydroPowerPlant | cim | Reservoir | HydroPowerPlants | 0..1 | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroGenEfficiencyCurve | HasA | HydroGeneratingUnit | cim | HydroGeneratingEfficiencyCurves | HydroGeneratingUnit | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | PenstockLossCurve | HasA | HydroGeneratingUnit | cim | PenstockLossCurve | HydroGeneratingUnit | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | TailbayLossCurve | HasA | HydroGeneratingUnit | cim | TailbayLossCurve | HydroGeneratingUnit | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | LevelVsVolumeCurve | HasA | Reservoir | cim | LevelVsVolumeCurve | Reservoir | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | SteamSupply | Supplies | SteamTurbine | cim | SteamSupplys | SteamTurbines | 0..n | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CTTEMPMWCurve | MemberOf | CombustionTurbine | cim | CTTempMWCurve | CombustionTurbine | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMGenerationDynamics | CombustionTurbine | Uses | HeatRecoveryBoiler | cim | CombustionTurbines | HeatRecoveryBoiler | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | Drives | PrimeMover | cim | Drives_SynchronousMachine | DrivenBy_PrimeMover | 0..n | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemotePoint | MemberOf | RemoteUnit | cim | Contains_RemotePoints | MemberOf_RemoteUnit | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMSCADA | RemoteUnit | AttachedTo | CommunicationLink | cim | Contain_RemoteUnits | MemberOf_CommunicationLinks | 0..n | ---- | ---- | 1..n | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValue | LinksTo | RemoteSource | cim | MeasurementValue | RemoteSource | 1 | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Control | ControlledBy | RemoteControl | cim | Control | RemoteControl | 1 | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | VoltageLevel | HasA | BaseVoltage | cim | VoltageLevel | BaseVoltage | 0..n | ---- | ---- | 1..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | CompositeSwitch | MemberOf | Substation | cim | Contains_CompositeSwitches | MemberOf_Substation | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Switch | MemberOf | CompositeSwitch | cim | Switches | CompositeSwitch | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | MemberOf | ConductorType | cim | Conductors | ConductorType | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireArrangement | MemberOf | ConductorType | cim | WireArrangements | ConductorType | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | WireArrangement | MemberOf | WireType | cim | WireArrangements | WireType | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | VoltageControlZone | ControlledBy | BusbarSection | cim | VoltageControlZone | BusbarSection | 0..1 | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | VoltageControlZone | RegulatedBy | RegulationSchedule | cim | VoltageControlZones | RegulationSchedule | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | HeatExchanger | MemberOf | PowerTransformer | cim | HeatExchanger | PowerTransformer | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | To | WindingTest | cim | To_TransformerWindings | To_WindingTest | 0..n | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | FromTest | WindingTest | cim | From_TransferWinding | From_WindingTests | 1 | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProduction | HydroPump | DrivenBy | SynchronousMachine | cim | Drives_HydroPump | DrivenBy_SynchronousMachine | 0..1 | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Control | Controls | RegulatingCondEq | cim | Controls | ControlledBy_RegulatingCondEq | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TransformerWinding | HasA | PowerTransformer | cim | Contains_TransformerWindings | MemberOf_PowerTransformer | 0..n | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | HasA | TransformerWinding | cim | TapChangers | TransformerWinding | 0..n | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | MVArCapabilityCurve | HasA | SynchronousMachine | cim | MVArCapabilityCurves | SynchronousMachines | 0..n | ---- | <> | 1..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | SynchronousMachine | HasDefault | MVArCapabilityCurve | cim | InitiallyUsedBySynchronousMachine | InitiallyUsesMVArCapabilityCurve | 1..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Line | MemberOf | SubGeographicalRegion | cim | Lines | Region | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | AreaLoadCurve | UsesA | DayType | cim | AreaLoadCurves | DayType | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadDemandModel | MemberOf | EnergyConsumer | cim | LoadDemandModels | EnergyConsumer | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | AreaLossCurve | HasA | LoadArea | cim | AreaLossCurves | LoadArea | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadDemandModel | BasedOn | DayType | cim | LoadDemandModels | DayType | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadDemandModel | BasedOn | Season | cim | LoadDemandModels | BasisFor | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | EnergyConsumer | MemberOf | PowerCutZone | cim | EnergyConsumers | PowerCutZone | 1..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | AreaLoadCurve | HasA | LoadArea | cim | AreaLoadCurves | LoadArea | 0..n | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMLoadModel | NonConformLoadSchedule | MemberOf | EnergyConsumer | cim | NonConformLoadSchedules | EnergyConsumer | 0..n | ---- | <> | 1 | TRUE | FALSE | TRUE | FALSE |  | FALSE
CIMTopology | ConnectivityNode | MemberOf | TopologicalNode | cim | ConnectivityNodes | TopologicalNode | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | TopologicalNode | MemberOf | TopologicalIsland | cim | TopologicalNodes | TopologicalIsland | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Terminal | ConnectedTo | ConnectivityNode | cim | Terminals | ConnectivityNode | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMTopology | ConnectivityNode | MemberOf | EquipmentContainer | cim | ConnectivityNodes | MemberOf_EquipmentContainer | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionEquipment | HasA | Unit | cim | ProtectionEquipments | Unit | 0..n | ---- | ---- | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | ProtectionEquipment | Operates | ProtectedSwitch | cim | OperatedBy_ProtectionEquipments | Operates_Breakers | 0..n | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMProtection | RecloseSequence | MemberOf | ProtectedSwitch | cim | RecloseSequences | Breaker | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ConductingEquipment | ProtectedBy | ProtectionEquipment | cim | ConductingEquipments | ProtectionEquipments | 0..n | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | PSRType | HasA | PowerSystemResource | cim | PSRType | PowerSystemResource | 0..1 | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | BasePower | MemberOf | BaseVoltage | cim | BasePower | BaseVoltage | 0..1 | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | PowerSystemResource | MemberOf | Company | cim | Operates_PSRs | OperatedBy_Companies | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | MemberOf | EquipmentContainer | cim | Contains_Equipments | MemberOf_EquipmentContainer | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Terminal | ExternalConnectionFor | ConductingEquipment | cim | Terminals | ConductingEquipment | 0..n | ---- | <> | 1..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Substation | MemberOf | SubControlArea | cim | Contain_Substations | MemberOf_SubControlArea | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | VoltageLevel | MemberOf | Substation | cim | Contains_VoltageLevels | MemberOf_Substation | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Bay | MemberOf | Substation | cim | Contains_Bays | MemberOf_Substation | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Bay | MemberOf | VoltageLevel | cim | Contains_Bays | MemberOf_VoltageLevel | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | CurveData | HasA | Curve | cim | CurveScheduleDatas | CurveSchedule | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IdentifiedObject | MemberOf | ModelingAuthoritySet | cim | IdentifiedObjects | ModelingAuthoritySet | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | ModelingAuthoritySet | MemberOf | ModelingAuthority | cim | ModelingAuthoritySets | ModelingAuthority | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | SubGeographicalRegion | MemberOf | GeographicalRegion | cim | Regions | Region | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Substation | MemberOf | SubGeographicalRegion | cim | Substations | Region | 0..n | ---- | <> | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | IrregularTimePoint | MemberOf | IrregularIntervalSchedule | cim | TimePoints | IntervalSchedule | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | RegularTimePoint | MemberOf | RegularIntervalSchedule | cim | TimePoints | IntervalSchedule | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | OutageSchedule | MemberOf | PowerSystemResource | cim | OutageSchedule | PSR | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | OutageSchedule | OperatedBy | SwitchingOperation | cim | OutageSchedule | SwitchingOperations | 0..1 | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | Switch | OperatedBy | SwitchingOperation | cim | Switches | SwitchingOperations | 0..n | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMOutage | ClearanceTag | AssignedTo | ConductingEquipment | cim | ClearanceTags | ConductingEquipment | 0..n | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Limit | MemberOf | LimitSet | cim | Limits | LimitSet | 0..n | ---- | <> | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | Terminal | MeasuredBy | Measurement | cim | Terminal | Measurements | 0..1 | ---- | ---- | 0..n | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | MeasurementValueQuality | MemberOf | MeasurementValue | cim | MeasurementValueQuality | MeasurementValue | 0..1 | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Control | Controls | Unit | cim | Controls | Unit | 0..n | ---- | ---- | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Control | UsesA | ControlType | cim | Control | ControlType | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | ValueToAlias | MemberOf | ValueAliasSet | cim | Values | ValueAliasSet | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | ValueAliasSet | Controls | Command | cim | ValueAliasSet | Controls | 0..1 | ---- | ---- | 0..n | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Discrete | AliasedBy | ValueAliasSet | cim | Discrete | ValueAliasSet | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | Command | ControlledBy | Discrete | cim | ControlledBy_Control | MeasuredBy_Measurement | 0..1 | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | SetPoint | ControlledBy | Analog | cim | ControlledBy_Control | MeasuredBy_Measurement | 0..1 | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | RegulatingCondEq | UsesA | Measurement | cim | RegulatingCondEqs | Measurement | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMWires | TapChanger | Regulates | Measurement | cim | TapChangers | Measurement | 0..n | ---- | ---- | 0..1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogValue | MemberOf | Analog | cim | Contain_MeasurementValues | MemberOf_Measurement | 0..n | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | DiscreteValue | MemberOf | Discrete | cim | Contain_MeasurementValues | MemberOf_Measurement | 0..n | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | StringMeasurementValue | MemberOf | StringMeasurement | cim | Contains_MeasurementValues | MemberOf_Measurement | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | MemberOf | Accumulator | cim | Contain_MeasurementValues | MemberOf_Measurement | 0..n | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogLimit | MemberOf | AnalogLimitSet | cim | Limits | LimitSet | 0..n | ---- | <> | 1 | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorLimit | MemberOf | AccumulatorLimitSet | cim | Limits | LimitSet | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AnalogLimitSet | Limits | Analog | cim | LimitSets | Measurements | 0..n | ---- | ---- | 0..n | TRUE | FALSE | FALSE | FALSE |  | FALSE
CIMMeas | AccumulatorLimitSet | Limits | Accumulator | cim | LimitSets | Measurements | 0..n | ---- | ---- | 0..n | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMFinancial | BusinessUnit | PartOfA | Company | cim | Company | BusinessUnits | 0..n | ---- | <> | 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
EnergyScheduling | HostControlArea | OperatedBy | ControlAreaOperator | cim | ControlledBy | Controls | 1..1 | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
CIMCore | SubControlArea | OperatesAs | HostControlArea | cim | SubControlAreas | HostControlArea | 0..n | ---- | ---- | 1..1 | TRUE | TRUE | FALSE | FALSE |  | FALSE
CIMLoadModel | LoadArea | MemberOf | SubControlArea | cim | MemberOf | MayContain | 0..1 | ---- | ---- | 0..1 | FALSE | FALSE | FALSE | FALSE |  | FALSE
ETXContingency | ContingencyGroupMember | IsMemberOf | ContingencyGroup | etx | ContingencyGroup | ContingencyGroupMember | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXContingency | ContingencyGroupMember | HasA | Contingency | etx | Contingency | ContingencyGroupMember | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | ConductingEquipment | BelongsTo | PerformanceModelingGroup | etx | PerformanceModelingGroup | ConductingEquipment | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | ConductingEquipment | BelongsTo | TransmissionServiceProvider | etx | TransmissionServiceProvider | ConductingEquipment | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | Substation | BelongsTo | TransmissionServiceProvider | etx | TransmissionServiceProvider | Substation | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | SynchronousMachine | ControlledBy | QualifiedServiceEntity | etx | QualifiedServiceEntity | SynchronousMachine | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | ACLineSegment | BelongsTo | LoadZone | etx | LoadZone | ACLineSegment | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | EnergyConsumer | BelongsTo | LoadZone | etx | LoadZone | EnergyConsumer | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | SynchronousMachine | BelongsTo | LoadZone | etx | LoadZone | SynchronousMachine | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | EnergyConsumer | BelongsTo | LoadGroup | etx | LoadGroup | EnergyConsumer | 1..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | EnergyConsumerAlternateConnection | MemberOf | EnergyConsumer | etx | EnergyConsumerAlternateconnection | EnergyConsumer | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | EnergyConsumerAlternateConnection | TransferTo | EnergyConsumer | etx | TransferTo_EnergyConsumer | TransferFrom_EnergyConsumerAlternateConnection | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | LoadGroup | MemberOf | LoadZone | etx | LoadZone | LoadGroup | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXLoadModel | LoadZone | MemberOf | LoadArea | etx | LoadArea | LoadZone | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | RegularIntervalSchedule | HasA | Season | etx | RegularIntervalSchedule | Season | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | RegularIntervalSchedule | HasA | DayType | etx | RegularIntervalSchedule | DayType | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | AngleDifferenceLimitSet | MemberOf | AngleDifference | etx | AngleDifferenceLimitSet | AngleDifference | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | AngleDifference | MonitorNodeA | ConnectivityNode | etx | AngleDifference | ConnectivityNodeA | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | AngleDifference | MonitorNodeB | ConnectivityNode | etx | AngleDifference | ConnectivityNodeB | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMCore | BaseVoltage | IsMonitored | VoltageMonitored | etx | BaseVoltage | VoltageMonitored | 1 | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | BusbarSection | IsMonitored | VLSBusBarMonitored | etx | BusbarSection | VLSBusBarMonitored | 1 | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | Monitored | MemberOf | MonitoredGroup | etx | Monitored | MonitoredGroup | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | VLSBusBarMonitored | Uses | VoltageLimitSet | etx | VLSBusBarMonitored | VoltageLimitSet | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | VoltageMonitored | Uses | VoltageLimitSet | etx | VoltageMonitored | VoltageLimitSet | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroupTerminal | MemberOf | BranchGroup | etx | BranchGroupTerminal | BranchGroup | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXMonitoring | BranchGroupTerminal | References | Terminal | etx | BranchGroupTerminal | Terminal | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | HasA | AccuracyClass | etx | AnalogValue | AccuracyClass | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | EnergyConsumer | HasA | AccuracyClass | etx | EnergyConsumer | AccuracyClass | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | SynchronousMachine | HasA | AccuracyClass | etx | SynchronousMachine | AccuracyClass | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | StationSupplyWRCurve | HasA | StationSupply | etx | StationSupplyWRCurve | StationSupply | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMLoadModel | StationSupply | Follows | SynchronousMachine | etx | StationSupply | SynchronousMachine | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | PowerTransformer | HasAMaster | PowerTransformer | etx | PowerTransformer | PowerTransformer | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | TransformerImpedanceCurve | HasA | TransformerWinding | etx | TransformerImpedanceCurve | TransformerWinding | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXNetwork | PhaseShifterImpedanceCurve | HasA | TapChanger | etx | PhaseShifterImpedanceCurve | TapChanger | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | TapRatioCurve | HasA | TapChanger | etx | TapRatioCurve | TapChanger | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | TapChanger | HasAMaster | TapChanger | etx | TapChanger | TapChanger | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMTopology | ConnectivityNode | BelongsTo | ConnectivityNodeGroup | etx | ConnectivityNode | ConnectivityNodeGroup | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXPlanning | ConnectivityNodeGroup | BelongsTo | PlanningArea | etx | ConnectivityNodeGroup | PlanningArea | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXPlanning | ConnectivityNodeGroup | BelongsTo | PlanningZone | etx | ConnectivityNodeGroup | PlanningZone | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinFlow | HasA | Terminal | etx | PinFlow | Terminal | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | GateInputPin | MemberOf | Gate | etx | Gate | GateInputPin | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinVoltage | HasA | ConnectivityNode | etx | ConnectivityNode | PinVoltage | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | Has | TriggerCondition | etx | TriggerCondition | Gate | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Gate | HasResulting | TriggerCondition | etx | TriggerCondition | ResultingGate | 1 | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinSwitch | HasA | Switch | etx | PinSwitch | Switch | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinGate | HasA | Gate | etx | PinGate | Gate | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinBranchGroup | BelongsTo | BranchGroup | etx | PinBranchGroup | BranchGroup | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PinTriggerCondition | HasA | TriggerCondition | etx | PinTriggerCondition | TriggerCondition | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | TriggerCondition | Has | RemedialActionScheme | etx | TriggerCondition | RemedialActionScheme | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | StageTrigger | TriggeredBy | TriggerCondition | etx | StageTrigger | TriggerCondition | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | StageTrigger | MemberOf | Stage | etx | StageTrigger | Stage | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | Stage | MemberOf | RemedialActionScheme | etx | Stage | RemedialActionScheme | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | PrivateProtectiveActions | MemberOf | StageTrigger | etx | PrivateProtectiveActions | StageTrigger | 1 | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveAction | MemberOf | ProtectiveActions | etx | ProtectiveAction | ProtectiveActions | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveAction | ArmedBy | DiscreteValue | etx | ProtectiveAction | DiscreteValue | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionShare | Has | SharedProtectiveActions | etx | ProtectiveActionShare | SharedProtectiveActions | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionAnalog | ReduceBy | AnalogValue | etx | ProtectiveActionAnalog | AnalogValue | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectActSynchronousMachine | References | SynchronousMachine | etx | ProtectiveActionSynchronousMachine | SynchronousMachine | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectActStationReduction | References | Substation | etx | ProtectiveActionStationReduction | Substation | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectActEnergyConsumer | References | EnergyConsumer | etx | ProtectiveActionEnergyConsumer | EnergyConsumer | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRASE | ProtectiveActionSwitch | References | Switch | etx | ProtectiveActionSwitch | Switch | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OwnerShare | Owns | PowerSystemResource | etx | OwnerShare | PowerSystemResource | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Owner | HasPercentage | OwnerShare | etx | Owner | OwnerShare | 1..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Rating | MemberOf | OwnerShareRatings | etx | Rating | OwnerShareRating | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OwnerShareRatings | BasedOn | DynamicRatingAnalogValue | etx | OwnerShareRatings | DynamicRatingsAnalogValue | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | AnalogValueLimit | FillIn | AnalogLimit | etx | AnalogValueLimit | AnalogLimit | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | AnalogValueLimit | Has | AnalogLimitType | etx | AnalogValueLimit | AnalogLimitType | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Rating | Uses | Unit | etx | Rating | Unit | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | OperatorShare | Operates | PowerSystemResource | etx | OperatorShare | PowerSystemResource | 1..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXRating | Operator | HasPercentage | OperatorShare | etx | Operator | OperatorShare | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | RegulatingCondEq | RegulatedBy | LoadBasedRegulationCurve | etx | RegulatingCondEquipment | LoadBasedRegulationSchedule | 0..1 | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | RegulatingCondEq | Regulates | Terminal | etx | RegulatingCondEquipment | Terminal | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | RegulatingCondEq | Regulates | ConnectivityNode | etx | RegulatingCondEquipment | ConnectivityNode | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | TapChanger | Regulates | Terminal | etx | TapChanger | Terminal | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMWires | TapChanger | Regulates | ConnectivityNode | etx | TapChanger | ConnectivityNode | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | HasNameOf | AccumulatorName | etx | AccumulatorValue | AccumulatorName | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AccumulatorValue | HasTypeOf | AccumulatorType | etx | AccumulatorValue | AccumulatorType | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | HasNameOf | AnalogLimitName | etx | AnalogLimit | AnalogLimitName | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | HasNameOf | AnalogName | etx | AnalogValue | AnalogName | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | HasNameOf | CommandName | etx | Command | CommandName | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | HasNameOf | DiscreteName | etx | DiscreteValue | DiscreteName | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | SetPoint | HasNameOf | SetPointName | etx | SetPoint | SetPointName | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | GenericEquipment | HasTypeOf | GenericEquipmentType | etx | GenericEquipment | GenericEquipmentType | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | HasTypeOf | DiscreteType | etx | DiscreteValue | DiscreteType | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AlternateLimit | BelongTo | AlternateLimitSet | etx | AlternateLimti | AlternateLimitSet | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AlternateLimit | BelongTo | LimitAlarmCategory | etx | AnalogLimit | LimitAlarmCategory | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogLimit | Contain | AlternateLimit | etx | AnalogLimit | AlternateLimit | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogRateLimit | BelongTo | LimitAlarmCategory | etx | AnalogRateLimit | LimitAlarmCategory | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | BelongTo | AnalogAlarmCategory | etx | AnalogValue | AnalogAlarmCategory | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | Contain | AnalogLimit | etx | AnalogValue | AnalogLimit | 0..n | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | Contain | SetPoint | etx | AnalogValue | Setpoint | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AlternateLimit | MemberOf | AnalogValue | etx | AlternameLimit | AnalogValue | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | AnalogMeasMsg | MemberOf | AnalogValue | etx | AnalogMeasMsg | AnalogValue | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | Has | AnalogRateLimit | etx | AnalogValue | AnalogRateLimit | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | Has | SCADAConditionAlarm | etx | AnalogValue | SCADAConditionAlarm | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | Has | SCADAHistory | etx | AnalogValue | SCADAHistory | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | HasSecondary | Site | etx | AnalogValue | Site | 0..n | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | AnalogValue | IncludedIn | ExceptionListDisplay | etx | AnalogValue | ExceptionListDisplay | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationArgument | MemberOf | Calculation | etx | CalculationArgument | Calculation | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | Calculation | TriggeredBy | CalculationTriggerTimer | etx | Calculation | CalculationTriggerTimer | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | Calculation | SourceOf | MeasurementValue | etx | Calculation | MeasurementValue | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | Calculation | Uses | Function | etx | Calculation | Function | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationArgument | AssignedTo | FunctionArgument | etx | CalculationArgument | FunctionArgument | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | MemberOf | MeasurementGroup | etx | CalculationConstant | MeasurementGroup | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CalculationConstant | Has | PermissionArea | etx | CalculationConstant | PermissionArea | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ConstantArgument | MappedTo | CalculationConstant | etx | ConstantArgument | CalculationConstant | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | FunctionArgument | MemberOf | Function | etx | FunctionArgument | Function | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | Command | LockedBy | CommandLock | etx | Command | CommandLock | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CommandLock | AssignedTo | AnalogValue | etx | CommandLock | AnalogValue | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | CommandLock | AssignedTo | DiscreteValue | etx | CommandLock | DiscreteValue | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlEvent | MappedTo | Command | etx | ControlEvent | Command | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | ControlSeq | MemberOf | ControlEvent | etx | ControlSeq | ControlEvent | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | BelongTo | DiscreteAlarmCategory | etx | DiscreteValue | DiscreteAlarmCategory | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | Contain | Command | etx | DiscreteValue | Command | 1 | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | Has | ConversionTable | etx | DiscreteValue | ConversionTable | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | DiscreteMeasMsg | MemberOf | DiscreteValue | etx | DiscreteMeasMsg | DiscreteValue | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | Has | SCADAConditionAlarm | etx | DiscreteValue | SCADAConditionalAlarm | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | Has | SCADAHistory | etx | DiscreteValue | SCADAHistory | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | HasSecondary | Site | etx | DiscreteValue | Site | 0..n | ---- | ---- | 0..n | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | DiscreteValue | IncludedIn | ExceptionListDisplay | etx | DiscreteValue | ExceptionListDisplay | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementAlias | MemberOf | MeasurementValue | etx | MeasurementAlias | MeasurementValue | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementArgument | MappedTo | MeasurementValue | etx | MeasurementArgument | MeasurementValue | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | MeasurementValue | MemberOf | MeasurementGroup | etx | MeasurementValue | MeasurementGroup | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementGroup | ContainedBy | MeasurementLocation | etx | MeasurementGroup | MeasurementLocation | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | Has | PermissionArea | etx | MeasurementLocation | PermissionArea | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | Has | VoltageLevel | etx | MeasurementLocation | VoltageLevel | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | MeasurementValue | BelongTo | Site | etx | MeasurementValue | Site | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | MeasurementValue | Has | PermissionArea | etx | MeasurementValue | PermissionArea | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMMeas | MeasurementValue | Has | SitePermission | etx | MeasurementValue | SitePermission | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SetPointLock | LockedBy | SetPoint | etx | SetPointLock | SetPoint | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SetPointLock | AssignedTo | AnalogValue | etx | SetPointLock | AnalogValue | 0..1 | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | SetPointLock | AssignedTo | DiscreteValue | etx | SetPointLock | DiscreteValue | 0..1 | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ForbiddenZone | MemberOf | GeneratingUnit | etx | ForbiddenZone | GeneratingUnit | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | FossilFuel | HasA | FossilFuelType | etx | FossilFuel | FossilFuelType | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | HasA | GenerationType | etx | GeneratingUnit | GenerationType | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | PartOf | ControlZone | etx | GeneratingUnit | ControlZone | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | PartOf | StartGroup | etx | GeneratingUnit | StartGroup | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
CIMProduction | GeneratingUnit | MemberOf | ResourceController | etx | GeneratingUnit | ResourceController | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | GenerationUnitShare | MemberOf | GeneratingUnit | etx | GeneratingUnitShare | GeneratingUnit | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | InadvertentInterchgDay | MemberOf | InadvertentInterchgProfile | etx | InadvertentInterchangeDay | InadvertentInterchangeProfile | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadActingAsResource | PartOf | ControlZone | etx | PowerSystemResource | Measurementusage | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadActingAsResource | PartOf | HostControlArea | etx | PowerSystemResource | Measurementusage | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | LoadReliefLevel | MemberOf | SubControlArea | etx | LoadReliefLevel | SubControlArea | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsageType | PartOf | MeasurementMappingName | etx | MeasurementUsageType | MeasurementMappingName | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETXSCADA | MeasurementLocation | Contains | MeasurementMappingName | etx | MeasurementLocation | MeasurementMappingName | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage | MemberOf | MeasurementUser | etx | MeasurementUsage | MeasurementUser | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage | DefinedBy | MeasurementUsageType | etx | MeasurementUsage | MeasurementUsageType | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage | Describes | MeasurementValue | etx | MeasurementUsage | MeasurementValue | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage | Describes | Control | etx | MeasurementUsage | Control | 0..n | ---- | ---- | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | MeasurementUsage | Describes | PowerSystemResource | etx | MeasurementUsage | PowerSystemResource | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | ResourceController | MemberOf | SubControlArea | etx | ResourceController | SubControlArea | 0..n | ---- | <> | 0..1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | TieEnd | MemberOf | PhysicalTiePoint | etx | TieEnd | PhysicalTiePoint | 0..n | ---- | <> | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_Areva | PhysicalTiePoint | AssociatedWith | Terminal | etx | PhysicalTiePoint | Terminal | 0..n | ---- | ---- | 1 | FALSE | FALSE | TRUE | FALSE |  | FALSE
ETX_ABB | SyncMachineSchedule | MemberOf | SynchronousMachine | etx | SyncMachineSchedules | SynchronousMachines | 0..n | ---- | <> | 1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | SwitchSchedule | MemberOf | Switch | etx | SwitchSchedules | Switch | 0..n | ---- | <> | 1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | SwitchSchedule | HasA | Season | etx | SwitchSchedule | Season | 0..n | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | SwitchSchedule | HasA | DayType | etx | SwitchSchedule | DayType | 0..n | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | SyncMachineSchedule | HasA | Season | etx | SyncMachineSchedule | Season | 0..n | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | SyncMachineSchedule | HasA | DayType | etx | SyncMachineSchedule | DayType | 0..n | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | TapSchedule | MemberOf | TapChanger | etx | TapSchedules | TapChanger | 0..n | ---- | <> | 1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | TapSchedule | HasA | Season | etx | TapSchedule | Season | 0..n | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETX_ABB | TapSchedule | HasA | DayType | etx | TapSchedule | DayType | 0..n | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMMeas | LimitSet | HasA | Season | etx | LimitSets | Season | 0..n | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | References | Terminal | etx | BranchGroup | Terminals | 0..n | ---- | ---- | 0..n | FALSE | TRUE | FALSE | FALSE |  | FALSE
ETXMonitoring | BranchGroup | ReferencesInverse | Terminal | etx | BranchGroup | InvTerminal | 0..n | ---- | ---- | 0..n | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMWires | Conductor | AssignsLosses | SubControlArea | etx | Conductor | SubControlArea | 0..1 | ---- | ---- | 0..1 | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | AssociatesDAM | LimitLogicType | etx | Equipment | DAM_LLT | 0..1 | ---- | ---- | 0..n | FALSE | TRUE | FALSE | FALSE |  | FALSE
CIMCore | Equipment | AssociatesRUC | LimitLogicType | etx | Equipment | RUC_LLT | 0..1 | ---- | ---- | 0..n | FALSE | TRUE | FALSE | FALSE |  | FALSE

## DataTypes
Package | Data Type Name | Inheritance Path | Name Space | Documentation
CIMEnumerations | BoilerControlMode |  | cim | Boiler Control Mode | EnumBoilerControlMode
CIMEnumerations | BreakerConfiguration |  | cim | Switching arangement for Bay. | EnumBreakerConfiguration
CIMEnumerations | CompanyType |  | cim | Type of the company. | EnumCompanyType
CIMEnumerations | ControlHouseEquipmentType | Domain | cim | Type of control house equipment. | EnumControlHouseEquipmentType
CIMEnumerations | CurveStyle |  | cim |  | EnumCurveStyle
CIMEnumerations | Y2AxisUnits |  | cim |  | EnumY2AxisUnits
CIMEnumerations | Y1AxisUnits |  | cim |  | EnumY1AxisUnits
CIMEnumerations | YAxisType |  | cim |  | EnumYAxisType
CIMEnumerations | XAxisUnits |  | cim |  | EnumXAxisUnits
CIMEnumerations | XAxisType |  | cim |  | EnumXAxisType
CIMEnumerations | WindingType |  | cim |  | EnumWindingType
CIMEnumerations | TransformerType |  | cim |  | EnumTransformerType
CIMEnumerations | TransformerControlMode |  | cim |  | EnumTransformerControlMode
CIMEnumerations | SynchronousMachineType |  | cim |  | EnumSynchronousMachineType
CIMEnumerations | SynchronousMachineOperatingMode |  | cim |  | EnumSynchronousMachineOperatingMode
CIMEnumerations | GeneratorControlSource |  | cim |  | EnumGeneratorControlSource
CIMEnumerations | BusbarConfiguration |  | cim |  | EnumBusbarConfiguration
CIMEnumerations | ClearanceTagType | Domain | cim |  | EnumClearanceTagType
CIMEnumerations | CoolantType |  | cim |  | EnumCoolantType
CIMEnumerations | AreaControlMode |  | cim |  | EnumAreaControlModel
CIMEnumerations | DayTypeName |  | cim |  | EnumDayTypeName
CIMEnumerations | EmissionType |  | cim |  | EnumEmissionType
CIMEnumerations | EmissionValueSource |  | cim |  | EnumEmissionValueSource
CIMEnumerations | FuelType |  | cim |  | EnumFuelType
CIMEnumerations | GeneratorControlMode |  | cim |  | EnumGeneratorControlMode
CIMEnumerations | GeneratorOperatingMode |  | cim |  | EnumGeneratorOperatingMode
CIMEnumerations | HydroPlantType |  | cim |  | EnumHydroPlantType
CIMEnumerations | Quantity |  | cim |  | EnumQuantity
CIMEnumerations | RampMethod |  | cim |  | EnumRampMethod
CIMEnumerations | RampStartMethod |  | cim |  | EnumRampStartMethod
CIMEnumerations | RampUnits |  | cim |  | EnumRampUnits
CIMEnumerations | RemoteUnitType |  | cim |  | EnumRemoteUnitType
CIMEnumerations | SeasonName |  | cim |  | EnumSeasonName
CIMEnumerations | Source |  | cim |  | EnumSource
CIMEnumerations | SwitchState |  | cim |  | EnumSwitchState
CIMEnumerations | TemperatureUnits |  | cim |  | EnumTemperatureUnits
CIMEnumerations | TurbineType |  | cim |  | EnumTurbineType
CIMEnumerations | Validity |  | cim |  | EnumValidity
CIMEnumerations | WindingConnection |  | cim |  | EnumWindingConnection
CIMEnumerations | PenstockType | Domain | cim | Type of hydro plant penstock. | EnumPenstockType
CIMEnumerations | SurgeTankCode | Domain | cim | Type (or absence) of surge tank that is associated with the hydro power plant. | EnumSurgeTankCode
CIMEnumerations | SpillwayGateType | Domain | cim | Type of spillway gate. | EnumSpillwayGateType
CIMEnumerations | TransformerCoolingType | Domain | cim |  | EnumTransformerCoolingType
CIMDataTypes | Integer | Domain | cim | A type with the value range -2**-31..2**31 -1
CIMDataTypes | AbsoluteDateTime | Domain | cim | Date and time as 'yyyy-mm-ddThh:mm:ss.sss', which conforms with ISO 8601. UTC time zone is specified as 'yyyy-mm-ddThh:mm:ss.sssZ'. A local timezone relative UTC is specified as 'yyyy-mm-ddThh:mm:ss.sss-hh:mm'.
CIMDataTypes | ActivePower | Domain | cim | Product of RMS value of the voltage and the RMS value of the in-phase component of the current (Megawatt)
CIMDataTypes | Admittance | Domain | cim | Ratio of current to voltage.
CIMDataTypes | AngleDegrees | Domain | cim | Measurement of angle in degrees
CIMDataTypes | AngleRadians | Domain | cim | Phase angle in radians
CIMDataTypes | ApparentPower | Domain | cim | Product of the RMS value of the voltage and the RMS value of the current (MegaVoltAmperes)
CIMDataTypes | Boolean | Domain | cim | A type with the value space 0..1 where 0 means false and 1 means true.
CIMDataTypes | Complex | Domain | cim | A real and imaginary pair of Float values.
CIMDataTypes | CompositeSwitchType | Domain | cim | An alphanumeric code that can be used as a reference to extar information such as the description of the interlocking scheme if any.
CIMDataTypes | Float | Domain | cim | A type defined by IEEE 754-1985 as double (OBSERVE, not as the IEEE 754-1985 float). The value range is m*2**e where the range of m is -2**52..2**52 -1 and the range of e is -1075..970.
CIMDataTypes | LongDouble | Domain | cim | A type defined by IEEE 754-1985 as a long double.
CIMDataTypes | LongLong | Domain | cim | A type with the value range -2**63..2**63 -1
CIMDataTypes | Octet | Domain | cim | A type with the value range 0..255
CIMDataTypes | Short | Domain | cim | A type with the value range -2**15..2**15 -1
CIMDataTypes | String | Domain | cim | A type consisting of a sequence of 8 bit characters. The character encoding is UTF-8.
CIMDataTypes | ULong | Domain | cim | A type with the value range 0..2**32 -1
CIMDataTypes | ULongLong | Domain | cim | A type with the value range 0..2**64 -1
CIMDataTypes | VoltagePerReactivePower | Domain | cim | Voltage variation with reactive power
ETXEnumerations | GenerationParticipationFactor |  | etx |  | EnumGeneratorParticipationFactor
ETXEnumerations | Gatetype |  | etx |  | EnumGateType
ETXEnumerations | Limittype |  | etx |  | EnumLimitType
ETXEnumerations | Ratingtype |  | etx |  | EnumRatingType
ETXEnumerations | LimitSetType |  | etx |  | EnumLimitSetType
ETXEnumerations | PreContLimitType |  | etx |  | EnumPreContLimitType
ETXEnumerations | PostContLimitType |  | etx |  | EnumPostContLimitType

## DataTypes - Enum
Package | Data Type - Enumeration | Enumerator | Label | Initial Value | Namespace | Documentation
CIMEnumerations | EnumBoilerControlMode | coordinated | LongInt | 0 | cim |  | coordinated
CIMEnumerations | EnumBoilerControlMode | following | LongInt | 1 | cim |  | following
CIMEnumerations | EnumBreakerConfiguration | singleBreaker | LongInt | 0 | cim |  | singleBreaker
CIMEnumerations | EnumBreakerConfiguration | breakerAndAHalf | LongInt | 1 | cim |  | breakerAndAHalf
CIMEnumerations | EnumBreakerConfiguration | doubleBreaker | LongInt | 2 | cim |  | doubleBreaker
CIMEnumerations | EnumBreakerConfiguration | noBreaker | LongInt | 3 | cim |  | noBreaker
CIMEnumerations | EnumCompanyType | pool | LongInt | 0 | cim |  | pool
CIMEnumerations | EnumCompanyType | municipal | LongInt | 1 | cim |  | municipal
CIMEnumerations | EnumCompanyType | isPrivate | LongInt | 2 | cim |  | private
CIMEnumerations | EnumCurveStyle | constantYValue | LongInt | 0 | cim |  | constantYValue
CIMEnumerations | EnumCurveStyle | straightLineYValues | LongInt | 1 | cim |  | straightLineYValues
CIMEnumerations | EnumCurveStyle | rampYValue | LongInt | 2 | cim |  | rampYValue
CIMEnumerations | EnumCurveStyle | formula | LongInt | 3 | cim |  | formula
CIMEnumerations | EnumY2AxisUnits | MW | LongInt | 1 | cim
CIMEnumerations | EnumY2AxisUnits | MVAr | LongInt | 2 | cim
CIMEnumerations | EnumY2AxisUnits | integer | LongInt | 3 | cim
CIMEnumerations | EnumY1AxisUnits | MW | LongInt | 1 | cim
CIMEnumerations | EnumY1AxisUnits | MVAr | LongInt | 2 | cim
CIMEnumerations | EnumY1AxisUnits | integer | LongInt | 3 | cim
CIMEnumerations | EnumY1AxisUnits | unitOfCurrencyPerHour | LongInt | 4 | cim
CIMEnumerations | EnumYAxisType | singleYValue | LongInt | 1 | cim |  | singleYValue
CIMEnumerations | EnumYAxisType | twoYValues | LongInt | 2 | cim |  | twoYValues
CIMEnumerations | EnumXAxisUnits | absoluteTime | LongInt | 1 | cim
CIMEnumerations | EnumXAxisUnits | normalizedTime | LongInt | 2 | cim
CIMEnumerations | EnumXAxisUnits | MW | LongInt | 3 | cim
CIMEnumerations | EnumXAxisType | absoluteTime | LongInt | 0 | cim
CIMEnumerations | EnumXAxisType | normalizedDailyTime | LongInt | 1 | cim | {0..25} hours
CIMEnumerations | EnumXAxisType | anyRealValue | LongInt | 2 | cim
CIMEnumerations | EnumWindingType | primary | LongInt | 1 | cim |  | primary
CIMEnumerations | EnumWindingType | secondary | LongInt | 2 | cim |  | secondary
CIMEnumerations | EnumWindingType | tertiary | LongInt | 3 | cim |  | tertiary
CIMEnumerations | EnumWindingType | quaternary | LongInt | 4 | cim |  | quaternary
CIMEnumerations | EnumTransformerType | fix | LongInt | 0 | cim |  | fix
CIMEnumerations | EnumTransformerType | voltageControl | LongInt | 1 | cim |  | voltageControl
CIMEnumerations | EnumTransformerType | phaseControl | LongInt | 2 | cim |  | phaseControl
CIMEnumerations | EnumTransformerType | voltageAndPhaseControl | LongInt | 3 | cim |  | voltageAndPhaseControl
CIMEnumerations | EnumTransformerControlMode | off | LongInt | 1 | cim | off | off
CIMEnumerations | EnumTransformerControlMode | local | LongInt | 2 | cim | local | local
CIMEnumerations | EnumTransformerControlMode | volt | LongInt | 3 | cim |  | volt
CIMEnumerations | EnumTransformerControlMode | mVAr | LongInt | 4 | cim | mVAr | mVAr
CIMEnumerations | EnumTransformerControlMode | MW | LongInt | 5 | cim | MW | MW
CIMEnumerations | EnumSynchronousMachineType | generator | LongInt | 0 | cim |  | Generator
CIMEnumerations | EnumSynchronousMachineType | condenser | LongInt | 1 | cim |  | Condenser
CIMEnumerations | EnumSynchronousMachineType | generator_or_condenser | LongInt | 2 | cim |  | Both
CIMEnumerations | EnumSynchronousMachineOperatingMode | generator | LongInt | 0 | cim |  | Generator
CIMEnumerations | EnumSynchronousMachineOperatingMode | condenser | LongInt | 1 | cim |  | Condenser
CIMEnumerations | EnumGeneratorControlSource | Unavailable | LongInt | 0 | cim
CIMEnumerations | EnumGeneratorControlSource | offAGC | LongInt | 1 | cim |  | OffAGC
CIMEnumerations | EnumGeneratorControlSource | onAGC | LongInt | 2 | cim |  | OnAGC
CIMEnumerations | EnumGeneratorControlSource | PlantControl | LongInt | 3 | cim |  | PlantControl
CIMEnumerations | EnumBusbarConfiguration | singleBus | LongInt | 0 | cim |  | singleBus
CIMEnumerations | EnumBusbarConfiguration | doubleBus | LongInt | 1 | cim |  | doubleBus
CIMEnumerations | EnumBusbarConfiguration | mainWithTransfer | LongInt | 2 | cim |  | mainWithTransfer
CIMEnumerations | EnumBusbarConfiguration | ringBus | LongInt | 3 | cim |  | ringBus
CIMEnumerations | EnumCoolantType | air | LongInt | 0 | cim |  | air
CIMEnumerations | EnumCoolantType | hydrogenGas | LongInt | 1 | cim |  | hydrogenGas
CIMEnumerations | EnumCoolantType | water | LongInt | 2 | cim |  | water
CIMEnumerations | EnumAreaControlModel | CF | LongInt | 0 | cim |  | CF
CIMEnumerations | EnumAreaControlModel | CTL | LongInt | 1 | cim |  | CTL
CIMEnumerations | EnumAreaControlModel | TLB | LongInt | 2 | cim |  | TLB
CIMEnumerations | EnumAreaControlModel | OFF | LongInt | 3 | cim |  | OFF
CIMEnumerations | EnumDayTypeName | weekday | LongInt | 0 | cim |  | weekday
CIMEnumerations | EnumDayTypeName | weekend | LongInt | 1 | cim |  | weekend
CIMEnumerations | EnumDayTypeName | holiday | LongInt | 2 | cim |  | holiday
CIMEnumerations | EnumDayTypeName | Sunday | LongInt | 10 | etx |  | Sunday
CIMEnumerations | EnumDayTypeName | Monday | LongInt | 11 | etx |  | Monday
CIMEnumerations | EnumDayTypeName | Tuesday | LongInt | 12 | etx |  | Tuesday
CIMEnumerations | EnumDayTypeName | Wednesday | LongInt | 13 | etx |  | Wednesday
CIMEnumerations | EnumDayTypeName | Thursday | LongInt | 14 | etx |  | Thursday
CIMEnumerations | EnumDayTypeName | Friday | LongInt | 15 | etx |  | Friday
CIMEnumerations | EnumDayTypeName | Saturday | LongInt | 16 | etx |  | Saturday
CIMEnumerations | EnumDayTypeName | Holiday1 | LongInt | 20 | etx |  | Holiday1
CIMEnumerations | EnumDayTypeName | Holiday2 | LongInt | 21 | etx |  | Holiday2
CIMEnumerations | EnumEmissionType | sulferDioxide | LongInt | 0 | cim |  | sulferDioxide
CIMEnumerations | EnumEmissionType | carbonDioxide | LongInt | 1 | cim |  | carbonDioxide
CIMEnumerations | EnumEmissionType | nitrogenOxide | LongInt | 2 | cim |  | nitrogenOxide
CIMEnumerations | EnumEmissionType | hydrogenSulfide | LongInt | 3 | cim |  | hydrogenSulfide
CIMEnumerations | EnumEmissionType | chlorine | LongInt | 4 | cim |  | chlorine
CIMEnumerations | EnumEmissionType | carbonDisulfide | LongInt | 5 | cim |  | carbonDisulfide
CIMEnumerations | EnumEmissionValueSource | measured | LongInt | 0 | cim |  | measured
CIMEnumerations | EnumEmissionValueSource | calculated | LongInt | 1 | cim |  | calculated
CIMEnumerations | EnumFuelType | coal | LongInt | 0 | cim |  | coal
CIMEnumerations | EnumFuelType | oil | LongInt | 1 | cim |  | oil
CIMEnumerations | EnumFuelType | gas | LongInt | 2 | cim |  | gas
CIMEnumerations | EnumGeneratorControlMode | setpoint | LongInt | 0 | cim |  | setpoint
CIMEnumerations | EnumGeneratorControlMode | pulse | LongInt | 1 | cim |  | pulse
CIMEnumerations | EnumGeneratorOperatingMode | Off | LongInt | 0 | cim |  | Off
CIMEnumerations | EnumGeneratorOperatingMode | Manual | LongInt | 1 | cim |  | Manual
CIMEnumerations | EnumGeneratorOperatingMode | Fixed | LongInt | 2 | cim |  | Fixed
CIMEnumerations | EnumGeneratorOperatingMode | LFC | LongInt | 3 | cim |  | LFC
CIMEnumerations | EnumGeneratorOperatingMode | AGC | LongInt | 4 | cim |  | AGC
CIMEnumerations | EnumGeneratorOperatingMode | EDC | LongInt | 5 | cim |  | EDC
CIMEnumerations | EnumGeneratorOperatingMode | MRN | LongInt | 6 | cim |  | MRN
CIMEnumerations | EnumGeneratorOperatingMode | REG | LongInt | 7 | cim |  | REG
CIMEnumerations | EnumHydroPlantType | runOfRiver | LongInt | 0 | cim |  | runOfRiver
CIMEnumerations | EnumHydroPlantType | pumpedStorage | LongInt | 1 | cim |  | pumpedStorage
CIMEnumerations | EnumHydroPlantType | majorStorage | LongInt | 2 | cim |  | majorStorage
CIMEnumerations | EnumHydroPlantType | minorStorage | LongInt | 3 | cim |  | minorStorage
CIMEnumerations | EnumQuantity | none | LongInt | 0 | cim |  | none
CIMEnumerations | EnumQuantity | time | LongInt | 1 | cim |  | time
CIMEnumerations | EnumQuantity | activePower | LongInt | 2 | cim |  | activePower
CIMEnumerations | EnumQuantity | reactivePower | LongInt | 3 | cim |  | reactivePower
CIMEnumerations | EnumQuantity | currency | LongInt | 4 | cim |  | currency
CIMEnumerations | EnumQuantity | voltage | LongInt | 5 | cim |  | voltage
CIMEnumerations | EnumRampMethod | yUnitsPerMinute | LongInt | 0 | cim |  | yUnitsPerMinute
CIMEnumerations | EnumRampMethod | rampCompletionInMinutes | LongInt | 1 | cim |  | rampCompletionInMinutes
CIMEnumerations | EnumRampStartMethod | zero | LongInt | 0 | cim |  | zero
CIMEnumerations | EnumRampStartMethod | fiftyPerCent | LongInt | 1 | cim |  | fiftyPerCent
CIMEnumerations | EnumRampStartMethod | oneHundredPerCent | LongInt | 2 | cim |  | oneHundredPerCent
CIMEnumerations | EnumRampUnits | MWPerMinute | LongInt | 0 | cim |  | MWPerMinute
CIMEnumerations | EnumRampUnits | rampCompletionInMin | LongInt | 1 | cim |  | rampCompletionInMin
CIMEnumerations | EnumRemoteUnitType | RTU | LongInt | 0 | cim |  | RTU
CIMEnumerations | EnumRemoteUnitType | SubstationControlSystem | LongInt | 1 | cim |  | SubstationControlSystem
CIMEnumerations | EnumRemoteUnitType | ControlCenter | LongInt | 2 | cim |  | ControlCenter
CIMEnumerations | EnumRemoteUnitType | IED | LongInt | 3 | cim |  | IED
CIMEnumerations | EnumSeasonName | winter | LongInt | 0 | cim |  | winter
CIMEnumerations | EnumSeasonName | spring | LongInt | 1 | cim |  | spring
CIMEnumerations | EnumSeasonName | summer | LongInt | 2 | cim |  | summer
CIMEnumerations | EnumSeasonName | fall | LongInt | 3 | cim |  | fall
CIMEnumerations | EnumSource | PROCESS | LongInt | 0 | cim |  | PROCESS
CIMEnumerations | EnumSource | DEFAULTED | LongInt | 1 | cim |  | DEFAULTED
CIMEnumerations | EnumSource | SUBSTITUTED | LongInt | 2 | cim |  | SUBSTITUTED
CIMEnumerations | EnumSwitchState | open | LongInt | 0 | cim |  | open
CIMEnumerations | EnumSwitchState | close | LongInt | 1 | cim |  | close
CIMEnumerations | EnumTemperatureUnits | celsius | LongInt | 0 | cim |  | celsius
CIMEnumerations | EnumTemperatureUnits | fahrenheit | LongInt | 1 | cim |  | fahrenheit
CIMEnumerations | EnumTurbineType | francis | LongInt | 0 | cim |  | francis
CIMEnumerations | EnumTurbineType | pelton | LongInt | 1 | cim |  | pelton
CIMEnumerations | EnumTurbineType | kaplan | LongInt | 2 | cim |  | kaplan
CIMEnumerations | EnumValidity | GOOD | LongInt | 0 | cim |  | GOOD
CIMEnumerations | EnumValidity | QUESTIONABLE | LongInt | 1 | cim |  | QUESTIONABLE
CIMEnumerations | EnumValidity | INVALID | LongInt | 2 | cim |  | INVALID
CIMEnumerations | EnumWindingConnection | D | LongInt | 0 | cim |  | D
CIMEnumerations | EnumWindingConnection | Y | LongInt | 1 | cim |  | Y
CIMEnumerations | EnumWindingConnection | Z | LongInt | 2 | cim |  | Z
ETXEnumerations | EnumGeneratorParticipationFactor | short | LongInt | 0 | etx |  | short
ETXEnumerations | EnumGeneratorParticipationFactor | long | LongInt | 1 | etx |  | long
ETXEnumerations | EnumGateType | and | LongInt | 0 | etx |  | and
ETXEnumerations | EnumGateType | or | LongInt | 1 | etx |  | or
ETXEnumerations | EnumGateType | nor | LongInt | 2 | etx |  | nor
ETXEnumerations | EnumGateType | nand | LongInt | 3 | etx |  | nand
ETXEnumerations | EnumGateType | not | LongInt | 4 | etx |  | not
ETXEnumerations | EnumGateType | ne | LongInt | 5 | etx |  | ne
ETXEnumerations | EnumGateType | eq | LongInt | 6 | etx |  | eq
ETXEnumerations | EnumGateType | le | LongInt | 7 | etx |  | le
ETXEnumerations | EnumGateType | lt | LongInt | 8 | etx |  | lt
ETXEnumerations | EnumGateType | ge | LongInt | 9 | etx |  | ge
ETXEnumerations | EnumGateType | gt | LongInt | 10 | etx |  | gt
ETXEnumerations | EnumLimitType | normalRating | LongInt | 0 | etx |  | normalRating
ETXEnumerations | EnumLimitType | fifteenminuteRating | LongInt | 1 | etx |  | fifteenminuteRating
ETXEnumerations | EnumLimitType | twoHourRating | LongInt | 2 | etx |  | twoHourRating
ETXEnumerations | EnumLimitType | conductorRating | LongInt | 3 | etx |  | conductorRating
ETXEnumerations | EnumLimitType | RateOfChange | LongInt | 4 | etx
ETXEnumerations | EnumLimitType | Clamp | LongInt | 5 | etx
ETXEnumerations | EnumLimitType | High1 | LongInt | 11 | etx
ETXEnumerations | EnumLimitType | High2 | LongInt | 12 | etx
ETXEnumerations | EnumLimitType | High3 | LongInt | 13 | etx
ETXEnumerations | EnumLimitType | High4 | LongInt | 14 | etx
ETXEnumerations | EnumLimitType | High5 | LongInt | 15 | etx
ETXEnumerations | EnumLimitType | High6 | LongInt | 16 | etx
ETXEnumerations | EnumLimitType | Low1 | LongInt | 21 | etx
ETXEnumerations | EnumLimitType | Low2 | LongInt | 22 | etx
ETXEnumerations | EnumLimitType | Low3 | LongInt | 23 | etx
ETXEnumerations | EnumLimitType | Low4 | LongInt | 24 | etx
ETXEnumerations | EnumLimitType | Low5 | LongInt | 25 | etx
ETXEnumerations | EnumLimitType | Low6 | LongInt | 26 | etx
ETXEnumerations | EnumRatingType | dynamicRating | LongInt | 0 | etx |  | dynamicRating
ETXEnumerations | EnumRatingType | staticRating | LongInt | 1 | etx |  | staticRating
ETXEnumerations | EnumLimitSetType | ratings | LongInt | 0 | etx | device ratings
ETXEnumerations | EnumLimitSetType | limits | LongInt | 1 | etx | telemetry limits
ETXEnumerations | EnumLimitSetType | both | LongInt | 2 | etx | apply to both device and telemetry measurements
ETXEnumerations | EnumPreContLimitType | none | LongInt | 0 | etx
ETXEnumerations | EnumPreContLimitType | normal | LongInt | 1 | etx
ETXEnumerations | EnumPostContLimitType | none | LongInt | 0 | etx
ETXEnumerations | EnumPostContLimitType | normal | LongInt | 1 | etx
ETXEnumerations | EnumPostContLimitType | LTE | LongInt | 2 | etx
ETXEnumerations | EnumPostContLimitType | MTE | LongInt | 3 | etx
ETXEnumerations | EnumPostContLimitType | STE | LongInt | 4 | etx
Domain

## DataTypes - Value&Unit
Package | Data Type Name | DataType | Unit | Initial Value | Namespace | Documentation