## Slide 1: Compliance Update
March 2007

## Slide 2: Control Performance Highlights
NERC CPS1 Performance
  Performance declined in February
    February performance comparison
      February 2007: 126.91
      February 2006: 141.06
    12 month rolling average comparison
      March 2006 February 2007: 141.47
      March 2005 February 2006: 127.97
PRR 525 Performance
  Initial scores for February indicate 32 QSEs passed / 1 non-wind-only QSE failed the measure
  Scores posted on the ERCOT Compliance Website
    SCE Performance Scores

## Slide 3: ERCOT’s CPS1 Monthly Trend

## Slide 4: ERCOT CPS1 Performance Comparison

## Slide 5: ERCOT CPS1 by Interval

## Slide 6: QSE PRR525 10-Minute Interval Scoring

## Slide 7: 525 Passing 10-Min Interval Percentage Trends

## Slide 8: October 3, 2006 Event Observations
LaaR Performance
  ERCOT deployed all RRS being provided by LaaRs in accordance with ERCOT DCS Event Operating Procedures.
  Six of ten QSEs with LaaR RRS awards did not respond with 95% of their award within 10 minutes.
    642 MW tripped – 1,150 MW obligation
    Took over 20 minutes to achieve 95% of obligation
  Seven Protocol Violation Notices issued.
    Six notices related to Section 6.5.4(2) – tripping requirements for LaaR
      1st occurrence – 1 MP
      2nd occurrence – 5 MPs
    One notice related to Section 6.5.1.1(4) – telemetry requirements
      1 MP

## Slide 9: December 22, 2006 Event Observations
LaaR performance
  Three Protocol Violation Notices issued.
    One notice related to Section 6.5.4(2) – tripping requirements for LaaR
    Two notices related to Section 6.5.1.1(4) – telemetry requirements
    Required corrective actions in progress
  ERCOT Operations to ask for retest of certain LaaR under-frequency relays that did not trip automatically. No violations determined due to lack of high-speed frequency recordings at these locations and very short time that frequency dipped below 59.7 Hz. High speed frequency recorders in Austin may not be sufficient to validate frequency-triggered LaaR performance across the grid.