ERCOT OPERATIONS REPORT

ON THE

EECP EVENT

OF

March 08, 2007

Executive Summary	3

Time Line and Description of Significant Events	4

Observations/Data Review...........................................................................................5

Lessons Learned.........................................................................................................10

### Executive Summary

ERCOT implemented Step One of its Emergency Electric Curtailment Plan (EECP) on March 08, 2007.  Factors that led to ERCOT implementing the EECP Step One:

At 06:53:00 an Advisory was issued for Adjusted Responsive Reserve (ARR) below 3000 MW.

At 14:08, the Total ERCOT Telemetered SCE drops below 0 and does not return back to 0 for approximately six and a half hours.  This drop in the Total ERCOT SCE was due to the negative Wind SCE. The Total ERCOT SCE reached its lowest value of -1050 MW at approximately 16:24:00.

At 15:05, ERCOT declared an Alert for ARR below 2500 MW.

The Evening load pickup climbed by 2,192 MW in one hour, starting at 18:00 and leveling off at 19:11:00 at approximately 33,354 MW.

At 18:52 as ARR and wind generation declined, ERCOT declared EECP step 1.  The Total ERCOT Telemetered SCE was -403 MW at this time.

At 19:05, the ARR increased to 2,500 MW.

EECP was terminated at 19:52:00.

At 20:00, the ARR increased to 3,000 MW.

Time Line and Description of Significant Events

- 06:53:00 March 08, 2007 Advisory issued for ARR below 3000 MW.

- 14:45:00 Several Wind only QSEs are contacted about their negative SCE, QSEs state they will adjust their SCE.

- 15:05:00 Alert issued for ARR below 2500 MW.

- 16:00:00 QSE contacted about their negative SCE, they were short by 250 MW.

- 17:08:00 Another QSE is contacted about their negative SCE, the QSE states they will bring on a CT’s to cover their schedule.

- 18:52:00 EECP Step 1 initiated.  Hotline call to QSEs instructing to call back with all units that are available and start times.

- 18:55:00 All RMR are at full output, 2 GTs were brought online, SPP was notified of EECP and requested Emergency Power across the DC tie.

- 18:58:00 Several QSEs call to inform ERCOT of additional available resources and start times if needed.

- 19:05:00 ARR rises above 2300 MW.

- 19:52:00 EECP terminated.  ARR was at 2,858 MW.

- 20:00:00 ARR rises above 3,000 MW.

Observations/Data Review

16:00 – 20:00 RRS vs. Total ERCOT Load

16:00 – 20:00 RRS vs. SCE

16:00 – 20:00 Regulation vs. Frequency

16:00 – 20:00 Total ERCOT SCE - Total Wind SCE

16:00 – 20:00 Total Wind SCE

Lessons Learned

Drop in total wind generation had a significant impact on ARR.

The quick load increase depleted ARR and precipitated EECP Step 1.

Replacement Reserve Services (RPRS) uses the planned output of wind.

There was no noticeable increase in available ARR as a result of the early Advisories and Alerts.

Replacement Reserve Service (RPRS) uses the planned output of wind units, may need to investigate using the Generation Adequacy Task Force (GATF) recommended percentages.