ERCOT Nodal Operating Guides

Section 8:  Telemetry and Communication

Draft (Month, Day, Year)

(Effective Upon Texas Nodal Market Implementation)

GP&L Comments:

- Please be proactive in working with the Integration and Design Authority (IDA) in keeping their document Texas Nodal Enterprise Integration External Interfaces Specification (XML spec) and the “yet to be released” ICCP Specification / document in sync with this document in the areas of the XML & ICCP data information.

- In the table of contents, the section numbering seems to be off – example – table states ERCOT ICCP Interface is 8.1.2 – inside the document, it is labeled as 8.1.1

- Please Note: Inside the section for the ICCP Interface (8.1.1 as stated in document), the document lists the set of Quality codes that corresponds to the TAC approved list. However, the EMS team through their SCADA Business Requirements Document requested an entirely different set. This needs to be tracked & reconciled between documents

- Weather Zone Data (Section 8.1.5.1 as stated in document) talks about requirements that would result in certain TSP’s providing an additional ICCP association for the transfer of WeatherZone tie line measurements. Question: I do not find this in the EMS Scada business requirements (though this level of detail may not be included until the conceptual or even detailed documents are issued). Are you sure the EMS Scada team is designing for this additional association? Does the ICCP specification (which has not been issued to Market Participants as of this time) include this – Bottom line: everyone needs to be in sync to avoid confusion, design issues, etc.

- Contents

8	Telemetry and Communication	8-38-2

8.1	Telemetry	8-38-2

8.1.1	ERCOT Interface RTUs	8-48-2

8.1.2	ERCOT ICCP Interface	8-48-28-5

8.1.3	Validation of Real Time Signals with Settlement Metering for Resources	8-58-28-5

8.1.4	Data from ERCOT to QSE’s	8-58-2

8.1.5	Data From ERCOT to TSP	8-58-2

8.1.6	Data from QSE/TSP to ERCOT	8-68-28-6

8.1.7	TSP/QSE Telemetry Restoration	8-108-288-1

8.1.8	QSE and TSP Data Acquisition	8-108-288-1

8.2	Calibration and Testing	8-118-288-1

8.2.1	Responsibility	8-118-288-1

8.2.2	Notification	8-118-288-1

8.2.3	Test Equipment	8-118-288-1

8.2.4	Disputes	8-118-288-1

8.2.5	Calibration Testing	8-118-288-1

8.2.6	Exchange of Information	8-128-288-1

8.2.7	Documentation	8-128-288-1

8.2.8	Operator One-line Displays	8-138-288-10

8.2.9	Notification of Changes	8-138-288-11

8.3	Communications	8-138-288-12

8.3.1	ERCOT WAN	8-138-288-12

8.3.2	ERCOT Responsibilities	8-168-288-13

8.3.3	QSE and TSP Responsibilities	8-168-288-13

8.3.4	TSP and QSE Supplied Communications	8-178-288-15

8.3.5	Maintenance and Restoration	8-188-288-16

8.4	Document Control	8-198-288-17

TSP	8-4

8-11

8-11

8-13

Telemetry and Communication

## 8.1	Telemetry

(1)

QSE control centers required to supply real-time telemetry data to ERCOT shall use an Inter-Control Area Communications Protocol (ICCP) interface through the ERCOT WAN.  QSEs shall also receive signals from ERCOT over the ICCP interface to implement frequency control.  or other device using

(2)	TSPs control centers required to supply real-time telemetry data to ERCOT shall use an ICCP interface through the ERCOT WAN.

(3)	Each QSE and/or TSP shall continuously provide to ERCOT the telemetry data quantities that they are responsible for.  The frequency of update, means of communication to ERCOT, and format for each point provided by each Entity shall follow the specifications in Attachment 9?, ERCOT Data Sets for that entity, unless otherwise approved specifiOT.  At the frequency specified in the TablesAttachment 9? update cycle shall provide new readings of all data points being monitored, not averages linked to prior cycle readings or repetition of readings from a previous cycle.  Design accuracy and availability of data points delivered to ERCOT, shall satisfy the requirements and standards for tTelemetry pPerformace and Stat Estimator pPerformance as specifed under Section 8.1.6,  ata from QSEs and /TDS to ERCOT.” ofthese guides.

(4)	The TSP shall maitinto any telemetered  of the largest line rating at each busERCOT  will identify the top 10% of MW/MVAR telemetry pairs and voltage points that are “essential”to reliability, system observability, support of State Estimator performance, or commercial Market concern which must meet the more stringent availability requirements defined below.

l provide data to ERCthang availability:99% of all data points will have an availability of at least 80% on a monthly basis

will be meas based on end-to-end connectivity of the  communications path and teExceptions to the above may be made with agreement with ERCOT for data points not significant in the solution of the State Estimator or required for the reliable operation on the ERCOT Transmission System.

QSEs, Resources and TSPs are required to provide power operation data to ERCOT including, but not limited to:

(a)	Real time generation data from QSEs;

(b)	Planned Outage information from Resources;

(c)	Transmission system network data used by any TSP’s control center, including:

(i)	Breaker and line switch status of all ERCOT Transmission Elements;

(ii)	Line flow MW and MVAR;

(iii)	Breaker, switches connected to all Resources;

(iv)	Transmission Facility Voltages; and

(v)	Transformer MW, MVAR and TAP.

(d)	Real time generation and Load Resource telemetry  data from QSEs;

(e)	Real time Generation meter splitting telemetry data from QSEs;

(f)	Planned Transmission Outage information from TSPs;

(g)	Transmission system network model data including constraints) from TSPs;

(h)	Current Operating Plans from QSEs; and

(i)	Dynamic Schedules from QSEs.

(5)	Real-Time telemetry data provided to ERCOT shall be at the same scan rate that the TSP or QSE control computers and data collection system obtains the data from telemetry.

unications Protocol (ICCP) over the ERCOT WAN Ethernet provides the real-time tTelemetry data from Market Participant computers, computer networks, or other devices.  Market Participants providing the  to the ERCOT WAN.  Suppliers of data using an ICCP link must format their data and coordinate installation according to ERCOT procedures (ERCOT WAN Agreement).  The telemetry data furnished by a Market Participant’s ICCP link shall reflect the data quality codes com_failed dividual data points as coordinated with ERCOT found in the Market Participant’s control computers and data collection system.  Market Participant’s shall provide documentation to ERCOT upon ERCOT’s request describing their control native system quality codes and the mapping defining the conversion of their RTU quality codeso the ERCOT defined quality codes.

8.1.1.1     Quality Codes

Status and  analogstelemeteeddata provided  toERCOT shall have willed with the sociated quality codes:

(1)	“ alid” – represents analog or status data that the TSPmarket ticipant considers valid;.

(2)	“ anual” – represents analog or status data that is manually entered manually aket participant control system (not received from the field electronically);.

(3)	“ uspect” - rRepresentsanalog or status data that the market participant in which thSP sure alidity;

(4)	“ nvalid” – rRepresentsanalog or status data that which the mparticipant considers to be has identified asity limits; and.

(5)	“ om_fail” – represents informs ERstatus data that the market participant considers to be not current due to communications failureprovided ERCOT is not current.

8.1.1.2  Availability Rf ICCP Links

(1)	ICCP links must achieve a monthly availability of -eightercent, excproved Pplanned Ooutages.  Avaiability wll be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data.  A link will be considered as available when at least eighty-five (85%) percent efined on that lnkessfully transferred to ERCOT with a “Valid” or “Manual” quality code.  This will include establishing a process to coordinate downtime for ICCP links and database maintenance.

(2)	ICCP links shall use fully redundant data communication between the QSE and TSPlinks between itsol center systems an Ssystems such ty single element of the communcationsystem can fail and:

(a)	For server failures, complete real-time data transfer must be re-established within five minutes by automatic failover to alternate server(s); and

(b)	For all other failures, complete real-time data transfer must continue to flow between the TSP’s, QSE’s, and ERCOT’s control systemscenters withs of all data continuing at a 30 second or less scan rate.

8.1.32	Validation of Real Time Signals Telemetry Data with Settlement Metering for Resources

(1)	Real-Time telemetry data from  esources

used to supply power or Ancillary Services shall be integrated by ERCOT and checked against settlement meter values on a monthly basis.

(2)	Where multiple generators share a single net settlement meter, the ratio of integrated Real- tie data from each generator shall be used to proportion the total settlement quantity.

8.1.3	Data from ERCOT to QSE’s

ERCOT shall provide operational data and issue instructions to QSE’s in accordance with the Operating Guide and the Protocols.  Attachment 8A in this guide provides the instructional and informational data sets that ERCOT will send to the QSEs.

8.1.4	Data from ERCOT to TSP

(1)	ERCOT shall provide operational data and issue instructions to the TSP in accordance with the Operating Guide and the Protocols.

(2)

ERCOT is required to provide the following power operation data to TSPs for the purpose of providing reliability information as determined by ERCOT:COot

(a)	Rele

Status of any breakers and switches in ERCOT's Real-Time data base;

(b)	State Estimator solutions;

(c)	Transmission line flows and voltages;

(d)	Transformer information;

(e)	QSE Resource data; and

(f)	Voltage schedules at transmission busses.

(3)	ERCOT will give notice to the Entities supplying the above list of data to ERCOT upon the initial provision of such data to the TSP.

8.1.5	Data from QSEs and TSPs to ERCOT

QSEs and TSPs shall provide Real-Time monitoring of power system quantities to ERCOT as defined in the Operating Guides and Protocols.  Attachment 8A of this guide,Operating Guide specifies the format and description for the content of each type of data point that ERCOT may request from TSPs and QSEs to satisfy the requirements in the Operating Guides and the Protocols.  Not all data points in Attachment 8A are necessarily required from each Entity.  ERCOT shall inform TSPs and QSEs if additions to presently furnished data are required.  All involved entities shall jointly resolve a means and schedule for providing data to ERCOT, including changes to existing data.  ERCOT shall consider alternatives and exceptions, on a case-by-case basis, to the extent that ERCOT determines that the  operational and reliability needs of the ERCOT system are not compromised.  Ultimately, it is the responsibility of the TSPs and QSEs to provide all data requested by ERCOT as set forth in the  Protocols and Operating Guides.

8.1.5.1	Weather Zone Data

(1)	A SPP that is responsible for providing Weather Zone tie-line measurement data to ERCOT is , they areo establish a backup to the primary source. using the method one option

(2)	SPPs having an EMS with a native ICCP application capable of four4 seond periodic data set transfers with minimum 300 points per data set, and hot standby backup ICCP servers with automatic fail-over capability, shall provide an additional ICCP association across the ERCOT WAN for the transfer of Weather Zone tie line measurements.  ICCP nodes should exist at primary and backup facilities.

SPnot hanclude the EMS data quality codes.  RTUs should exist at primary and backup facilities.2	Teleme Measurements Data

Acquisition of good telemetry status and analog measurements data (Telemetry) for the transmission power system (System) together with an accurate model of the System are processed by a state estimator to provide an optimal estimate of the System state at a given point in time while filtering measurement noise (error) and detecting gross errors. The quality and availability of Telemetry provided to ERCOT are important to the performance of ERCOT’s State Estimator.

Beyond general Telemetry performance criterion there are more stringent criterion needed at locations where state estimates are “critically important” (e.g., locations where reliability, security, and Market impact are of more focused concern).

(1)	ERCOT is required to monitor transmission assets operated at 60 kV or above and direct its operation within safe facility limits to preventfrom  da  This may requireTo do this, Erequest that addital MW, MVAR, and voltage telemetry be installed, while attempting to minimize adding telemetry equipment to as few locations as practicable.

(2)	ERCOT may also request additional telemetry when it determines that network observability or the measurement redundancy are not adequate to produce acceptable Sstte Eestmator results per the established State Estimator TAC dards approved by the Technical Advisory Committee (TAC).

(3)	Prior to making a request for additional telemetry, ERCOT will provide evidence supporting a congestion or reliability problem requiring additional observability and  specify what depected improvements in system observibility are needed.  If the request is for telemetry additions at more than one location, ERCOT shallwill priore the requested additions.

(4)	Upon receipt of a ERCOT request for additional telemetry, the TSP or QSE shall acknowledgement receipt of the request and shall have 60 days to either:

(a)	Accept ERCOT’s request for additional telemetry, provide the telemetry within 18 months, and notify ERCOT of the implementation schedule;

(b)	Provide an alternative solution to ERCOT, for implementation within the next 18 months, which meets the requirements described by ERCOT;

(c)	Propose a normal topology change (change normal status of switch(es)) in the area which would eliminate the security violations which are ERCOT’s concern. (i.e. eliminates the possibility of flow through a Transmission Element thus changing the security problem into a planning problem which is un-affected by generation dispatch);

(d)	Indicate that the requested telemetry point is at a location where the TPT or QSE does not have the authority to install the requested telemetry.  For points on privately owned facilities connected to the ERCOT Transmission Grid, an attempt will be made to facilitate ERCOT's telemetry request; or

(e)	File a request with the Public Utility Commission of Texas (PUCT) requesting expedited action for an Order directing that the responsibility for operational monitoring and reliability af this specific element or elements of the transmission system be withdrawn from ERCOT and assigned to the requesting TPT.  ERCOT will then immediately remove the elements from its Real- Time Congestion Maagement system as monitored elements pending the PUCT decision.

(5)	If ERCOT rejects the alternate solution provided by the TSP or QSE then that entity may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.

(6)	ERCOT shall contract the TSP or QSE for verification of receipt of a ERCOT request for additional telemetry if ERCOT has not received acknowledgement from the TSP or QSAE that a request has been received by within thi days of is sending., E QSE for verification of rece

(7)	Nothing in this section shall limit the SPP’s or QSE’s appeal process outlined in Protocol Section 3.10.7.4, Telemetry Criteria.

8.1.65.2.1	General Telemetry Performance Criterion

The following criterion will apply in general to Real-Time telemetry provided to ERCOT:

(1)	be greater than 4% of full scale.(2)	The TSP shall maintain the sum of flows into any telemetered bus less than the greater of 5 MW or 5% of the largest line rating at each bus.

(2)	Each QSE or TPT shall provide telemetry data to ERCOT such thatllowing availNinety-eight (98%) percent of all telemetry provided to ERCOT must achieves a montterly availability of at least eighty (80%) percent., excAvailability will be measured based on end-to-end connectivity of the  comunications path and the passing of Real-Time data with good quality codes at the scheduled periodicity.

(b)	ICCP links must achieve a monthly availability of ninety-eight (98%) percent of the time, excluding approved planned outages.  Availability will be measured based on end-to-end connectivity of the  communications path and the passing of Real-Time data.  A link will be considered as available when at least eighty-five (85%) percent of the data defined on that link is successfully transferred to ERCOT with a  quality code.  This will include establishing a process to coordinate downtime for ICCP links and database maintenance.

TDSSPshll make reasonable efforts to obtain tels from retail Ccutomers asociated with new Ccutomer-ownd substations to meet this standard or obtain agreement from ERCOT that these retail Ccutomers hav entered into arrangements with ERCOT to provide this data to ERCOT.  If the data cannot be obtained under either of these methoids ERCOT shall report such case to the PUClesale Electric Market Monitor.

(4)	Tsubstations to provide this data and meet this standard  obtain into agreements with ERCOT to provide this data.(5)Exceptio not significant toin the solution of the State Estimator or required for the reliable operation onf the ERCOT Transmission System.  Some examples of these are:

(a)	Substation with no more than two transmission lines and less than 10 MW of load;

(b)	Connection of Loads along a continuous, non-branching circuit that may be combined for telemetry purposes;

(c)	Substations connected radially to the bulk transmission system.

8.1.5.2.2	Critically Important Telemetry Performance Criterion

(1)	ERCOT shall create a list of those  MW/MVAR tTelemetry pairs, nt exceedin 10% of the lines Transmissements in ERCOT, and up to twenty (20) voltage points thaentifiedas “critically important” to reliability, system observability, support of State Estimator performance, or are of a commercial Market concern. TheseThis list itically important telemetry must meet more stringent criterion for accuracy and availability where specifically addressed. ERCOT willshall review and publish thist annually. ERCOT willshall use the following criterio identify critically important tTelemetry:

(a)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(b)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(c)	Loss of a telemetry point that results in the inability of ERCOT to monitor  loading on transmission facilities designated as critically important to transmission reliability by ERCOT. A list of these critical facilities will be published annually.

(d)	Telemetry necessary to monitor transmission elements identified as causing 80% of congestion cost in the year for which the most recent data is available..

(e)	Telemetry necessary to monitor the t0) most votage critical buses designated by ERCOT and approved by TAC each October.

(2)	itically important Telemetry provided toCrit

Each QSE or TDSPTSP shall provide identified critical telemetry data to ERCOT such that meets the following availability:

(980%) percent of h dingneges.  Avalabil-end connectivity of the  communicationsd the passing of Real-Time data with Vvalid or Mmanual  good uality codes at the schedlty.  A link ll be onsiderablishing  process to coordinate downtime for ICCP links, critically iortant RTU’s and database maintenance.

8.1.5.3	State Estimator Data

The ERCOT State Estimator produces load flow base cases which are used to analyze the reliability of the transmission grid. Accurate and redundant telemetry and an accurate transmission power system model are required by sState eEstimator in orderto prodce an optimal estimation of the transmission power system state. The sState eEstimator results ar used n contingency analysis, congestion management, and other network analysis real-time sequence functions.

8.1.5.3.1	Telemetry Status and Analog Measurements Data

(1)	The quality and availability of telemetry provided to ERCOT are important to the performance of the ERCOT State Estimator.  Acquisition of good telemetry status and analog measurements data (Telemetry) for the transmission power system (System) together with an accurate model of the System are processed by a state estimator to provide an optimal estimate of the System state at a given point in time while filtering measurement noise (error) and detecting gross errors.

telemetry provided to ERCOT are mT State Estimator.

(2)	Telemetry is not needed at every bus of the System network model to arrive at a good estimate of the System’s state. There are general telemetry performance criterion, such that sufficient numbers and placement of measurements and accuracy of measurements thatavailable to achieve System observability and an overall good State Estimator performance.

(3)	Beyond general telemetry performance criterion there are more stringent criterion needed at locations where state estimates are “critically important” due to reliability, security, and Market impact are of more focused con

8.1.5.3.2	State Estimator Performance Requirements

(1)	The ERCOT     e Estimator performance shall converges for  97%of run during a one wely est period.

(2)

(bje

tTansmission eElements identified as causing 80% of congestion cost in the latest year for which data is available, the difference between the MW telemetry value and the MW State Estimaor vale shall be less than 3% of the associated element emergency rating on at least 95% of samples measured in a one month trial.

(4)	ERCOT will confirm that the MW base case element flows used in contingency analmato line flows used in creaObjective met if difference of all identified elements < 3% of equipment  over 95% of samples measured during a 1 month trial.  To be measured on all State estimator samples of each month and posted.

each October; Telemeter bus voltage minus state estimator voltage within 2% orObjective met if difference of all identified voltages < equipment accuracy or 2% of nominal voltage over 95% of samples measured during a 1 month trial.  To be measured on all State estimator samples of each month and posted.On the twenty (20) most voltage critical buses designated by ERCOT and approved by TAC each October,; tThe difference between the telemetered bus voltage and the minus sState eEstimator voltage shall be within the greater of 2% or the accuracy of the telemetered voltage measurement involved for at least 95% of samples measured during a one1 month trial.

(5)	On all Transmission Eeements greater than 100kV, ; e difference between sSate eEsimator MW solution and the SCADA measurement will be less than 10 MW or 10% of the associated emergency rating (whichever is greater) on 99.5% of all elements during a 30 day period.  All equipment failing this test will be reported to the associated TSP providing the measurement data for investigation and correction repaithi0 days of detection.

On all transmission elements > 100KV; the difference between state estimator MW solution and the scada measurement will be less than 10 MW or 10% of the associated emergency rating (whichever is greater) on 99.5% of all equipment.  All equipment failing this test will be reported to the associated TSP for repair within 10 days of detection.

(6)	To meet these State Estimator objectives ERCOT shallwill:

(a)      Work with TSP’s to resolveidentified problems in accordance with ERCOT these Opg Guides prior to requesting directing adquipment;.

(b)       In event of failure to meet the standard in 8.1.6.3.2 2 and  ERCOT may requestdirect additionemetry be installed on llements contributing most to 80% of congestion costs for the latest year for which data is available, to l protocols.  65.5.2 (7)). If the TSP disputes the ERCOT request for additional telemetry, the TSss available under Operating Guide Section 8.1.56.2, ERCOT Requests for Telemetry;.

(c)      	Enforce the requirements of Protocol 3.10.7.4.2 (5), Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows,  by alarming any sum of flow around a bus the greater of 5% of the largest line rating connected to the bus or 5MW, and requesting that the applicable TSP or QSE correct the failure;.

(d)	Post monthly results for compliance with Section 8.1.6.3.2 items 1 through 5 above; and.

(e)	ERCOT shall consider the quality codes sent by the data provider in assigning confidence factors for the data to be used in the State Estimator.  Valid and Manual quality codes shall be considered as good quality.  Quality codes sent as not good quality shall be considered at a lower confidence.  The confidence shall continue to decrease over time.

8.1.76	TSP and /QSE Telemetry Restoration

Real-time telemetryedata shall be provided continuously.  Data that is inaccurate or of bad qualityLoshether failed or in error, must be restored promptly by the provider of the telemeterye data.  It is recognized that some data may be of more importance criti other data.  ERCOT will inform the TSP or QSE of if a dn this category that item ito be repaired to service as quickly as possible.  QSE’s and SP’s shallprovide information to ERCOT of any and all corrective actions taken to restore reported telemetry errors repairOT upon request.  When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 2b days, take corrective action to either

(a)	Calibrate/repair the mis-behaving equipment;

(b)	Request an outage to schedule calibration/repair of the mis-behaving equipment;

(c)	Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame; or

(d) 	Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.

Before ERCOT requests review/re-calibration of a telemetry problem with a piece of equipment it shall discuss the problem with the provider to attempt to arrive at a consensus decision for the most appropriate action.

8.1.7	QSE and TSP Data Acquisition

Suppliers of Real-Ttme telemetry must collect and process telemetry data from field equipment at their control centers before passing to the ERCOT interface.  The equipment and processes are owned and operated entirely by the supplier.  Traditionally, utilities have used both analog and digital methods of transmission at existing facilities.  It is the responsibility of the QSEs and TSPs who supply other Eenities’ data to ERCOT to also arrange for reliable delivery of telemetry data from the field equipment from the other entities in order to support the requirements in these Operating Guides.

## 8.2	Calibration and Testing

8.2.1	Responsibility

It is the responsibility of the owner of telemetry equipment to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds that which is specified in these Operating Guides, for both the overall system and for individual equipment where detailed herein.  Coordination of Ooutags required for these activities with ERCOT is also the responsibility of the owner.  Upon ERCOT’s request, eEach SP and QSE shall upon Rest furnisde ERCOT access to its preventive maintenance and calibration test procedures and records for purposes of  assureing accurate telemetry of data.  If a TSP and/or QSE epeatedly fails other telemetry metrics defined in these Operating Ggides, ERCOT may require the owner to revise its procedures to ensure accuracy and availability of telemetry dataa revision of this plan.

8.2.2	Notification

ERCOT and all affected parties shall be notified at least 72 hours in advance, or at a mutually acceptable advance notice, prior to any calibrations or planned maintenance. In Emergency Conditions, the owner of the telemetry and associated equipment may make necessary repairs with notification to affected parties within 24 hours.  ERCOT or other parties sharing data from the equipment may request copies of the repair and calibration records.

8.2.3	Test Equipment

Test equipment and test standards intended to be used for the calibration of telemetry and associated equipment shall have an accuracy and precision that are equal to or better than the accuracy of the equipment under test.

8.2.4	Disputes

Where a dispute over the accuracy or performance of any telemetry equipment exists, ERCOT may request a comparison of standards and/or a joint calibration of affected equipment.

8.2.5	Calibration Testing

All telemetry and associated equipment for analog data quantities (MW, MVAR, Volts, LTC tap positions, etc.) shall be tested as needed to ensure accuracy and performance.  Entities providing telemetry data to ERCOT shall make their test records, procedures and maintenance criteria available to ERCOT upon request.

8.2.6	Exchange of Information

Before energizing and placing into service any new or relocated facility connected to the ERCOT Transmission Grid, a TSP, QSE, or Resource Entity shall enter appropriate information in the Outage Scheduler and coordinate with ERCOT, and receive written notice of approval from, ERCOT, as specified in Protocol Section 3.3.1, ERCOT Approval of New or Relocated Facilities.

8.2.7	Documentation

(1)

Information on existing and future ERCOT System

(a).Information necessary to represent the TSP’s Transmission Facilities in any model of the ERCOT Transmission Grid whose creation has been approved by ERCOT, including modeling information detailed in procedures of ERCOT and the Network Data Support Working Group (NDSWG); a

(b)2.	Identification of a designated TSP contact person thate ERCOT can contact regarding questions ERCOT may have on the information provided;.

(c).Consistent data with existing ERCOT Transmission Facilities owned or operated by the TSP represented in the appropriate pPlnning mModl.  At a minimum, the impedance data (resistance, reactance, and charging), Continuous Rating, and Emergency Rating shall exactly match corresponding data represented in the pPlaning mModel  TSPs shall provide reasons for any data that does not exactly match.

(2)	The energization or removal of equipment in the Network Operations Model shall be done in accordance with Protocol Section 3.3.2.1, Information to Be Provided to ERCOT.(a)	Proposed energize date;

(c)	TSP(s) responsible for rating affected transmission element(s);

(e)	Identification of existing Transmission Facilities involved and new Transmission Facilities (if any) being added or existing Transmission Facilities being permanently removed from service;

(g)	Outages required (clearly identify each Outage if multiple Outages are required), including sequence of Outage and estimate of Outage duration;

(i)	Supervisory Control and Data Acquisition modification work, including descriptions of the telemetry points or changes to existing telemetry, providing information on equipment being installed, changed, or monitored;

(k)	Statement of completion, including:

(ii)	Statement to be made at completion of total project.

(i)	Existing status;

(iii)	Proposed final configuration.

(3)	TSPs

shall furnish pertinent information to ERCOT on request, including the following:

(a)	Connection diagrams;

(b)	Metering one line diagram;

(c)	Substation one line diagram;

(d)	Panel schematics and one line diagrams;

(e)	Instrument transformer (CT and PT) data (ratios, test reports, nameplate);

(f)	Transducer conversion constants;

(g)	Meter constants;

(h)

Certified calibration test reports of any device used for telemetry; and

(i)	Other data as may be requested.

8.2.8	Operator One-line Displays

Market Participants providing Telemetry data to ERCOT shall have one-line diagrams displayable on their computer systems for viewing by its operations staff.  Displays shall be provided for all substations or power plant switchyards that include data passed to the ERCOT interface.

8.2.9	Notification of Changes

(11) rk Opemetry , Changes to Work

(1)	 ERCOT shall review the information and notify the requestor of any required modifications in ccordance with Protocol Section 3.10 (11), Network Operations Modeling and Telemetry.  ERCOT may, at its discretion, require changes or more details regarding the work plan for the .

(2)	ERCOT and any other affected parties shall be informed of changes to telemetry and associated equipment per Protocol Section 3.10.1, Time Line for Network Operations Model Change Requests.

## 8.3	Communications

The following sections describe the communications

standards of the wide area network (WAN) utilized for Real-Time data communications (Operational) and voice communications (Operational) that shall be used to exchange security and reliability information between:

(a)	ERCOT and a QSE; and

(b)	ERCOT and a TSP.

8.3.1	ERCOT WAN

ERCOT shall provide for a wide area network (ERCOT WAN) for secure communications path between ERCOT and the Market Participants in order to facilitate wholesale operations and frequency control as a single control area.  This communications network uses redundant, digital communications between ERCOT control centers and one or more facilities at each QSE and TSP.  The ERCOT WAN shall have sufficient bandwidth capacity and speed to enable:

(1)	Real-time (telemetry) data exchange for frequency control and transmission security;

(2)	Operational voice communications for both normal and emergency use.  The ERCOT WAN supports both off-premise exchanges (OPX) with ERCOT’s control facilities and the ERCOT hotlines; and

(3)	Data exchange to support applications programming interface (API) routines.  These include power scheduling, operating plans, outage requests, dispatch instructions, posting of information and other applications.

8.3.1.1	QSE Use of Domain Name Service (DNS) or ERCOT Web-Based Front Page for Site Failover

A QSE possessing backup sites must utilize one of the following two options:

(a)	A  AN (Wide Area Network) Domain Name Service (DNS) server; or

(b)	An  nCOT provided web-based DNS service to facilitate the failover process when moving its operations between primary and backup sites.

The requirements of these options are specified below.

8.3.1.1.1	DNS Server Configuration for Failover Support

(1)	A QSE is required to provide and maintain its own DNS servers that must be accessible by the ERCOT WAN.  The failover process requires the following:

(a)	DNS servers must support zone transfers over TCP port 53;.

(b)	Firewalls must allow zone transfers to ERCOT DNS servers;.

(c)	Zone files for the QSE's domains, (.g. www.examplepower.com, ) ut reside on its WAN accessible DNS servers;.

(d)	DNS servers must be set up as the master for its zone;.

(e)	DNS servers must allow ERCOT DNS servers to transfer the zone files (ERCOT will be set up as a secondary/slave server for the zone);.

(f)	The zone files must contain names for all local servers the QSE will need ERCOT services to access.  At a minimum, it must contain entries for the servers that can be switched over to the backup site.  The zone file must also contain entries for the QSE's primary website address,  .g. www.examplepower.com, ) a other common internet accessible sites that ERCOT servers may have occasional need to access; and.

(g)	Time to Live (TTL) values for backup host entries in the zone file must be set to 0 in order to prevent the host to IP address mappings from being cached on the client machines.  This allows any changes made to a zone file to take effect immediately upon a zone transfer.

(2)	Once its DNS servers are operational, the QSE shall timely contact its ERCOT Client Services Representative and request that an ERCOT network administrator work with the QSE to test the functionality of the DNS setup.  The QSE must contact the ERCOT Client Services Representative at least five Business Days before testing.

(3)	After the zone transfer testing is complete, the QSE shall supply its ERCOT Client Services Representative with a list of participant servers, their DNS names, and their roles on the network.  The ERCOT Client Services Representative will then contact the application owners at ERCOT to change application communications to use the DNS name instead of IP addresses.

(4)	After successful completion of the test, when a QSE backup site failover is desired, the QSE shall update the zone file with its disaster recovery IP addresses and publish it to the ERCOT DNS servers.  The change will be effective immediately.  The QSE shall also implement a DNS server at its backup site.  This allows updated zone files to be published regardless if the primary site is up or not.

8.3.1.1.2	Web-Based DNS Access

(1)	This access is provided as an alternative method for any QSE that does not wish to maintain its own DNS servers.  Access is provided over the ERCOT WAN only.  The QSE is responsible for access through its networks to the web servers located on the ERCOT WAN.  The QSE shall adhere to ERCOT password requirements.

(2)	To failover to or from a backup site, the QSE shall update the IP address of the existing entry.  ERCOT servers will accept the change and start using the new IP immediately.

(3)	Once the QSE has connectivity to the web server over the ERCOT WAN, it shall contact its ERCOT Client Services Representative and request that an ERCOT network administrator work with the QSE to test the functionality of the DNS setup.  The QSE shall contact the ERCOT Client Services Representative at least five Business Days before testing.  After testing is completed, the Client Services Representative will contact the application owners at ERCOT to change application communications to use DNS names instead of IP addresses.

(4)	After successful completion of the test, when a QSE site failover is desired, the QSE shall change the Web page entries with the active site information and the change will be effective immediately.

8.3.2	ERCOT Responsibilities

ERCOT supplies interface requirements, equipment, installation and 24-hour maintenance for the entire ERCOT WAN, including equipment at each QSE and TSP control facility, as well as ERCOT’s control centers.  ERCOT’s responsibilities include:

(a)	Supply and install fully configured and tested Customer Premises Equipment including routers, CSU/DSUs, LAN switch/hub and all support equipment for management purposesl

(b)	Order and provision of local loop, network access point and transport;

(c)	Design, configure, test, and install network monitoring and management service;

(d)	Provide 24-hour network monitoring and management;

(e)	Provide 24X7 maintenance, with 4-hour response, for all ERCOT equipment located at participant site; and

(f)	ERCOT will be the single point of contact for all network issues.

8.3.3	QSE and TSP Responsibilities

(1)	TSPs and QSEs whose facilities connect to the ERCOT WAN are required to sign an agreement with ERCOT governing installation, operation and maintenance.  Users of the ERCOT WAN shall provide signal connections, uninterruptible power, and physical space for ERCOT-supplied WAN interface equipment at their control centers, as well as 24-hour access for ERCOT installation and maintenance personnel.

(2)	At these facilities, computer and communications equipment connected to ERCOT WAN interfaces is the complete responsibility of the QSE or TSP.   Facilities shall have uninterruptible power supplies (UPS) capable of independently supplying all equipment connected to the ERCOT WAN for at least 72 hours.

(3)	Any TSP or QSE facility, whether primary or backup, involved in the transfer of the data sets identified in Attachment 8A, will be required to connect directly to the ERCOT WAN Primary Private Network and Point-to-Point paths. If a TSP and QSE utilize the same EMS and server network at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TSP and QSE share a centralized PBX, separate OPX circuits will be terminated for each participant.  The Hotline will not be allowed to connect through the PBX system and is required for each participant.

(4)	A QSE or TSP involved in the transfer of the critical data identified in Attachment 8A of this guide, will be required to provide the following communication resources to support the connection to the ERCOT private network:

(a)

Provide an analog business phone line or PBX analog extension for trouble-shooting and maintenance of equipment;

(b)	Provide a height of 24” of rack space in a 19” wide rack;

(c)	Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above;

(d)	Provide building wiring from circuit termination to equipment rack;

(e)	Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility;

(f)	Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors;

(g)	Provide on site personnel to escort ERCOT employees or contractors;

(h)	Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN;

(i)	Market Participant will be required to sign a security connection agreement with ERCOT;

(j)	Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site. Market Participants are responsible for their own security through this connection;

(k)	Provide a channel bank with at least one T1 interface, 4 FXS and two 4 wire analog ports. Connect FXS (e.g. PBX, key system) and 4 wire ports to the appropriate equipment.  On the digital T1 stream, levels for voice are zero dpm for transmit and receive;

(l)	Hotline must be a 500 set not attached to the Market Participant’s Phone System;

(m)	Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended; and

(n)	Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential.

(5)	Internet (optional)

A QSE or TSP not involved in the transfer of the data identified in Attachment 8A of these Operating Guides, is not required to, but, may request ERCOT to provide an optional connection to the ERCOT private network.  When such a request is met by ERCOT, the QSE or TSP must then provide the above stated communications resources.

8.3.4	TSP and QSE Supplied Communications

(1)	Each TSP and QSE must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN.  For TSPs these include, but may not be limited to, voice communications and SCADA for substations and other Transmission Facilities.  For QSEs, these include, but may not be limited to, voice and SCADA for generating plants and loads.

(2)	QSEs and TSPs shall supply, implement and maintain all data and voice communication facilities required to fulfill the obligations set forth in these Operating Guides.

(3)	Proper performance, maintenance and testing of communication paths not directly connected to the ERCOT WAN shall be the responsibility of the TSP or QSE providing the path.

(4)	QSEs communicating with connected resources and TSPs communicating with substations are encouraged to use privately owned communication facilities.  Backup facilities utilizing common carriers, different privately owned facilities, or communications paths to a site are encouraged to provide increased reliability, i.e. separate paths to a site using different carrier, having multiple microwave paths leaving a site, etc.

8.3.5	Maintenance and Restoration

(1)	It is the joint responsibility of ERCOT WAN-connected parties to coordinate maintenance and restoration activities so its reliability is not compromised.  Coordination and notification procedures defined by ERCOT are to be followed by all parties.

(2)	All circuits shall be tested annually or as otherwise requested by ERCOT for end-to-end performance.  Special attention shall be given to circuits not used for routine communications (including backup circuits).

(3)	The hotline and any backup (alternate path) voice circuits shall be used regularly to insure proper performance.  ERCOT will specify test procedures for hotline circuits.

(4)	Scheduled outages of communication circuits that could reduce the reliability of interconnected operations shall be coordinated between the affected companies and ERCOT.

(5)	In the event of wide spread communication failures, priority shall be given to restoring communication circuits between QSE Control Centers/TSP Control Centers and ERCOT first, and then between QSEs and TSPs second.

(6)	Test equipment and test standards intended to be used for the calibration or repair of communication equipment shall be certified to values of accuracy and precision, which are equal to or better than the accuracy of the equipment under test.

### Authorities

Distribution List

Change History

Attachment 8A:	ERCOT Data Sets

For any required data, the following table describes how the data is to be provided to ERCOT or is provided from ERCOT.

| ACTION |  | DATA QUANTITY |  | PURPOSE |  | SUPPLIED BY |  | RECEIVED BY |  | FREQUENCY |  | MODE OF COMM. |  | FORMAT |  | PROTOCOLS REFERENCE / COMMENTS |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DAY-AHEAD SCHEDULING PROCESS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Day Ahead Notification |  | Network Operations Model topology which includes Transmission Outages |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area |  | XML |  | Protocol Section 4.2.3 (a), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Weather assumptions used by ERCOT to forecast system conditions |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area |  | XML |  | Protocol Section 4.2.3 (b), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Any weather-related changes to the transmission contingency list |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area |  | XML |  | Protocol Section 4.2.3 (c), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | ERCOT System, Weather Zone, and Load Zone Load forecasts for next seven days |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area |  | XML |  | Protocol Section 4.2.3 (d), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Load forecast distribution factors |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area |  | XML |  | Protocol Section 4.2.3 (e), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Load Profiles for non-IDR metered Customers |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area MIS Secure Area |  |  |  | Protocol Section 4.2.3 (f), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Distribution Loss Factors and forecasted ERCOT-wide Transmission Loss Factors |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area MIS Secure Area |  |  |  | Protocol Section 4.2.3 (g), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Current list of Settlements Points that may be used for market processes & transactions |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area MIS Secure Area |  |  |  | Protocol Section 4.2.3 (h), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Mapping of Settlement Points to Electrical Buses in the Network Operations Model |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Secure Area MIS Secure Area |  |  |  | Protocol Section 4.2.3(i), Posting Forecasted ERCOT System Conditions |  |  |
|  |  | Wind-Powered Generation Resource Production Potential forecasts |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Each Hour |  | API & MIS Certified Area |  | XML |  | Protocol Section 4.2.2 (4), Wind-Powered Generation Resource Production Potential |  |  |
|  |  | Aggregated Wind-Powered Generation Resource Production Potential forecasts |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Each Hour |  | API & MIS Secure Area |  | XML |  | Protocol Section 4.2.2 (5), Wind-Powered Generation Resource Production Potential |  |  |
|  |  | Ancillary Services Plan |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Public Area |  | XML |  | Protocol Section 4.2.1.1(1), Ancillary Services Plan |  |  |
|  |  | Ancillary Service Obligations |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Certified Area |  | XML |  | Protocol Section 4.2.1.2 (2), Ancillary Service Obligation Assignment and Notice |  |  |
|  |  | QSE’s Load Ratio Share used for the Ancillary Service Obligation calculation |  | Day-Ahead Planning |  | ERCOT |  | QSE |  | Daily by 0600 |  | API & MIS Certified Area |  | XML |  | Protocol Section 4.2.1.2 (3), Ancillary Service Obligation Assignment and Notice |  |  |
| Self-Arranged Ancillary Services |  | Self-Arranged Ancillary Service Quantities, by service |  | QSE submit Self-Arranged Ancillary Service |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.7.1 (2), Self-Arranged Ancillary Services Quantities |  |  |
| Ancillary Service Offers |  | Generation Resource-specific Ancillary Service Offers |  | QSE submit Ancillary Service Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.7.2 (1), Ancillary Service Offers |  |  |
|  |  | Load Resource-specific Ancillary Service Offers |  | QSE submit Ancillary Service Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.7.2 (2), Ancillary Service Offers |  |  |
|  |  | Ancillary Service Offer Validation |  | Notify QSE of invalid Offers |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.7.2.2 (3), Ancillary Service Offer Validation |  |  |
|  |  | Corrected Ancillary Service Offers |  | QSE submit corrected Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.7.2.2 (3), Ancillary Service Offer Validation |  |  |
| Ancillary Service Trades |  |  |  | QSE submit Ancillary Service Trades |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 4.4.7.3 (2), Ancillary Service Trades |  |  |
|  |  | Ancillary Service Trades Validation |  | Notify QSE of invalid Trades |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.7.3 (3), Ancillary Service Trades |  |  |
|  |  | Corrected Ancillary Service Trades |  | Submit Corrected Trades |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 4.4.7.3 (3), Ancillary Service Trades |  |  |
|  |  | Valid Trades |  | Notify both buying and selling QSE |  | ERCOT |  | QSE |  | As needed |  | API & MIS Certified Area |  | XML |  | Protocol Section 4.4.7.3.2 (2), Ancillary Service Trade Validation |  |  |
| Current Operating Plan (COP) |  | Submit for any Resource and for Resources that will provide Ancillary Service |  | QSE submit COP |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 3.9.1, Current Operating Plan (COP) Criteria and 4.4.7.4 (3), Ancillary Service Supply Responsibility |  |  |
|  |  | Current Operating Plan Validation |  | Notify QSE of invalid COP |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 3.9.2 (4), Current Operating Plan Validation |  |  |
| Capacity Trades |  |  |  | QSE submit Capacity Trades |  | QSE |  | ERCOT |  | Daily bye1430 will n the DRUC pr |  | API |  | XML |  | Protocol Section 4.4.1 (2), Capacity Trades |  |  |
|  |  |  |  |  |  |  |  |  |  |  | , if feill be u |  |  |  |  |  | 3), Capacity Trades |  |
|  |  | Capacity Trade Validation |  | Notify QSE of invalid Capacity Trades |  | ERCOT |  | QSE |  | As needed |  | API & MIS Certified Area |  | XML |  | Protocol Section 4.4.1.2 (2), Capacity Trade Validation |  |  |
|  |  | Corrected Capacity Trades |  | QSE submit corrected Trades |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 4.4.1 (4), Capacity Trades |  |  |
| Energy Trades |  |  |  | QSE submit Energy Trades |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 4.4.2 (2), Energy Trades |  |  |
|  |  |  |  |  | Invalid Capacity Trades |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Energy Trades Validation |  | Notify QSE of invalid Trades |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.2 (24, Energy Trades Val |  |  |
|  |  | Corrected Energy Trades |  | QSE submit corrected Trades |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 4.4.2 (4), Energy Trades |  |  |
| Three-Part Supply Offers |  | Energy Offer Curve, Startup offers and Minimum-Energy Offers |  | QSE submit Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.2.1 (2), Startup Offer and Minimum-Energy Offer Criteria |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | MIS Certified Area |  |  |  |  |  |
|  |  | Three-Part Supply Offer Validation |  | Notify QSE of invalid Offers |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.9.2.2 (3), Startup Offer and Minimum-Energy Offer Validation |  |  |
|  |  | Corrected Three-Part Supply Offers |  | QSE submit correct Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.2.2 (3), Startup Offer and Minimum-Energy Offer Validation |  |  |
| DAM Energy-Only Offer Curve |  |  |  | QSE submit DAM Energy-Only Offer Curve |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.5 (1), DAM Energy-Only Offer Curves |  |  |
|  |  | Energy-Only Offer Curve Validation |  | Notify QSE of invalid Offers |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.9.5.2 (2), DAM Energy-Only Offer Validation |  |  |
|  |  | Corrected Energy-Only Offer Curve |  | QSE submit corrected Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.5.2 (2), DAM Energy-Only Offer Validation |  |  |
| DAM Energy Bids |  |  |  | QSE submit DAM Energy Bids |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.6 (1), DAM Energy Bids |  |  |
|  |  | Energy Bid Validation |  | Notify QSE of invalid Bids |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.9.6 (2), DAM Energy Bid Validation |  |  |
|  |  | Corrected Energy Bids |  | QSE submit corrected bids |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.6 (2), DAM Energy Bids Validation |  |  |
| Energy Offer Curve |  |  |  | QSE submit Energy Offer Curve |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.3 (2), Energy Offer Curve |  |  |
|  |  | Energy Offer Curve Validation |  | Notify QSE of invalid Offer Curve |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.9.3.2 (2), Energy Offer Curve Validation |  |  |
|  |  | Corrected Energy Offer Curve |  | QSE submit corrected Offer Curve |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.9.3.2 (2), Energy Offer Curve Validation |  |  |
| Self-Schedules |  |  |  | QSE submit Self-Schedules |  | QSE |  | ERCOT |  | Any interval before the end of the Adjustment Period |  | API |  | XML |  | Protocol Section 4.4.3 Self-Schedules |  |  |
|  |  | Self-Schedules Validation |  | Notify QSE of invalid Self-Schedules |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.3 (3), Self-Schedules |  |  |
|  |  | Corrected Self-Schedules |  | QSE submit corrected Self-Schedules |  | QSE |  | ERCOT |  | As needed |  | API |  | XML |  | Protocol Section 4.4.3 (3), Self-Schedules |  |  |
| DC Tie Schedules |  |  |  | QSE’s Submit DC-Tie Schedules |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 4.4.4 (3), DC Tie Schedules |  |  |
|  |  | DC-Tie Schedule Validation |  | Notify QSE of invalid DC-Tie Schedule |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.4 (4), DC Tie Schedules |  |  |
|  |  | Corrected DC-Tie Schedules |  | QSE submit corrected information |  | QSE |  | ERCOT |  | Daily by 1430 |  | API |  | XML |  | Protocol Section 4.4.4 (4), DC Tie Schedules |  |  |
| CRR Offers |  | CRR Account Holders to sell CRRs in DAM |  | QSE submit CRR Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.5, CRR Offers |  |  |
|  |  | CRR Offer Validation |  | Notify QSE of invalid Offers |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.5.2 (3), CRR Offer Validation |  |  |
|  |  | Corrected CRR Offers |  | QSE submit corrected Offers |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.5.2 (3), CRR Offers |  |  |
| PTP Obligation Bids |  |  |  | QSE submit PTP Obligation Bids |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.6.1 (1), PTP Obligation Bid Criteria |  |  |
|  |  | PTP Obligation Bid Validation |  | Notify QSE of invalid Bids |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 4.4.6.2 (3), PTP Obligation Bid Validation |  |  |
|  |  | Corrected PTP Obligation Bids |  | QSE submit corrected Bids |  | QSE |  | ERCOT |  | Daily by 1000 |  | API |  | XML |  | Protocol Section 4.4.6.2 (3), PTP Obligation Bid Validation |  |  |
| DAM Results |  |  |  | Awarded DAM Transactions |  | ERCOT |  | QSE |  | Daily, no later than 1330 |  | API |  | XML |  | Protocol Section 4.5.3 (1), Communicating DAM Results |  |  |
|  |  | MCPC, Settlement Point Prices, LMPs, Shadow Prices, Quantities |  | View additional information |  | ERCOT |  | QSE |  | Daily, no later than 1330 |  | API & MIS Public Area |  | XML |  | Protocol Section 4.5.3 (2), Communicating DAM Results |  |  |
| QSE Current Operating Plan |  | Resource Availability Status |  | QSE submit COP |  | QSE |  | ERCOT |  | Daily by 1430, then as needed |  | API |  | XML |  | Protocol Section 3.9, Current Operating Plan (COP) 44..43Ancla |  |  |
|  |  |  |  | Notify QSE of invalid COP |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 3.9.2 (1), Current Operating Plan Validation |  |  |
|  |  |  |  | QSE correct COP |  | QSE |  | ERCOT |  | Daily by 1430, then as needed |  | API |  | XML |  | Protocol Section 3.9.2 (1), Current Operating Plan Validation |  |  |
| ADJUSTMENT PERIOD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Adjustment Period Schedule Changes |  | Current Operating Plan |  | QSE submit and update Resource Status |  | QSE |  | ERCOT |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.4.5, Resource Status |  |  |
|  |  | Capacity Trades, Energy Trades, Self-Schedules, and Ancillary Service Trades |  | QSE submit and update Trades and Schedules |  | QSE |  | ERCOT |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.4.1, Capacity Trades, Energy Trades, Self-Schedule, and Ancillary Service Trades |  |  |
|  |  | Output Schedules |  | QSE submit and update Output Schedules |  | QSE |  | ERCOT |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.4.2, Output Schedules |  |  |
|  |  | Non-DSR Resource |  | QSE submit and update Output schedule for a non-DSR Resource |  | QSE |  | ERCOT |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.4.2.1, Output Schedules for Resources Other than Dynamically Scheduled Resources |  |  |
|  |  |  |  | QSE submit Incremental and Decremental Energy Offer Curves for DSRs |  | QSE |  | ERCOT |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.4.2.2, Output Schedules Dynamically Scheduled Resources |  |  |
|  |  | Energy Offer Curve |  | QSE submit and update Energy Offer Curves |  | QSE |  | ERCOT |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.4.3 (3), Energy Offer Curve |  |  |
|  |  | Three-Part Supply Offers |  | QSE submit Three-Part Supply Offers for Off-line Generation Resources |  | QSE |  | ERCOT |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.3.1 (1), Activities for the Adjustment Period |  |  |
|  |  |  |  | Notify QSEs of HRUC results |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 5.5.3 (2), Communication of RUC Commitments and Decommitments |  |  |
| Supplemental Ancillary Service Market |  |  |  | Notify QSEs of intent to procure additional Ancillary Services |  | ERCOT |  | QSE |  | As needed during Adjustment Period |  | API |  | XML |  | Protocol Section 6.4.8.2 (2), Supplemental Ancillary Service Market |  |  |
|  |  |  |  | QSEs may resubmit Ancillary Service Offers |  | QSE |  | ERCOT |  | 30 minutes from time of notice |  | API |  | XML |  | Protocol Section 6.4.8.2 (2), Supplemental Ancillary Service Market |  |  |
|  |  |  |  | Notify QSEs with awards |  | ERCOT |  | QSE |  | As needed |  | API |  | XML |  | Protocol Section 6.4.8.2 (2), Supplemental Ancillary Service Market |  |  |
|  |  |  |  | QSE submit updated COP and updated Ancillary Service Schedule |  | QSE |  | ERCOT |  | As needed |  | API |  | XML |  | Protocol Section 6.4.8.2 (2), Supplemental Ancillary Service Market |  |  |
| OPERATING PERIOD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| LFC Inputs |  | Frequency |  | Real-Time Monitoring and Control |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.6.1(3), LFC Process. |  |  |
| Generation Resource Data |  | Generation Resource MW |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) a, Operational Data Requirements Net and Gross Generation is required. |  |  |
|  |  | Generation Resource Mvar |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) b, Operational Data Requirements Net and Gross Reactive is required. |  |  |
|  |  | Plant Auxiliary Load |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) c, Operational Data Requirements. |  |  |
|  |  | Status of switching devices in the plant switchyard not monitored by the TSP affecting flows on the ERCOT System |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) d, Operational Data Requirements. |  |  |
|  |  | Generation Resource Breaker and Switch Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) f, Operational Data Requirements. |  |  |
|  |  | Generator Step-up Transformers Tap Position |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.1.13 (1) (d) (ii) (A), Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
|  |  | Generation Resource High Sustained Limit (HSL) |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.5 (1), Resource Status, Protocol Section 6.5.5.2 (2) g, Operational Data Requirements and Protocol Section 6.5.7.1.13 (1) (d) (ii) (B), Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
|  |  | Generation Resource Low Sustained Limit (LSL) |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.5 (1), Resource Status, Protocol Section 6.5.5.2 (2) j, Operational Data Requirements and Protocol Section 6.5.7.1.13 (1) (d) (ii) (C), Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
|  |  | Generation Resource High Emergency Limit (HEL) |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) h, Operational Data Requirements. |  |  |
|  |  | Generation Resource Low Emergency Limit (LEL) |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) j, Operational Data Requirements. |  |  |
|  |  | Text reason for any Resource where a ramp rate is deviating from a standard ramp rate curve for the resource, or the HSL is less than, or LSL is greater than, the normal high and low limits set in protocol section 3.7.1, Resource Parameter Criteria |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.5 (1), Resource Status |  |  |
|  |  | Generation Resource Normal Ramp Rate |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.5 (1), Resource Status. |  |  |
|  |  | Generation Resource Emergency Ramp Rate |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.5 (1), Resource Status. |  |  |
|  |  | Generation Resource Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.5 (1), Resource Status and 6.5.5.1(1). |  |  |
|  |  | Generation Resource Regulation Up Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) k, Operational Data Requirements. |  |  |
|  |  | Generation Resource Regulation Down Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) k, Operational Data Requirements. |  |  |
|  |  | Generation Resource Responsive Reserve Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) k, Operational Data Requirements. |  |  |
|  |  | Generation Resource Non-Spin Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) k, Operational Data Requirements. |  |  |
|  |  | Generation Resource Regulation Up Participation Factor |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) l, Operational Data Requirements. |  |  |
|  |  | Generation Resource Regulation Down Participation Factor |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) l, Operational Data Requirements. |  |  |
|  |  | Generation Resource Responsive Reserve Participation Factor |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) l, Operational Data Requirements. |  |  |
|  |  | Generation Resource Inhibit Regulation Up Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (6), Operational Data Requirements. |  |  |
|  |  | Generation Resource Inhibit Regulation Down Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (6), Operational Data Requirements. |  |  |
|  |  | Combined-Cycle Configuration |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (8) b, Operational Data Requirements. |  |  |
|  |  | Generation Resource DSR Base Point |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.6.1(8) j, LFC Process Description. |  |  |
|  |  | Private Network Net Interchange to ERCOT |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 Sec |  | ICCP |  | Blocks 1 & 2 |  | For private networks, the net interchange shall be provided along with gross MW and MVar per generation Resource. |  |  |
| Wind Powered Generation Resource Data |  | Wind Speed |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (4), Operational Data Requirements. |  |  |
| Load Resource Data |  | Load Resource MW |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2(4) a, Operational Data Requirements. Shall be telemetered to ERCOT using a (-) sign convention. |  |  |
|  |  | Resource Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.5 (1), Resource Status, Protocol Section 6.5.5.1(1), Changes in Resource Status, Protocol Section 6.5.5.2 (8) b & c, Operational Data Requirements. |  |  |
|  |  | Load Resource Breaker Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (4) c, Operational Data Requirements. |  |  |
|  |  | Load Resource Low Power Consumption (LPC) |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2(4) d, Operational Data Requirements. Shall be telemetered to ERCOT using a (-) sign convention |  |  |
|  |  | Load Resource Maximum Power Consumption (MPC) |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (4) e, Operational Data Requirements. Shall be telemetered to ERCOT using a (-) sign convention |  |  |
|  |  | Load Resource High-Set Under-frequency Relay Status (if RRS resource) |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (4) g, Operational Data Requirements. |  |  |
|  |  | Load Responsive Reserve Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (4) f, Operational Data Requirements. |  |  |
|  |  | Load Resource Responsive Reserve Participation Factor |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Regulation Down Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource Regulation Down Participation Factor |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource Regulation Up Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource Regulation Up Participation Factor |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource Non-Spin Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource Inhibit Regulation Up Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource Inhibit Regulation Down Status |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource NRAMP |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource ERAMP |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.6, Load Participation (implied). |  |  |
|  |  | Load Resource DSR Output Schedule |  | Real-Time Monitoring, SCED & Security Analysis |  | QSE |  | ERCOT |  | 2 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (2) e, Operational Data Requirements |  |  |
| Note: Requirements were written with the May 5, 2006 Protocols. This requirement came after that date. |  | Controllable Load Resource Scheduled Power Consumption that represents zero Ancillary Service Deployments |  | Real-Time Monitoring |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (4) h, Operational Data Requirements |  |  |
| Note: Requirements were written with the May 5, 2006 Protocols. This requirement came after that date. |  | Controllable Load Resource Net Reactive Power (in MVar) |  | Real-Time Monitoring |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2 (4) i, Operational Data Requirements |  |  |
| DSR Load |  | DSR Load Schedules |  | Real-Time Monitoring |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.2.5 (3) a, DSR Load. |  |  |
|  |  | DSR Output Schedules |  | Real-Time Monitoring |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.4.2.5 (3) a, DSR Load. |  |  |
| Bus Data |  | Unit High Side Bus Voltage kV |  | Real-Time Monitoring |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.5.2, Voltage Support Service, May be supplied by the TSP. Low Side with appropriate transformer model may be substituted. |  |  |
|  |  | Bus Voltage at Private Network connection to ERCOT |  | Real-Time Monitoring |  | QSE |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | This voltage may be supplied by the TSP. |  |  |
| Data sent to QSE |  | LMPs created by each SCED process for each Resource Node and the Settlement Point Price at each Hub and Load Zone |  | SCED Results |  | ERCOT |  | QSE |  | 5 min |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.3.2, Activities for Real-Time Operations |  |  |
|  |  | Regulation MW |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.6.2.1 (8), Deployment of Regulation Service. |  |  |
|  |  | Responsive Reserve MW |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.6.2.2 (11), Deployments of Responsive Reserve Service. |  |  |
|  |  | Non-Spinning Dispatch Instruction (on/off) |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.6.2.3 (4), Non-Spinning Reserve Service Deployment. |  |  |
| Generation Resource Data sent to QSE |  | Resource identifier |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.4 (a), Base Points. |  |  |
|  |  | Generator base point MW |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.4 (b), Base Points. |  |  |
|  |  | Generator LMP |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.3.2 (2), Activities for Real-Time Operations. |  |  |
|  |  | Generator Suspend Ramping to Base Point (on/off) |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.6.1 (9), LFC Process Description |  |  |
|  |  | Generator base point above HASL due to RRS (on/off) |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.4 (c), Base Points. |  |  |
|  |  | Time of Dispatch |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.4 (d), Base Points. |  |  |
|  |  | Pseudo unit dispatch (on/off) |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.4 (e), Base Points. |  |  |
| Emergency Base Point Data Packet |  | Resource Identifier |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.9.2 (3) c, Failure of the SCED Process. |  |  |
|  |  | Emergency base point (on/off) |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.9 (1), Emergency Operations. |  |  |
|  |  | Time of Dispatch Instruction - Start |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.9.2 (3) c, Failure of the SCED Process. |  |  |
|  |  | Time of Dispatch Instruction - Duration |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.9.2 (3) c, Failure of the SCED Process. |  |  |
| Bus Data Set |  | HUB or Load zone LMP |  | LFC |  | ERCOT |  | QSE |  | 4 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.3.2 (2), Activities for Real-Time Operations. |  |  |
| Ancillary Services Capacity Monitor |  | Responsive Reserve Capacity from Generation Resources |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) a, Ancillary Services Capacity Monitor. |  |  |
|  |  | Responsive Reserve Capacity from Load Resources |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) b, Ancillary Services Capacity Monitor. |  |  |
|  |  | Non-Spinning Reserve available from On-Line Generation Resources with Energy Offer Curves |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) c, Ancillary Services Capacity Monitor. |  |  |
|  |  | Non-Spinning Reserve available from undeployed Load Resources |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) d, Ancillary Services Capacity Monitor. |  |  |
|  |  | Non-Spinning Reserve available from Off-Line Generation Resources |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) e, Ancillary Services Capacity Monitor. |  |  |
|  |  | Non-Spinning Reserve available from Resources with Output Schedules |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) f, Ancillary Services Capacity Monitor. |  |  |
|  |  | Undeployed Regulation Up and Undeployed Regulation Down |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) g, Ancillary Services Capacity Monitor. |  |  |
|  |  | Available capacity with Energy Offer Curves in the ERCOT System that can used to increase Base Points in SCED |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) h, Ancillary Services Capacity Monitor. |  |  |
|  |  | Available capacity with Energy Offer Curves in the ERCOT System that can used to decrease Base Points in SCED |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) i, Ancillary Services Capacity Monitor. |  |  |
|  |  | Available capacity without Energy Offer Curves in the ERCOT System that can used to increase Base Points in SCED |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) j, Ancillary Services Capacity Monitor. |  |  |
|  |  | Available capacity with Energy Offer Curves in the ERCOT System that can used to decrease Base Points in SCED |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) k, Ancillary Services Capacity Monitor. |  |  |
| Note: Requirements were written with the May 5, 2006 Protocols. This requirement came after that date. |  | Responsive Reserve Capacity from Controllable Load Resources |  |  |  | ERCOT |  | QSE |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.5 (1) c, Ancillary Services Capacity Monitor |  |  |
| Security Analysis |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bus Data |  | Bus Voltage kV |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(i), Data Inputs and Outputs for the Real-Time Sequence and SCED |  |  |
| Transformer Data |  | Transformer Flow MW |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(ii), Data Inputs and Outputs for the Real-Time Sequence and SCED. Positive flow is into the transformer. |  |  |
|  |  | Transformer Flow Mvar |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(ii), Data Inputs and Outputs for the Real-Time Sequence and SCED. Positive flow is into the transformer |  |  |
|  |  | LTC Tap Position |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(v), Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
| Transmission Line Data |  | Line Flow MW |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(ii), Data Inputs and Outputs for the Real-Time Sequence and SCED. Positive flow is out of the station |  |  |
|  |  | Line Flow Mvar |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(ii), Data Inputs and Outputs for the Real-Time Sequence and SCED. Positive flow is out of the station |  |  |
| Shunt (Inductive or Capacitive Data |  | MW |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(ii), Data Inputs and Outputs for the Real-Time Sequence and SCED. Positive for supplying VAR Negative for absorbing VAR |  |  |
|  |  | Mvar |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(ii), Data Inputs and Outputs for the Real-Time Sequence and SCED. Positive for supplying VAR Negative for absorbing VAR |  |  |
|  |  | Bank Breaker Status |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13(1)(a)(iii), Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
| Circuit Breaker Data |  | Circuit Breaker MW flow |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.4 (2), Telemetry Criteria. Positive flow is from bus section to equipment (optional) |  |  |
|  |  | Circuit Breaker Mvar |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.4 (2), Telemetry Criteria. Positive flow is from bus section to equipment (optional) |  |  |
|  |  | Breaker Status |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.4 (2), Telemetry Criteria. |  |  |
| Load Data |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Load metering is preferred from the high side of the transformation point of the substation distribution transformer. |  |  |
|  |  | Load in MW |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.4 (2), Telemetry Criteria. (Implied). Negative for Load MW. |  |  |
|  |  | Load in Mvar |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.4 (2), Telemetry Criteria. (Implied). Negative for Load Mvar. |  |  |
| DC Tie Injection Data |  | DC Injection in MW |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.2 (3), Modeling of Resources and Transmission Loads. Positive flow is out of the station. |  |  |
|  |  | DC Injection in Mvar |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.2 (3), Modeling of Resources and Transmission Loads. Positive flow is out of the station |  |  |
|  |  | DC Tie Breaker Status |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.7.2 (3), Modeling of Resources and Transmission Loads. (Implied) |  |  |
| Weather Zone Tie Line Data |  | Temperature |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13 (1) e, Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
|  |  | Wind Speed (if available) |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 6.5.7.1.13 (1) e, Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
| Dynamic Rating Data |  | Line ID |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 60 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.8.1 (1) a, Dynamic Ratings Delivered via ICCP. |  |  |
|  |  | From Status |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 60 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.8.1 (1) b, Dynamic Ratings Delivered via ICCP. |  |  |
|  |  | To Station |  | Real-Time Monitoring, SCED & Security Analysis |  | TSP |  | ERCOT |  | 60 sec |  | ICCP |  | Blocks 1&2 |  | Protocol Section 3.10.8.1 (1) c, Dynamic Ratings Delivered via ICCP. |  |  |
|  |  | Normal Rating |  | Real-Time Security Analysis |  | TSP |  | ERCOT |  | 60 min |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.10.8.1 (1) d, Dynamic Ratings Delivered via ICCP. |  |  |
|  |  | Emergency Rating |  | Real-Time Security Analysis |  | TSP |  | ERCOT |  | 60 min |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.10.8.1 (1) d, Dynamic Ratings Delivered via ICCP. |  |  |
|  |  | 15-Minute Rating |  | Real-Time Security Analysis |  | TSP |  | ERCOT |  | 60 min |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.10.8.1 (1) d, Dynamic Ratings Delivered via ICCP. |  |  |
| Weather Zone Data |  | Current Temperature for each applicable Weather Zone |  | Real-Time Security Analysis |  | TSP |  | ERCOT |  | 10 min |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 3.10.8.1, Dynamic Ratings Delivered via ICCP |  |  |
| Block Load Transfer Point Data |  | Switching Device Status at BLT points. |  | BLT Transfers |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.9.5(i), Block Load Transfers between ERCOT and Non-ERCOT Control Areas |  |  |
| Other Modeled Devices (SVCs, etc.) |  | MW |  |  |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.1.13, Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
|  |  | MVar |  |  |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.1.13, Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |
|  |  | Status |  |  |  | TSP |  | ERCOT |  | 10 sec |  | ICCP |  | Blocks 1 & 2 |  | Protocol Section 6.5.7.1.13, Data Inputs and Outputs for the Real-Time Sequence and SCED. |  |  |

NOTE:	Real-Time data for Security Analysis can be provided to TSPs on request.

Private Network refers to generators with self-serve private load behind a single meter at the point of injection into the ERCOT grid.

LEGEND:

Mode of Communication

Web Portal - Online application available to market participants via the World Wide Web.

TCH - Transaction Clearinghouse.  The mechanism used to send/receive EDI transactions.

API - Programmatic API. A message protocol used to automate data exchange between ERCOT and market participants.

ICCP - Inter-Control Center Communication Protocol.  A standard protocol used to automate data exchange real-time control information between the ERCOT and participants.

Format

EDI - Electronic Data Exchange format. EDI formats are specified by the Texas SET working group and are based on standard EDI transaction protocols.

XML - eXtensible Markup Language.  XML is a self-describing meta language used to facilitate the exchange of data. XML will format requests and receive replies using the API.

CSV - Comma Separated Values.  A generic file format where elements of data are separated by commas within a file.

Office Document - One of the common Microsoft Office file formats such as MS Word or MS Excel.