Old EECP6.5.9.4		Emergency Electric Curtailment Plan (EECP)

(1)	At times it may be necessary to reduce ERCOT System Demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing Demand during such emergencies, ERCOT shall initiate and coordinate the implementation of the Emergency Electric Curtailment Plan (EECP) following the steps set forth below in Section 6.5.9.4.2, Restoration of Market OperationsEECP Steps.

(2)	The goal of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of cascading Outages.

(23)	ERCOT’s operating procedures must meet the following goals:

(a)	Use of market processes to the fullest extent practicable without jeopardizing the reliability of the ERCOT System;

(b)	Use of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(c)	Maximum use of ERCOT System capability;

(d)	Maintenance of station service for nuclear-powered Generation Resources;

(e)	Securing startup power for Generation Resources;

(f)	Operation of Generation Resources during loss of communication with ERCOT; and

(g)	Restoration of service to Loads in the manner defined in the Operating Guides.

(3)	ERCOT is responsible for coordinating with QSEs, TSPs, and DSPs to monitor ERCOT System conditions, initiating the EECP steps set forth herein, notifying all QSEs, and coordinating the implementation of the EECP steps while maintaining transmission security limits.

(4)	ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation.

(5)	During the EECP, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using the DC Ties or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with NERC scheduling guidelines.

(56)	Some of the EECP steps are not applicable if transmission security violations exist. There may be insufficient time to implement all EECP steps in sequence, however, to the extent practicable, ERCOT shall use Ancillary Services that QSEs have made available in the market to maintain or restore reliability.

(67)	ERCOT may immediately implement Step 53 of the EECP any time the steady-state system frequency is below 59.8 Hz and shall immediately implement Step 53 any time the steady-state frequency is below 59.5 Hz.

(78)	Percentages for Step 53 Load shedding mustwill be based on the previous year’s TSP peak Loads, as reported to ERCOT, and must be reviewed by ERCOT and modified annually as required.

6.5.9.4.1	General Procedures Prior to EECP StepsOperations

(1)	Step 1

(a)	Maintain 2,300 MW of reserves from Resources comprised of:

(i)	Undeployed Responsive Reserve; and

(ii)	The amount of Non-Spinning Reserve that has been deployed but has not ramped to its specified output level.

(b)	To maintain that 2,300 MW, ERCOT shall:

(i)	Use available Resources that can be deployed to increase Responsive Reserves;

- (1)	Prior to declaring EECP Step 1 detailed in Section 6.5.9.4.2, EECP Steps, ERCOT may perform the following operations consistent with Good Utility Practice:

- (ii)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase Responsive Reserve levels on other Resources;

- (iii)	Suspend any ongoing generating unit or Resource performance testing;

- (iv)	Commit available Resources as necessary that can respond in the timeframe of the emergency; such.  Such commitments arewill be settled using the HRUC process;

(v)	Use available DC Tie import capacity not already being used by QSEs and inquire about availability of BLTs;

(vi)	Request QSEs to voluntarily interrupt a DC Tie Schedule exporting power from ERCOT and, in the event no QSE will voluntarily interrupt its export schedule, ERCOT shall initiate curtailment of all non-firm export schedules in accordance with NERC Control Area energy scheduling guidelines; and(vii)	Start RMR Unitsc)	Start RMR units available in the time frame of the emergency. RMR Units mayunits should be loaded to full output capability as necessary.capability;

(2)	Step 2

Maintain 1,800 MW of ERCOT’s reserve from Resources comprised of undeployed Responsive Reserve Service. ERCOT shall:

(a)	Relax confidentiality requirements of transmission operating and system capacity information, if needed to improve communications during the Emergency Condition; and

(d)	Issue Dispatch Instructions to QSEs to suspend any ongoing ERCOT required generating unit or Resource performance testing;

(e)	Utilize available resources providing Non-Spin Reserve Services as required; and

(f)	ERCOT shall use the PRC to determine the appropriate Emergency Notification and EECP Steps.

(2)	In addition, ERCOT may issue an appeal through the public news media for voluntary load reduction if authorized by the ERCOT Chief Executive Officer or its designee based on an evaluation of existing and expected system conditions.

6.5.9.4.2	EECP Steps

(1)	Step 1 - Maintain a sum total of 2300 MW that results from adding 1) the amount of ERCOT Physical Responsive Reserve (PRC) MW (refer to Section 6..5.7.5) and 2) the amount of RRS MW which is supplied from Load Resources.

(a)	ERCOT will:

(i)	Notify the Southwest Power Pool Security Coordinator;

(ii)	Issue a manual HRUC Dispatch Instructions to Generation Resources available and off-line that can perform within the expected timeframe of the emergency;

(iii)	Use available DC Tie import capacity not already being used and inquire about availability of BLTs;

(b)	QSEs will notify ERCOT of any Resources uncommitted but available in the timeframe of the emergency.

(2)	Step 2 - Maintain a sum total of 2300 MW that results from adding 1) the amount of ERCOT Physical Responsive Reserve (PRC) MW (refer to Section 6.5.7.5) and 2) the amount of RRS MW which is supplied from Load Resources.

(a)	In addition to the measures associated with Step 1, ERCOT will:

(i)	Instruct TSPs and DSPs to reduce Customers load by using distribution voltage reduction measures, if deemed beneficial by the TSP or DSP;

(ii)	Instruct QSEs to deploy Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) in accordance with the following.

- (b)	Deploy half of the Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Load providing Responsive Reserve.  ERCOT shall develop a procedure for determining which Load Resources to interrupt and to equitably allocate Load Resources to one of two deployment stacks to enable a 50% deployment, which procedure must be approved in advance by TAC.

(3)	Step 3

Maintain ERCOT undeployed Responsive Reserve Service equal to the largest Generation Resource On-Line in ERCOT. The undeployed Responsive Reserve Service may come from Load Resources capable of controllably reducing or increasing consumption under dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action) and from Generation Resources.  To maintain that level of undeployed RRS, ERCOT:

(a)	Shall instruct TSPs and DSPs to reduce Load by using distribution voltage reduction management tools, if deemed beneficial by the TSP and DSP;

(b)	Shall instruct QSEs to interrupt all remaining Responsive Reserve supplied by Load Resources; and

- At the discretion of the ERCOT Operator deploy the remaining Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt all remaining Load providing Responsive Reserve.

- The ERCOT Operator may deploy both of the  Responsive Reserve groups at the same time; and

- ERCOT shall post a list of Load Resources on the MIS Certified Area for each QSE who are selected to interrupt under paragraph (1), Group 1 and those selected under paragraph (2), Group 2, following the DRUC.   ERCOT shall develop a process for determining which individual Load Resources to place in Group 1 and which to place in Group 2 to equitably allocate Load Resources that is based on random sampling of individual Load Resources until at least half of the total Mw amount of Load Resources providing Responsive Reserve is established in Group 1.  All remaining Load Resources shall be listed in Group 2.

(ciii)	May, withWith the approval of the affected Non-ERCOT Control Areacontrol area, may instruct TSPs or DSPs to implement Block Load Transfers, as described in 6.5.9.5, Block Load Transfers between ERCOT and Non-ERCOT Control AreasBLTs, which transfer Loadload from the ERCOT Control Area to Non-ERCOT Control Areas.control area to Non-ERCOT control areas.  Use of a BLT will be defined in the ERCOT Operating Guides.

(d)	ERCOT shall initiate curtailment of all remaining export schedules in accordance with NERC Control Area energy scheduling guidelines.

(4)	Step 4 – Maintain system frequency at 60 Hz

In addition to measures listed above(iv)	Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary Load curtailmentenergy conservation.

(5)	Step 5 —b)	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)	Step 3 – Maintain system frequency at 59.8 Hz or greater

(a)	In addition to measures listed above, ERCOT shall instruct, in 100 MW blocks, all TSPs and DSPs having control over distribution feeder breakers or control of breakers serving retail customers to shed Load to maintain a steady-associated with Steps 1 and 2, ERCOT will direct all TSPs and DSPs and their agents to shed firm load, in 100 MW blocks, distributed as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hz. ERCOT shall allocate manual Load shedding for ERCOT-wide emergencies based on the amount of Load that is served by each TSP

(b)	In addition to measures associate with Steps 1 and 2, TSPs and DSPs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs shall not manually drop load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan.

Document comparison done by Workshare DeltaView on Friday, March 16, 2007 11:57:45 AM

| Input: |  |
| --- | --- |
| Document 1 | file://C:/temp/old EECP.doc |
| Document 2 | file://C:/temp/new EECP.doc |
| Rendering set | standard |

| Legend: |  |
| --- | --- |
| Insertion |  |
| Deletion |  |
| Moved from |  |
| Moved to |  |
| Style change |  |
| Format change |  |
| Moved deletion |  |
| Inserted cell |  |
| Deleted cell |  |
| Moved cell |  |
| Split/Merged cell |  |
| Padding cell |  |

| Statistics: |  |
| --- | --- |
|  | Count |
| Insertions | 69 |
| Deletions | 56 |
| Moved from | 9 |
| Moved to | 9 |
| Style change | 0 |
| Format changed | 0 |
| Total changes | 143 |