## Sheet1
MP | Sort | Section # | Comment | Accepted / Rejected | Resolution
Garland | A | Title Page | The language should allow for knowledgeable persons other than just operators to work with the testing due to availability of operators. | Clarification | Personnel other than operations at the MP end are acceptable provided the testing is performed from an operator's console to assure ERCOT operators and TSP/QSE operators are looking at the same elements being tested. Normal SCADA control access must be authorized to manually replace a point at the MP system.
Garland | A | Title Page | Language should be added that states that any analog or status substitutions should not cause any activity in the real-time system - this includes circumstances of tripping a line or causing an SCE error as examples. | Clarification | The intent is to use a quick toggle back and forth so that typical systems will not be materially effected.
Garland | A | Title Page | Quality flag requirements should be noted as not resolved as yet - there are the TAC approved set & the EMS Business Requirement set - not sure what you test for until that is resolved | Accepted | ERCOT will specify quality codes required in April 2007.
NRG | B | E1 Overview | Release 2 - Verify ICCP Communications, Performance and Failover for TSPs, QSEs and ERCOT and perform Point-to-Point Verification for all SCADA telemetry that exist in the ERCOT Zonal Production EMS at the time of EDS 1 Release 2. | Clarification | ERCOT's intent is to perform p2p for all points required in the Nodal protocols. ERCOT will start the test as indicated, however exit criteria states that all points will be tested.
TXU | C1 | R1 Objectives | TXU: Need to find a way to conduct this test using data from the production environment but not require QSEs to override actual production data. | Clarification | QSE will have a separate ICCP Nodal environment that contains all points required by the Nodal protocols. These points will not be contained in the Zonal system.
NRG | C2 | R1 MP Readiness | Release 1 Market Participant (MP) readiness - For EDS 1 - Release 1 to be conducted; the following activities are required from MPs: ERCOT to verify the alarm configuration with selected TSPs and QSEs, by having MPs' Operators randomly test selected breakers and switches, and enter values that exceed selected limits to test message organization/categorization. | Accepted | Will add text to approach document.
CNP | D1 | R2 Description | The data set provided to ERCOT from CNP is expected to remain about the same (plus routine updates and addition of new telemetry) upon transition to the Nodal EMS system. The redundant ICCP links and host servers are currently in place and operational. Link failover tests can be re-verified. | Accepted | Will perform verification as planned.
CNP | D1 | R2 Description | Rather than perform a complete point-to-point checkout of all exchanged data points it is better to address systemic issues identified as a result of the Beta test and the NMT process previously performed. Full point-to-point check out should only be considered for all new data points or if there is a quantifiable reason to believe the bulk of the existing telemetry input to ERCOT is in error. | Pending | Summary of the Beta Testing results will be reviewed and presented to TPTF. The purpose of the p2p test is to verify mapping at ERCOT and to detect errors at ERCOT. So far, test results indicate greater than 5% of points have errors and that the errors are significant. P2P is likely required to resolve ERCOT's errors.
LCRA | D2 | R2 Objectives | (Note that the quality code of switches that are not telemetered may not show a "manual entered" quality code for either of their states since their state is always set manually.) | Clarification | Agreed this is an issue at ERCOT and one that ERCOT will need to resolve. To-date the Beta Testing shows differences between MPs.
NRG | D3 | R2 Entry Criteria | Must be configured to exchange with MPs all SCADA - ICCP and RTU if applicable - data that exist in the ERCOT Zonal EMS system at the time of EDS 1 Release 2, via ICCP | Clarification | RTU will not be configured in Nodal but may be used to support EDS 1 mapping during the p2p testing. New points as required by Nodal protocols must use ICCP.
NRG | D4 | R2 Exit Criteria | Verify ICCP performance for each TSP and QSE during failover configurations | Accepted | Will add text to approach document.
NRG | D4 | R2 Exit Criteria | Verify ICCP and EMS failover performance at ERCOT | Accepted | Will add text to approach document.
NRG | D5 | R2 MP Readiness | For EDS 1 - Release 1 to begin; the following capacities are required from MPs: MPs to have redundant ICCP capabilities, configured to communicate with ERCOT EDS 1 Nodal EMS | Accepted | Will add text to approach document.
NRG | D5 | R2 MP Readiness | For EDS 1 - Release 1 to begin; the following capacities are required from MPs: MPs ICCP data links to be configured with same data sets as those used for both the ICCP and RTU data links if applicable in the Zonal market. | Accepted | Will add text to approach document.
NRG | T | Timeline | Note: when will MPs need to have redundant ICCP data links, with the required data sets, and configured to communicate with ERCOT Nodal EMS? | Clarification | Will add Release 2 Market Participant (MP) Readiness section to address as MP readiness criteria.
NRG | T | Timeline | Note: which metrics if any, are passed after the completion of EDS1 Release 2? | Pending | Will identify specific metrics.
NRG | Z | Appendix | Note: could the topology diagram(s) be exchanged several days before the test? | Accepted | Will add text to approach document. In cases where ERCOT has access to the MPs one-line displays, ERCOT will not require a copy of the topology diagrams (at the direction of the MP).
NRG | Z | Appendix | Note: could the point list be exchanged several days before the test? | Accepted | Will add text to approach document.
NRG | Z | Appendix | Note: should it indicate "Manually Replaced"? | Accepted | Will add text to approach document.